## Cover
Preview
This Excel workbook is a part of the "Technology Data for the Indonesian Power Sector 2024" publication.
It provides the quantitative data in an easy-to-use manner, but should be understood in the context of the report where further descriptions are available, incl. the underlying methodology for the work.
The full report can be found at the website of the Danish Energy Agency in the drop-down publication list:
https://ens.dk/en/our-responsibilities/global-cooperation/country-cooperation/indonesia
Disclaimer
This publication and the material featured herein are provided “as is”. All reasonable precautions have been taken by the authors to verify the reliability of the material featured in this publication. Neither the authors, the General Directorate of Electricity nor any of its officials, agents, data or other third-party content providers or licensors provides any warranty, including as to the accuracy, completeness or fitness for a particular purpose or use of such material, or regarding the non-infringement of third-party rights, and they accept no responsibility or liability with regard to the use of this publication and the material featured therein.
Contact information
DG Electricity:
- pramudya@esdm.go.id
Danish Energy Agency:
- ksath@ens.dk
- morten@indodepp.com
Ea Energy Analysis:
- rin@eaea.dk

## Geothermal - large
Technology
| Technology | Geothermal power plant - large system (flash or dry)
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 55 | 55 | 55 | 30 | 500 | 30 | 500 |  | 1
| Generating capacity for total power plant (MWe) | 110 | 110 | 110 | 30 | 500 | 30 | 500 |  | 1
| Electricity efficiency, net (%), name plate | 16 | 17 | 18 | 8 | 18 | 10 | 20 | A | 5
| Electricity efficiency, net (%), annual average | 15 | 16 | 17 | 8 | 18 | 10 | 20 | A | 5
| Forced outage (%) | 10 | 10 | 10 | 5 | 30 | 5 | 30 |  | 1
| Planned outage (weeks per year) | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 1
| Technical lifetime (years) | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 1,10
| Construction time (years) | 2 | 2 | 2 | 1.5 | 3 | 1.5 | 3 | H | 1,10
| Space requirement (1000 m2/MWe) | 30 | 30 | 30 | 20 | 40 | 20 | 40 |  | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 90 | 90 | 90 | 70 | 100 | 70 | 100 |  | 1
| Capacity factor (%), incl. outages | 80 | 80 | 80 | 70 | 100 | 70 | 100 |  | 1
Ramping configurations
| Ramping (% per minute) | 3 | 10 | 20 | [5 empty] | 8
Minimum load (% of full load)
Warm start-up time (hours)
Cold start-up time (hours)
Environment
| PM 2.5 (gram per Nm3) | - | - | - | - | - | - | - | C | 6
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | C | 6
| NOX (g per GJ fuel) | - | - | - | - | - | - | - | C | 6
| CH4 (g per GJ fuel) | - | - | - | - | - | - | - | C | 6
| N2O (g per GJ fuel) | - | - | - | - | - | - | - | C | 6
Financial data
| Nominal investment (M$/MWe) | 4.4 | 4.4 | 3.96 | 3.3 | 5.5 | 1.7 | 5.1 | B,D,E,F | 1,2,3,4
| - of which equipment | 60% | 60% | 60% | 40% | 70% | 40% | 70% |  | 9
| - of which installation | 40% | 40% | 40% | 30% | 50% | 30% | 50% |  | 9
| Fixed O&M ($/MWe/year) | 110000 | 110000 | 99000 | 82500 | 137500 | 74250 | 123750 | B,D,G | 3,11
| Variable O&M ($/MWh) | 0.27 | 0.27 | 0.24 | 0.2025 | 0.3375 | 0.3 | 0.18 | B,D | 1,4
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
Technology specific data
| Exploration costs (M$/MWe) | 0.16 | 0.15 | 0.15 | 0.11 | 0.21 | 0.11 | 0.21 |  | 7
| Confirmation costs (M$/MWe) | 0.16 | 0.15 | 0.15 | 0.11 | 0.21 | 0.11 | 0.21 |  | 7
References:
1 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
2 | IEA, World Energy Outlook, 2023
3 | IRENA, 2023, Renewable Power Generation Costs in 2022
4 | Learning curve approach for the development of financial parameters.
5 | Moon & Zarrouk, 2012, “Efficiency Of Geothermal Power Plants: A Worldwide Review”.
6 | Yuniarto, et. al., 2015. “Geothermal Power Plant Emissions in Indonesia”.
7 | Geothermal Energy Association, 2006, "A Handbook on the Externalities, Employment, and Economics of Geothermal Energy".
8 | Geothermal Energy Association, 2015, "Geothermal Energy Association Issue Brief: Firm and Flexible Power Services Available from Geothermal Facilities"
9 | IRENA, 2015, Renewable Power Generation Costs in 2014.
10 | Moore, 2016, "Geothermal Power Generation: Developments and Innovation, chapter 18: Project permitting, finance, and economics for geothermal power generation"
11 | NREL ATB 2023
Notes:
A | The efficiency is the thermal efficiency - meaning the utilization of heat from the ground. Since the geothermal heat is renewable and considered free, then an increase in effciency will give a lower investment cost per MW. These large units are assumed to be flach units at high source temperatures.
B | Uncertainty (Upper/Lower) is estimated as +/- 25%, which is an estimate build upon cases from IRENA (ref. 9)
C | Geothermal do emit H2S. From Minister of Environment Regulation 21/2008 this shall be below 35 mg/Nm3.
D | The learning rate is assumed to impact the geothermal specific equipment and installation. The power plant units (i.e. the turbine and pump) is assumed to have very litle development. From Ref. 9 it is assumed that half of the investment cost are on the geothermal specific equipment.
E | Investment cost are including Exploration and Confirmation costs (see under Technology specific data).
F | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on varying learning rates
G | O&M includes costs related to the continous management of the geothermal site to maintain capacity and performance. Given cost is estimated for two sets of wells for makeup and reinjection over the 25-year life of the project to maintain performance.
H | Refers to construction of the steam cycle power plant itself. Preperation of the geothermal site includes surveying, exploration, drilling, resource confirmation, which can take 4-5 years in total.

## Geothermal - small
Technology
| Technology | Geothermal power plant - small system (binary or condensing)
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 10 | 10 | 10 | 0.3 | 20 | 0.3 | 20 |  | 1,8
| Generating capacity for total power plant (MWe) | 20 | 20 | 20 | 5 | 30 | 5 | 30 |  | 1
| Electricity efficiency, net (%), name plate | 10 | 11 | 12 | 6 | 12 | 8 | 14 | A | 5
| Electricity efficiency, net (%), annual average | 10 | 11 | 12 | 6 | 12 | 8 | 14 | A | 5
| Forced outage (%) | 10 | 10 | 10 | 50 | 30 | 50 | 30 |  | 1
| Planned outage (weeks per year) | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 1
| Technical lifetime (years) | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 1,10
| Construction time (years) | 2 | 2 | 2 | 1,5 | 3 | 1,5 | 3 | H | 1,10
| Space requirement (1000 m2/MWe) | 30 | 31 | 32 | 20 | 40 | 20 | 40 |  | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 90 | 90 | 90 | 70 | 100 | 70 | 100 |  | 1
| Capacity factor (%), incl. outages | 80 | 80 | 80 | 70 | 100 | 70 | 100 |  | 1
Ramping configurations
Ramping (% per minute)
Minimum load (% of full load)
Warm start-up time (hours)
Cold start-up time (hours)
Environment
| PM 2.5 (gram per Nm3) | - | - | - | - | - | - | - | B | 6
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | B | 6
| NOX (g per GJ fuel) | - | - | - | - | - | - | - | B | 6
| CH4 (g per GJ fuel) | - | - | - | - | - | - | - | B | 6
| N2O (g per GJ fuel) | - | - | - | - | - | - | - | B | 6
Financial data
| Nominal investment (M$/MWe) | 5.5 | 5.5 | 4.95 | 4.2 | 7 | 1.8 | 4.82 | C,D,E,F | 1,2,4,8,11
| - of which equipment | 60% | 60% | 60% | 40% | 70% | 40% | 70% |  | 3
| - of which installation | 40% | 40% | 40% | 30% | 50% | 30% | 50% |  | 3
| Fixed O&M ($/MWe/year) | 145000 | 145000 | 130500 | 108750 | 181250 | 163125 | 97875 | C,D,G | 1,4,9,11
| Variable O&M ($/MWh) | 0.39 | 0.39 | 0.351 | 0.2925 | 0.4875 | 0.43875 | 0.26325 | C,D | 1,4
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
Technology specific data
| Exploration costs (M$/MWe) | 0.16 | 0.15 | 0.15 | 0.11 | 0.21 | 0.11 | 0.21 |  | 7
| Confirmation costs (M$/MWe) | 0.16 | 0.15 | 0.15 | 0.11 | 0.21 | 0.11 | 0.21 |  | 7
References:
1 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
2 | Budisulistyo & Krumdieck , 2014, "Thermodynamic and economic analysis for the pre- feasibility study of a binary geothermal power plant"
3 | IRENA, 2015, Renewable Power Generation Costs in 2014.
4 | Learning curve approach for the development of financial parameters.
5 | Moon & Zarrouk, 2012, “Efficiency Of Geothermal Power Plants: A Worldwide Review”.
6 | Yuniarto, et. al., 2015. “Geothermal Power Plant Emissions in Indonesia”.
7 | Geothermal Energy Association, 2006, "A Handbook on the Externalities, Employment, and Economics of Geothermal Energy".
8 | Climate Policy Initiative, 2015, Using Private Finance to Accelerate Geothermal Deployment: Sarulla Geothermal Power Plant, Indonesia.
9 | IRENA, 2023, Renewable Power Generation Costs in 2022
10 | Moore, 2016, "Geothermal Power Generation: Developments and Innovation, chapter 18: Project permitting, finance, and economics for geothermal power generation"
11 | NREL ATB 2023
Notes:
A | The efficiency is the thermal efficiency - meaning the utilization of heat from the ground. Since the geothermal heat is renewable and considered free, then an increase in effciency will give a lower investment cost per MW. These smaller units are assumed to be binary units at medium source temperatures.
B | Geothermal do emit H2S. From Minister of Environment Regulation 21/2008 this shall be below 35 mg/Nm3.
C | Uncertainty (Upper/Lower) is estimated as +/- 25%.
D | Investment cost are including Exploration and Confirmation costs (see under Technology specific data).
E | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
F | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates varying between 10-15% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.
G | O&M includes costs related to the continous management of the geothermal site to maintain capacity and performance. Given costs is estimated for two sets of wells for makeup and reinjection over the 25-year life of the project to maintain performance.
H | Refers to construction of the steam cycle power plant itself. Preperation of the geothermal site includes surveying, exploration, drilling, resource confirmation, which can take 4-5 years in total.

## Large hydro power plant
Technology
| Technology | Hydro power plant - large system
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 60 | 60 | 60 | 17 | 175 | 100 | 2000 | G | 1,8
| Generating capacity for total power plant (MWe) | 200 | 200 | 200 | 68 | 700 | 100 | 2000 | G | 1,8
| Electricity efficiency, net (%), name plate | 95 | 95 | 95 | 85 | 97 | 85 | 97 | A | 7
| Electricity efficiency, net (%), annual average | 95 | 95 | 95 | 85 | 97 | 85 | 97 | A | 7
| Forced outage (%) | 4 | 4 | 4 | 2 | 10 | 2 | 10 |  | 1
| Planned outage (weeks per year) | 6 | 6 | 6 | 3 | 10 | 3 | 10 |  | 1
| Technical lifetime (years) | 50 | 50 | 50 | 40 | 90 | 40 | 90 | B | 1
| Construction time (years) | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 1
| Space requirement (1000 m2/MWe) | 62 | 62 | 62 | 47 | 78 | 47 | 78 | C | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 55 | 55 | 55 | 20 | 95 | 20 | 95 | G | 1,2,11
| Capacity factor (%), incl. outages | 51 | 51 | 51 | 20 | 95 | 20 | 95 | G | 1,2,11
Ramping configurations
| Ramping (% per minute) | 30 | 30 | 30 | 10 | 86 | 10 | 90 |  | 3
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3
| Warm start-up time (hours) | 0.3 | 0.2 | 0.1 | 0 | 0.5 | 0 | 0.3 |  | 3
| Cold start-up time (hours) | 2 | 1.7 | 0.2 | 0.1 | 7 | 0.1 | 7 |  | 3
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 2.2 | 2.112 | 1.958 | 1.65 | 2.75 | 1.4685 | 2.4475 | D,E,F | 1,4,5,6
| - of which equipment | 30% | 30% | 30% | 20% | 50% | 20% | 50% | H | 6,10
| - of which installation | 70% | 70% | 70% | 50% | 80% | 50% | 80% | H | 6,10
| Fixed O&M ($/MWe/year) | 43000 | 41000 | 38000 | 32250 | 53750 | 28500 | 47500 | C | 1,4,5,6
| Variable O&M ($/MWh) | 0.74 | 0.71 | 0.66 | 0.555 | 0.925 | 0.495 | 0.825 | C | 1,5
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
References:
1 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
2 | Branche, 2011, “Hydropower: the strongest performer in the CDM process, reflecting high quality of hydro in comparison to other renewable energy sources”.
3 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".
4 | IRENA, 2023, Renewable Power Generation Costs in 2022
5 | Learning curve approach for the development of financial parameters.
6 | IEA, 2021, Hydropower Special Market Report
7 | Stepan, 2011, Workshop on Rehabilitation of Hydropower, “The 3-Phase Approach”.
8 | Prayogo, 2003, "Teknologi Mikrohidro dalam Pemanfaatan Sumber Daya Air untuk Menunjang Pembangunan Pedesaan. Semiloka Produk-produk Penelitian Departement Kimpraswill Makassar".
9 | General Electric, www.gerenewableenergy.com, Accessed: 20th July 2017
10 | ASEAN, 2016, "Levelised cost of electricity of selected renewable technologies in the ASEAN member states".
11 | MEMR, 2023, "Handbook of Energy & Economic Statistics of Indonesia 2022"
Notes:
A | This is the efficiency of the utilization of the waters potential energy. This can not be compared with a thermal power plant that have to pay for its fuel.
B | Hydro power plants can have a very long lifetime is operated and mainted properly. Hover Dam in USA is almost 100 years old.
C | Uncertainty (Upper/Lower) is estimated as +/- 25%.
D | Numbers are very site sensitive. There will be an improvement by learning curve development, but this improvement will equalized because the best locations will be utilized first. The investment largely depends on civil work.
E | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
F | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 10-15% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.
G | Based on data collection from Indonesian projects
H | For large hydropower plants the civil works and earthworks to establish tunneling and dams are often the biggest share of the costs (around 50% according to Ref 6). These costs are included as instalaltion costs as described in the overall methodology.

## Medium-small hydro power plant
Technology
| Technology | Hydro power plant - Medium/small system
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 5 | 5 | 5 | 1 | 22 | 1 | 50 | E | 2,9
| Generating capacity for total power plant (MWe) | 11 | 11 | 11 | 1 | 100 | 20 | 100 | E | 2,9
| Electricity efficiency, net (%), name plate | 95 | 95 | 95 | 85 | 97 | 85 | 97 | A | 1
| Electricity efficiency, net (%), annual average | 95 | 95 | 95 | 85 | 97 | 85 | 97 | A | 1
| Forced outage (%) | 4 | 4 | 4 | 2 | 10 | 2 | 10 |  | 1
| Planned outage (weeks per year) | 6 | 6 | 6 | 3 | 10 | 3 | 10 |  | 1
| Technical lifetime (years) | 50 | 50 | 50 | 40 | 90 | 40 | 90 |  | 1
| Construction time (years) | 3 | 3 | 3 | 2 | 6 | 2 | 6 |  | 1
| Space requirement (1000 m2/MWe) | 14 | 14 | 14 | 11 | 18 | 11 | 18 | B
Additional data for non thermal plants
| Capacity factor (%), theoretical | 55 | 55 | 55 | 20 | 95 | 20 | 95 |  | 8,9
| Capacity factor (%), incl. outages | 51 | 51 | 51 | 20 | 95 | 20 | 95 |  | 8,9
Ramping configurations
| Ramping (% per minute) | 50 | 50 | 50 | 30 | 100 | 30 | 100 |  | 3
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 3
| Cold start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 3
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 2.5 | 2.4 | 2.225 | 1.875 | 3.125 | 1.6688 | 2.7812 | C,D | 5,6,9
| - of which equipment | 40% | 40% | 40% | 20% | 50% | 20% | 50% | F | 6
| - of which installation | 60% | 60% | 60% | 50% | 80% | 50% | 80% | F | 6
| Fixed O&M ($/MWe/year) | 47800 | 45800 | 42500 | 35850 | 59750 | 31875 | 53125 |  | 4,5,6,9
| Variable O&M ($/MWh) | 0.57 | 0.5472 | 0.513 | 0.4275 | 0.7125 | 0.38475 | 0.64125 | B | 1
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
References:
1 | Stepan, 2011, Workshop on Rehabilitation of Hydropower, “The 3-Phase Approach”.
2 | Prayogo, 2003, "Teknologi Mikrohidro dalam Pemanfaatan Sumber Daya Air untuk Menunjang Pembangunan Pedesaan. Semiloka Produk-produk Penelitian Departement Kimpraswill Makassar".
3 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".
4 | Energy and Environmental Economics, 2014, "Capital Cost Review of Power Generation Technologies - Recommendations for WECC’s 10- and 20-Year Studies".
5 | IRENA, 2023, Renewable Power Generation Costs in 2022
6 | IEA, 2021, Hydropower Special Market Report
7 | ASEAN, 2019, "Levelised cost of electricity of selected renewable technologies in the ASEAN member states".
8 | Branche, 2011, “Hydropower: the strongest performer in the CDM process, reflecting high quality of hydro in comparison to other renewable energy sources”.
9 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
Notes:
A | This is the efficiency of the utilization of the waters potential energy. This can not be compared with a thermal power plant that have to pay for its fuel.
B | Uncertainty (Upper/Lower) is estimated as +/- 25%.
C | Numbers are very site sensitive. There will be an improvement by learning curve development, but this improvement will equalized because the best locations will be utilized first. The investment largely depends on civil work.
D | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
E | Based on data collection from Indonesian projects
F | For hydropower plants the civil works and earthworks to are often a significant share of the costs which are included as installation according to the methodology.

## Mini-micro hydro power plant
Technology
| Technology | Hydro power plant - Mini/micro system
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 0.5 | 0.5 | 0.5 | 0.1 | 1 | 0.1 | 1 | G | 1,8
| Generating capacity for total power plant (MWe) | 0.69 | 0.69 | 0.69 | 0.1 | 1.3 | 0.1 | 1.3 | G | 1,8
| Electricity efficiency, net (%), name plate | 80 | 80 | 80 | 70 | 90 | 70 | 90 | A | 7
| Electricity efficiency, net (%), annual average | 80 | 80 | 80 | 70 | 90 | 70 | 90 | A | 7
| Forced outage (%) | 4 | 4 | 4 | 2 | 10 | 2 | 10
| Planned outage (weeks per year) | 6 | 6 | 6 | 3 | 10 | 3 | 10
| Technical lifetime (years) | 50 | 50 | 50 | 40 | 90 | 40 | 90 | B
| Construction time (years) | 2 | 2 | 2 | 1.5 | 3 | 1.5 | 3
Space requirement (1000 m2/MWe)
Additional data for non thermal plants
| Capacity factor (%), theoretical | 55 | 55 | 55 | 20 | 95 | 20 | 95 |  | 1,2
| Capacity factor (%), incl. outages | 51 | 51 | 51 | 20 | 95 | 20 | 95 |  | 1,2
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | E
| Minimum load (% of full load) | - | - | - | - | - | - | - | E
| Warm start-up time (hours) | - | - | - | - | - | - | - | E
| Cold start-up time (hours) | - | - | - | - | - | - | - | E
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 2.7 | 2.592 | 2.403 | 2.025 | 3.375 | 1.8022 | 3.0038 | D,F | 1,4,5
| - of which equipment | 40% | 40% | 40% | 20% | 50% | 20% | 50% |  | 6
| - of which installation | 60% | 60% | 60% | 50% | 80% | 50% | 80% |  | 6
| Fixed O&M ($/MWe/year) | 60400 | 58000 | 54000 | 45300 | 75500 | 40500 | 67500 | C | 1,4,5
| Variable O&M ($/MWh) | 0.57 | 0.5472 | 0.5073 | 0.4275 | 0.7125 | 0.38048 | 0.63412 | C | 1,5
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
References:
1 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
2 | Branche, 2011, “Hydropower: the strongest performer in the CDM process, reflecting high quality of hydro in comparison to other renewable energy sources”.
3 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".
4 | IRENA, 2023, Renewable Power Generation Costs in 2022
5 | Learning curve approach for the development of financial parameters.
6 | IEA, 2021, Hydropower Special Market Report
7 | IFC, 2015, "Hydroelectric Power - A guide for developers and investers".
8 | Prayogo, 2003, "Teknologi Mikrohidro dalam Pemanfaatan Sumber Daya Air untuk Menunjang Pembangunan Pedesaan. Semiloka Produk-produk Penelitian Departement Kimpraswill Makassar".
Notes:
A | This is the efficiency of the utilization of the waters potential energy. This can not be compared with a thermal power plant that have to pay for its fuel.
B | Hydro power plants can have a very long lifetime is operated and mainted properbly. Hover Dam in USA is almost 100 years old.
C | Uncertainty (Upper/Lower) is estimated as +/- 25%.
D | Numbers are very site sensitive and the uncertainty can be even more extreme than listed. There will be an improvement by learning curve development, but this improvement will equalized because the best locations will be utilized first. The investment largely depends on civil work.
E | It is assumed that micro and mini hydro do not have a reservior (run-of-river) and therefor is not capable of regulation. The possibility of a turbine bypass could give the possibility of down regulation.
F | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
G | Based on data collection from Indonesian projects

## Ground-mounted PV
Technology
| Technology | PV ground-mounted, utility-scale, grid connected
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity a typical power plant (MWe) | 50 | 80 | 100 |  |  |  |  | A | 1
| Electricity efficiency, net (%), name plate | - | - | - |  |  |  |  | B
| Electricity efficiency, net (%), annual average | - | - | - |  |  |  |  | B
| Forced outage (%) | - | - | -
| Planned outage (weeks per year) | - | - | -
| Technical lifetime (years) | 27 | 30 | 35 | 25 | 30 | 28 | 42 |  | 1
| Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 1.5 | 0.25 | 1 |  | 1
| Space requirement (1000 m2/MWp) | 9.1 | 8.3087 | 7.5417 | 6 | 13 | 5 | 12 | U,V | 7,8
Additional data for non thermal plants
| Capacity factor (%), theoretical | 20.5479 | 21.1187 | 21.6895 | 17.4658 | 23.6301 | 18.4361 | 24.9429 | L,M | 1,2,3
| Capacity factor (%), incl. outages | 20.4452 | 21.0131 | 21.5811 | 17.3784 | 23.512 | 18.3439 | 24.8182 | L,M,X | 1,2,3
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | C
| Minimum load (% of full load) | - | - | - | - | - | - | - | C
| Warm start-up time (hours) | - | - | - | - | - | - | - | C
| Cold start-up time (hours) | - | - | - | - | - | - | - | C
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 0.96 | 0.672 | 0.48 | 0.828 | 1.5 | 0.288 | 0.6 | E,P,R,S | 1,4,5,8,9
| - of which equipment | 85% | 80% | 76% | [5 empty] | 1,4
| - of which installation | 15% | 20% | 24% |  |  |  |  | W | 1,4
| Fixed O&M ($/MWe/year) | 7500 | 6800 | 6100 | 3800 | 11300 | 3100 | 9200 | Q | 1,4
| Variable O&M ($/MWh) | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0
Technology specific data
| Global horizontal irradiance (kWh/m2/y) | 1700 | 1700 | 1700 | 1300 | 2200 | 1300 | 2200 | F | 1,2,3
| DC/AC sizing factor (Wp/W) | 1.2 | 1.2 | 1.2 |  |  |  |  | G | 1,5
| Transposition Factor for fixed tilt system | 1.01 | 1.01 | 1.01 |  |  |  |  | H | 3
| Performance ratio [-] | 0.86 | 0.9 | 0.92 |  |  |  |  | I | 1,5
| PV module conversion efficiency (%) | 0.205 | 0.23 | 0.26 | [5 empty] | 1,4,5
| Inverter lifetime (years) | 12.5 | 15 | 15 | [5 empty] | 5
Output
| Full load hours (kWh/kW) | 1800 | 1850 | 1900 | 1350 | 2300 | 1450 | 2450 | J, L,M
| Peak power full load hours (kWh/kWp) | 1500 | 1550 | 1600 | 1600 | 2750 | 1750 | 2950 | K, L,M
Financial data
| PV module & inverter cost ($/Wp) | 0.408 | 0.2688 | 0.1824 | 0.3519 | 0.6375 | 0.10944 | 0.228 |  | 1,4
| Balance Of Plant cost ($/Wp) | 0.272 | 0.1792 | 0.1216 | 0.2346 | 0.425 | 0.07296 | 0.152 |  | 1,4
| Installation and other cost ($/Wp) | 0.12 | 0.112 | 0.096 | 0.1035 | 0.1875 | 0.0576 | 0.12 | W | 1,4
| Specific investment, total system ($/Wp) | 0.8 | 0.56 | 0.4 | 0.69 | 1.25 | 0.24 | 0.5 | E | 1,4,5,8,9
| Specific investment, total system (M$/MW) | 0.96 | 0.672 | 0.48 | 0.828 | 1.5 | 0.288 | 0.6 | P | 1,4,5,8,9
References:
1 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
2 | Data analysed from www.renewables.ninja for multiple locations in Indonesia.
3 | PVGIS © Europeen Communitees 2001-2012.
4 | IRENA, Renewable Power Generation Costs in 2022, 2023
5 | The Danish Energy Agency, Technology data for generation of electricity and district heating, 2023.
6 | Space requirement mapped for local utility-scale PV by EA Energy Analysis in 2023, based on emthodology of ref. 7
7 | M. Bolinger and G. Bolinger, Land Requirements for Utility-Scale PV: An Empirical Update on Power and Energy Density, 2022
8 | World Energy Outlook 2022, IEA, 2023
9 | IRENA, Future of Solar PV - Deployment, investment,technology, grid integration and socio-economic aspects, 2019
Notes:
A | Listed as MWe. The MWp will depend on the DC/AC siizing factor
B | See "PV module conversion efficiency (%)". The improvement in technology development is also captured in capacity factor, investment costs and space requirement.
C | The generation from a PV system reflects the yearly and daily variation in solar irradiation. It is possible to curtail solar, and this can be done rapidly.
E | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
F | The global horizontal irradiation is a measure of the energy resource potential available and depends on the exact geographical location. 1700 kWh/m2/year corresponds to a resource slightly above the median value in Java. The range of GHI across the country ranges from 1300 kWh/m2 to 2200 kWh/m2.
G | The DC/AC equals module peak capacity Wp divided by plant capacity We (output of the inverter). The sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity.
H | The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. In Indonesia the TF factor for fixed systems is very low, adding only 0-1 % to the production.
I | The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non- STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the potential added benefit of having bifacial modules which raise the generation by 5%.
J | The full load hours is defined as the peak full load hours*DC/AC sizing factor
K | The number of full load hours is calculated based on the other values in the table. The formula is: Peak full load hours = Global horizontal irradiance * transposition factor * performance ratio.
L | Capacity factor = Full load hours / 8760.
M | The capacity factor or full load hours depend greatly on the global horizontal irradiance at the specific plant site. For sites significantly different from the 1700 kWh/m2/year solar irradiation mentioned here, the caacity factors should be adjusted accordingly.
P | The “specific investment, total system per rated capacity W(AC)” is calculated as “specific investment, total system per Wp(DC)” multiplied by the sizing factor.
Q | The cost of O&M includes insurance and regular replacement of inverters, technical operation, preventive maintenance, commercial operation, corrective maintenance, insurance, greenkeeping and security. O&M costs are assumed to decrease slower than for equipments. Reported values have a wide range so a +/- 50% interval is suggested for the uncertainty intervals.
R | Invstment cost projections and unertainty ranges are based on a continued reduction estimated from a number of sources incl. ref. 1, 5, 8, 9.
S | For 2023, uncertainty ranges are based on cost spans of various sources, incl. Focus Group Discussions with various stakeholders
T | PV module conversion efficiency (%) is the ration of the energy from the sun that hits the solar panel that is coverted into DC eletricity in the module. | Is the ration of the energy from the sun that hits the solar panel that is coverted into DC eletricity in the module
U | Estimations of space requirements are based on the mapping of the average polygonal area occupied by PV arrays and electrical equipments like inverter pad of existing utility scale PV plants in Indonesia and Singapore. The methode is decribed in [8].
V | The space requirement is reduced because of the improved efficiency of the modules, assuming that total area decrease by only 80 % of the decreased demand for modul area.
W | The cost of labour and the installation performance is not expected to improve in the same extent as the costs for the equipment. Therefore, the share of installation cost would increase over the years.
X | Yearlly outage time is assumed to be 0,5 % equal to approxemately 2 hours.

## Rooftop PV
Technology
| Technology | PV household scale, rooftop, grid connected
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for total power plant (kWe(AC)) | 5 | 5 | 5 |  |  |  |  | A | 1
| Electricity efficiency, net (%), name plate | - | - | - |  |  |  |  | B
| Electricity efficiency, net (%), annual average | - | - | - |  |  |  |  | B
| Forced outage (%) | - | - | -
| Planned outage (weeks per year) | - | - | -
| Technical lifetime (years) | 27 | 30 | 35 | 25 | 30 | 28 | 42 |  | 1
| Construction time (years) | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.1 | 0.5 |  | 1
| Space requirement (m2/kWe(AC)) | 5.1 | 4.5734 | 4.0721 | 4.4 | 6 | 4 | 5.5 | V | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 20.5479 | 21.1187 | 21.6895 | 17.4658 | 23.6301 | 18.4361 | 24.9429 | L,M | 1,2,3
| Capacity factor (%), incl. outages | 20.4452 | 21.0131 | 21.5811 | 18.4007 | 22.4897 | 19.4229 | 23.7392 | L,M,X | 1,2,3
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | C
| Minimum load (% of full load) | - | - | - | - | - | - | - | C
| Warm start-up time (hours) | - | - | - | - | - | - | - | C
| Cold start-up time (hours) | - | - | - | - | - | - | - | C
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 1.2 | 0.84 | 0.6 | 1.152 | 1.92 | 0.36 | 0.756 | E,R,S | 1,4,5,6,8,9
| - of which equipment | 80% | 75% | 70% | [5 empty] | 1,5,6
| - of which installation | 20% | 25% | 30% |  |  |  |  | W | 1,5,6
| Fixed O&M ($/MWe/year) | 4900 | 4400 | 3900 | 2500 | 7400 | 2000 | 5900 | Q | 1,5,6
| Variable O&M ($/MWh) | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0
Technology specific data
| Global horizontal irradiance (kWh/m2/y) | 1700 | 1700 | 1700 | 1300 | 2200 | 1300 | 2200 | F | 2,3
| DC/AC sizing factor (Wp/W) | 1.2 | 1.2 | 1.2 |  |  |  |  | G | 1,4
| Transposition Factor for fixed tilt system | 1.01 | 1.01 | 1.01 |  |  |  |  | H | 3
| Performance ratio | 0.86 | 0.9 | 0.92 |  |  |  |  | I | 1,4
| PV module conversion efficiency (%) | 0.205 | 0.23 | 0.26 |  |  |  |  | T | 1,4,6
| Inverter lifetime (years) | 12.5 | 15 | 15 | [5 empty] | 4
Output
| Full load hours (kWh/kW) | 1800 | 1850 | 1900 |  |  |  |  | J, L
| Peak power full load hours (kWh/kWp) | 1500 | 1550 | 1600 |  |  |  |  | K, L
Financial data
| PV module & inverter cost ($/Wp) | 0.68 | 0.44625 | 0.2975 | 0.6528 | 1.088 | 0.1785 | 0.37485 |  | 1,5,6
| Balance Of Plant cost ($/Wp) | 0.12 | 0.07875 | 0.0525 | 0.1152 | 0.192 | 0.0315 | 0.06615 |  | 1,5,6
| Installation and other cost ($/Wp) | 0.2 | 0.175 | 0.15 | 0.192 | 0.32 | 0.09 | 0.189 | W | 1,5,6
| Specific investment, total system ($/Wp) | 1 | 0.7 | 0.5 | 0.96 | 1.6 | 0.3 | 0.63 | E,R,S | 1,4,5,6,8,9
| Specific investment, total system (million $/MW) | 1.2 | 0.84 | 0.6 | 1.152 | 1.92 | 0.36 | 0.756 | P | 1,4,5,6,8,9
References:
1 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
2 | Data analysed from www.renewables.ninja for multiple locations in Indonesia.
3 | PVGIS © Europeen Communitees 2001-2012.
4 | The Danish Energy Agency, Technology data for generation of electricity and district heating, 2023.
5 | USAID, Panduan Perencanaan dan Pemanfaatan PLTS ATAP DI INDONESIA, 2020
6 | IRENA, Renewable Power Generation Costs in 2022, 2023
7 | IESR, Indonesia Solar Energy Outlook 2023
8 | World Energy Outlook 2022, IEA 2023
9 | IRENA, Future of Solar PV - Deployment, investment,technology, grid integration and socio-economic aspects, 2019
Notes:
A | Listed as MWe. The MWp will depend on the DC/AC siizing factor
B | See "PV module conversion efficiency (%)". The improvement in technology development is also captured in capacity factor, investment costs and space requirement.
C | The generation from a PV system reflects the yearly and daily variation in solar irradiation. It is possible to curtail solar, and this can be done rapidly.
E | Investment cost include the engineering, procurement and construction (EPC). See description under Methodology.
F | The global horizontal irradiation is a measure of the energy resource potential available and depends on the exact geographical location. 1700 kWh/m2 corresponds to a resource slightly above the median value in Java. The range of GHI across the country ranges from 1330 kWh/m2 to 2200 kWh/m2.
G | The DC/AC equals module peak capacity Wp divided by plant capacity We(output of the inverter). The sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity.
H | The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. In Indonesia the TF factor for fixed systems is very low, adding only 0-1 % to the production.
I | The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non- STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
J | The full load hours is defined as the peak full load hours*DC/AC sizing factor
K | The number of full load hours is calculated based on the other values in the table. The formula is: Peak full load hours = Global horizontal irradiance * transposition factor * performance ratio.
L | Capacity factor = Full load hours / 8760.
M | The capacity factor or full load hours depend greatly on the global horizontal irradiance at the specific plant site. For sites significantly different from the 1700 kWh/m2/year solar irradiation mentioned here, the caacity factors should be adjusted accordingly.
P | The “specific investment, total system per rated capacity W(AC)” is calculated as “specific investment, total system per Wp(DC)” multiplied by the sizing factor.
Q | The cost of O&M includes insurance and regular replacement of inverters, technical operation, preventive maintenance, commercial operation, corrective maintenance, insurance, greenkeeping and security. O&M costs are assumed to decrease slower than for equipments. Reported values have a wide range so a +/- 50% interval is suggested for the uncertainty intervals.
R | Invstment cost projections and future unertainty ranges are assumed to be similar to the ones for ground-mounted plants and is based on a continued cost redutions estimated from a number of sources, incl. ref. 1, 4, 8, 9.
S | For 2023, uncertainty ranges are based on cost spans of various sources.
T | PV module conversion efficiency (%) is the ration of the energy from the sun that hits the solar panel that is coverted into DC eletricity in the module. | Is the ration of the energy from the sun that hits the solar panel that is coverted into DC eletricity in the module
V | The space requirement is reduced because of the improved efficiency of the modules, assuming that total area decrese by only 95 % of the decreased demand for modul area.
W | The cost of labour and the installation performance is not expected to improve in the same extent as the costs for the equipment. Therefore, the share of installation cost would increase over the years.
X | Yearlly outage time is assumed to be 0,5 % equale approxemately 2 hour.

## Industrial PV
Technology
| Technology | PV Industrial scale, rooftop or ground mounted - grid connected
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for total power plant (kWe) | 100 | 100 | 100 |  |  |  |  | A | 1
| Electricity efficiency, net (%), name plate | - | - | - |  |  |  |  | B
| Electricity efficiency, net (%), annual average | - | - | - |  |  |  |  | B
| Forced outage (%) | - | - | -
| Planned outage (weeks per year) | - | - | -
| Technical lifetime (years) | 27 | 30 | 35 | 25 | 30 | 28 | 42 |  | 1
| Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 1.5 | 0.25 | 1 |  | 1
| Space requirement (1000 m2/MWe) | 5.1 | 4.5734 | 4.0721 | 4.4 | 6 | 4 | 5.5 | V | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 20.5479 | 21.1187 | 21.6895 | 16.0632 | 19.6327 | 18.1177 | 22.1439 | L,M | 1,2,7
| Capacity factor (%), incl. outages | 20.4452 | 21.0131 | 21.5811 | 18.4007 | 22.4897 | 19.4229 | 23.7392 | L,M,X | 1,2,7
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | C
| Minimum load (% of full load) | - | - | - | - | - | - | - | C
| Warm start-up time (hours) | - | - | - | - | - | - | - | C
| Cold start-up time (hours) | - | - | - | - | - | - | - | C
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 1.08 | 0.756 | 0.54 | 1.032 | 1.728 | 0.324 | 1.296 | E,R,S | 1,3,5,6,8,9
| - of which equipment | 80% | 75% | 70% |  |  |  |  | D | 1,5,6
| - of which installation | 20% | 25% | 30% |  |  |  |  | D,W | 1,5,6
| Fixed O&M ($/MWe/year) | 4700 | 4200 | 3700 | 2400 | 7100 | 1900 | 5600 | Q | 4,5
| Variable O&M ($/MWh) | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0
Technology specific data
| Global horizontal irradiance (kWh/m2/y) | 1700 | 1700 | 1700 | 1300 | 2200 | 1300 | 2200 | F,M | 1,2,7
| DC/AC sizing factor (Wp/We) | 1.2 | 1.2 | 1.2 |  |  |  |  | G | 1,5
| Transposition Factor for fixed tilt system | 1.01 | 1.01 | 1.01 |  |  |  |  | H | 7
| Performance ratio | 0.86 | 0.9 | 0.92 |  |  |  |  | I | 1,5
| PV module conversion efficiency (%) | 0.205 | 0.23 | 0.26 |  |  |  |  | T | 1,3,5
| Inverter lifetime (years) | 12.5 | 15 | 15 | [5 empty] | 5
Output
| Full load hours (kWh/kW) | 1800 | 1850 | 1900 |  |  |  |  | J,L
| Peak power full load hours (kWh/kWp) | 1500 | 1550 | 1600 |  |  |  |  | K,L
Financial data
| PV module & inverter cost ($/Wp) | 0.612 | 0.40163 | 0.26775 | 0.5848 | 0.9792 | 0.16065 | 0.6426 | D | 1,5,6
| Balance Of Plant cost ($/Wp) | 0.108 | 0.070875 | 0.04725 | 0.1032 | 0.1728 | 0.02835 | 0.1134 | D | 1,5,6
| Installation and other cost ($/Wp) | 0.18 | 0.1575 | 0.135 | 0.172 | 0.288 | 0.081 | 0.324 | D,W | 1,5,6
| Specific investment, total system ($/Wp) | 0.9 | 0.63 | 0.45 | 0.86 | 1.44 | 0.27 | 1.08 | E,R,S | 1,3,5,6,8,9
| Specific investment, total system (million $/MW) | 1.08 | 0.756 | 0.54 | 1.032 | 1.728 | 0.324 | 1.296 | P | 1,3,5,6,8,9
References:
1 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
2 | Data analysed from www.renewables.ninja for multiple locations in Indonesia.
3 | IRENA, Renewable Power Generation Costs in 2022, 2023
4 | Cirata 1 MW Solar PV O&M and Financial Perspective, Sharing Experience. PJB.
5 | The Danish Energy Agency, Technology data for generation of electricity and district heating, 2023.
6 | USAID, Panduan Perencanaan dan Pemanfaatan PLTS ATAP DI INDONESIA, 2020
7 | PVGIS © Europeen Communitees 2001-2012.
8 | World Energy Outlook 2022, IEA 2023
9 | IRENA, Future of Solar PV - Deployment, investment,technology, grid integration and socio-economic aspects, 2019
Notes:
A | Listed as MWe. The MWp will depend on the DC/AC siizing factor
B | See "PV module conversion efficiency (%)". The improvement in technology development is also captured in capacity factor, investment costs and space requirement.
C | The generation from a PV system reflects the yearly and daily variation in solar irradiation. It is possible to curtail solar, and this can be done rapidly.
D | The share of different elementes of the total system costs are based on a general assumption on a differences from utility scale systems, which is then applied to the full system costs.
E | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
F | The global horizontal irradiation is a measure of the energy resource potential available and depends on the exact geographical location. 1700 kWh/m2 corresponds to a resource slightly above the median value in Java. The range of GHI across the country ranges from 1330 kWh/m2 to 2200 kWh/m2.
G | The DC/AC equals module peak capacity Wp divided by plant capacity We(output of the inverter). The sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity.
H | The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. In Indonesia the TF factor for fixed systems is very low, adding only 0-1 % to the production.
I | The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non- STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
J | The full load hours is defined as the peak full load hours*DC/AC sizing factor
K | The number of full load hours is calculated based on the other values in the table. The formula is: Peak full load hours = Global horizontal irradiance * transposition factor * performance ratio.
L | Capacity factor = Full load hours / 8760.
M | The capacity factor or full load hours depend greatly on the global horizontal irradiance at the specific plant site. For sites significantly different from the 1700 kWh/m2/year solar irradiation mentioned here, the caacity factors should be adjusted accordingly.
P | The “specific investment, total system per rated capacity W(AC)” is calculated as “specific investment, total system per Wp(DC)” multiplied by the sizing factor.
Q | The cost of O&M includes insurance and regular replacement of inverters, technical operation, preventive maintenance, commercial operation, corrective maintenance, insurance, greenkeeping and security. O&M costs are assumed to decrease slower than for equipments. Reported values have a wide range so a +/- 50% interval is suggested for the uncertainty intervals.
R | Invstment cost projections and future unertainty ranges are assumed to be similar to the ones for ground-mounted plants and is based on a continued cost reduction estimated from a number of sources, incl. ref. 1, 4, 8, 9.
S | For 2023, uncertainty ranges are based on cost spans of various sources
T | PV module conversion efficiency (%) is the ration of the energy from the sun that hits the solar panel that is coverted into DC eletricity in the module. | Is the ration of the energy from the sun that hits the solar panel that is coverted into DC eletricity in the module
V | The space requirement is reduced because of the improved efficiency of the modules, assuming that total area decrese by only 95 % of the decreased demand for modul area.
W | The cost of labour and the installation performance is not expected to improve in the same extent as the costs for the equipment. Therefore, the share of installation cost would increase over the years.
X | Yearlly outage time is assumed to be 0,5 % equale approxemately 2 hour.

## Floating PV
Technology
| Technology | PV Floating, utility-scale, grid connected
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for total power plant (MWe) | 30 | 80 | 100 |  |  |  |  | A | 1
| Electricity efficiency, net (%), name plate | - | - | - |  |  |  |  | B
| Electricity efficiency, net (%), annual average | - | - | - |  |  |  |  | B
| Forced outage (%) | - | - | -
| Planned outage (weeks per year) | - | - | -
| Technical lifetime (years) | 27 | 30 | 35 | 25 | 30 | 28 | 42 |  | 1
| Construction time (years) | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.2 | 1 |  | 1
| Space requirement (1000 m2/MWe) | 8.3 | 7.488 | 6.7104 | 7.2 | 10 | 5 | 9 | V | 9
Additional data for non thermal plants
| Capacity factor (%), theoretical | 21.1187 | 21.6895 | 22.8311 | 14 | 22 | 16 | 23 | M,L | 1,2,4
| Capacity factor (%), incl. outages | 21.0131 | 21.5811 | 22.7169 | 14 | 22 | 16 | 23 | M,L,X | 1,2,4
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | C
| Minimum load (% of full load) | - | - | - | - | - | - | - | C
| Warm start-up time (hours) | - | - | - | - | - | - | - | C
| Cold start-up time (hours) | - | - | - | - | - | - | - | C
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 1.2 | 0.7392 | 0.48 | 1.15 | 1.9 | 0.25 | 0.6 | E,R,S | 1,3,8,11,12
| - of which equipment | 90% | 86% | 82% | [5 empty] | 1,3,6
| - of which installation | 10% | 14% | 18% |  |  |  |  | W | 1,3,6
| Fixed O&M ($/MWe/year) | 9000 | 7500 | 6100 | 4500 | 13500 | 3100 | 9200 | Q | 3
| Variable O&M ($/MWh) | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0
Technology specific data
| Global horizontal irradiance (kWh/m2/y) | 1700 | 1700 | 1700 | 1300 | 2200 | 1300 | 2200 | F,M | 1,2,7
| DC/AC sizing factor (Wp/W) | 1.2 | 1.2 | 1.2 |  |  |  |  | G | 1,5
| Transposition Factor for fixed tilt system | 1.01 | 1.01 | 1.01 |  |  |  |  | H | 7
| Performance ratio | 0.903 | 0.945 | 0.966 |  |  |  |  | I | 1,4,5
| PV module conversion efficiency (%) | 0.205 | 0.23 | 0.26 |  |  |  |  | T | 1,3,5
| Inverter lifetime (years) | 12.5 | 15 | 15 | [5 empty] | 1,5
Output
| Full load hours (kWh/kW) | 1850 | 1900 | 2000 |  |  |  |  | J, L
| Peak power full load hours (kWh/kWp) | 1550 | 1600 | 1650 |  |  |  |  | K, L
Financial data
| PV module & inverter cost ($/Wp) | 0.54 | 0.31786 | 0.1968 | 0.513 | 0.864 | 0.11808 | 0.246 |  | 1,3,6
| Balance Of Plant cost ($/Wp) | 0.36 | 0.2119 | 0.1312 | 0.342 | 0.576 | 0.07872 | 0.0615 |  | 1,3,6
| Installation and other cost ($/Wp] | 0.1 | 0.08624 | 0.072 | 0.095 | 0.16 | 0.0432 | 0.1925 |  | 1,3,6
| Specific investment, total system ($/Wp) | 1 | 0.616 | 0.4 | 0.95 | 1.6 | 0.24 | 0.5 | E,R,S | 1,3,8,11,12
| Specific investment, total system (M$/MW) | 1.2 | 0.7392 | 0.48 | 1.14 | 1.92 | 0.288 | 0.6 | P | 1,3,8,11,12
References:
1 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
2 | Data analysed from www.renewables.ninja for multiple locations in Indonesia.
3 | IRENA, Renewable Power Generation Costs in 2022, 2023
4 | Benefits of pairing floating solar photovoltaics with hydropower reservoirs in Europe 2023, https://www.sciencedirect.com/science/article/pii/S136403212200870X?via%3Dihub
5 | The Danish Energy Agency, Generation of electricity and district heating, 2020.
6 | M Rosa-Clot and G.M. Tina, Levelized Cost of Energy (LCOE) Analysis
7 | PVGIS © Europeen Communitees 2001-2012.
8 | World Energy Outlook 2022, IEA 2023
9 | Iselectric brochure. Last accessed: September 2020
10 | The Energy and Resources Institute, Floating Solar Photovoltaic (FSPV): A Third Pillar to Solar PV Sector?, 2019
11 | A A Untoro et al, Study of Economic Viability of Floating Photovoltaic Electric Power in Indonesia, 2021
12 | International Bank for Reconstruction and Development, Where Sun Meets Water: Floating Solar Market Report, 2018
13 | NREL, Floating Photovoltaic System Cost Benchmark: Q1 2021 Installations on Artificial Water Bodies, 2021
14 | IRENA, Future of Solar PV - Deployment, investment,technology, grid integration and socio-economic aspects, 2019
Notes:
A | Listed as MWe. The MWp will depend on the DC/AC siizing factor
B | See "PV module conversion efficiency (%)". The improvement in technology development is also captured in capacity factor, investment costs and space requirement.
C | The generation from a PV system reflects the yearly and daily variation in solar irradiation. It is possible to curtail solar, and this can be done rapidly.
E | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
F | The global horizontal irradiation is a measure of the energy resource potential available and depends on the exact geographical location. 1700 kWh/m2 corresponds to a resource slightly above the median value in Java. The range of GHI across the country ranges from 1330 kWh/m2 to 2200 kWh/m2.
G | The DC/AC equals module peak capacity Wp divided by plant capacity We(output of the inverter). The sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity.
H | The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. In Indonesia the TF factor for fixed systems is very low, adding only 0-1 % to the production.
I | The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. For Floating PV, a 5% improvement in performance is included due to effects of cooling from the water service, as described in reference 4. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non- STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
J | The full load hours is defined as the peak full load hours*DC/AC sizing factor
K | The number of full load hours is calculated based on the other values in the table. The formula is: Peak full load hours = Global horizontal irradiance * transposition factor * performance ratio.
L | Capacity factor = Full load hours / 8760.
M | The capacity factor or full load hours depend greatly on the global horizontal irradiance at the specific plant site. For sites significantly different from the 1700 kWh/m2/year solar irradiation mentioned here, the caacity factors should be adjusted accordingly.
P | The “specific investment, total system per rated capacity W(AC)” is calculated as “specific investment, total system per Wp(DC)” multiplied by the sizing factor.
Q | The cost of O&M includes insurance and regular replacement of inverters, technical operation, preventive maintenance, commercial operation, corrective maintenance, insurance, greenkeeping and security. O&M costs are assumed to decrease slower than for equipments. Reported values have a wide range so a +/- 50% interval is suggested for the uncertainty intervals.
R | Invstment cost projections and future unertainty ranges are assumed to be similar to the ones for ground-mounted plants and are based on a continued cost reduction estimated from a number of sources.
S | For 2023, uncertainty ranges are based on cost spans of various sources.
T | PV module conversion efficiency (%) is the ration of the energy from the sun that hits the solar panel that is coverted into DC eletricity in the module. | Is the ration of the energy from the sun that hits the solar panel that is coverted into DC eletricity in the module
U | Estimations of space requirements are based on the mapping of the average polygonal area occupied by PV arrays and electrical equipments like inverter pad of existing floating PV plants in Indonesia and Singapore.
V | The space requirement is reduced because of the improved efficiency of the modules, assuming that total area decrese by only 90 % of the decreased demand for module area.
W | The cost of labour and the installation performance is not expected to improve in the same extent as the costs for the equipment. Therefore, the share of installation cost would increase over the years. The cost of instalation is expected to be 10 % lower than for Ground mounted, based on [13]
X | Yearlly outage time is assumed to be 0,5 % equale approxemately 2 hours.

## Wind Onshore
Technology
| Technology | Wind power - Onshore
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 3.5 | 4.5 | 6 | [5 empty] | 3
| Generating capacity for total power plant (MWe) | 70 | 90 | 120 | [5 empty] | 1
| Rotor Diameter (m) | 139.1955 | 178.4124 | 225.6758
| Hub Height (m) | 110 | 150 | 180
| Specific Power (W/m2) | 230 | 180 | 150
| Forced outage (%) | 2.5 | 2 | 2 | [5 empty] | 3
| Planned outage (weeks per year) | 0.16 | 0.16 | 0.16 | 0.05 | 0.26 | 0.05 | 0.26 |  | 3
| Technical lifetime (years) | 27 | 30 | 30 | 25 | 35 | 25 | 40 |  | 3
| Construction time (years) | 1.5 | 1.5 | 1.5 | [5 empty] | 1
| Space requirement (1000 m2/MWe) | 14 | 14 | 14 | [5 empty] | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 28 | 32 | 36 | 15 | 35 | 15 | 40 | A,B | 6,7
| Capacity factor (%), incl. outages | 27.216 | 31.2635 | 35.1714 | [5 empty] | 3
Ramping configurations
| Ramping (% per minute) | - | - | - |  |  |  |  | E
| Minimum load (% of full load) | - | - | - |  |  |  |  | E
| Warm start-up time (hours) | - | - | -
| Cold start-up time (hours) | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 1.65 | 1.2 | 0.95 | 1.2 | 2.35 | 0.6 | 1.85 | A,D,F | 1,5,8
| - of which equipment | 65% | 65% | 65% |  |  |  |  | C | 2,3
| - of which installation | 35% | 35% | 35% |  |  |  |  | C | 2,3
| Fixed O&M ($/MWe/year) | 40000 | 36000 | 30000 | 30000 | 70000 | 25000 | 60000 | G | 4,5,9
| Variable O&M ($/MWh) | 0 | 0 | 0 | [5 empty] | 4,5
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0
References:
1 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
2 | IRENA, Renewable Power Generation Costs in 2022, 2023
3 | Danish Energy Agency, 2012/2016.Technology Data on Energy Plants - Generation of Electricity and District Heating, Energy Storage and Energy Carrier Generation and Conversion
4 | IEA Wind Task 26, 2015, "Wind Technology, Cost, and Performance Trends in Denmark, Germany, Ireland, Norway, the EU, and the USA: 2007–2012".
5 | NREL ATB 2023
6 | Renewables Ninja
7 | Global Wind Atlas
8 | ASEAN Centre for Energy, China Renewable Energy Engineering Institute. "Research on Applicantions of Low Wind Speed Power in ASEAN". Nov 2021.
9 | Stehly, Tyler and Patrick Duffy. 2021. 2020 Cost of Wind Energy Review. Golden, CO: National Renewable Energy Laboratory. NREL/TP-5000-81209. https://www.nrel.gov/docs/fy22osti/81209.pdf.
Notes:
A | The onshore turbine assumed in this technology catalog is a class III turbine, as the onshore wind speeds in Indonesia are very low.
B | The capacity factor provided represents the expected performance at the best onshore wind locations in Indonesia (where average wind speeds are above 6 m/s), which are found almost exclusicly on Jawa. However, the majority of Indonesia as very low wind speeds, where capacity factor below 20% should be expected
C | Equipment: Cost of turbines including transportation. Installation: Electricical infrastructure of turbine, civil works, grid connection, planning and management. The split of cost may vary considerably from project to project.
D | The CapEx decrease comes from the NREL ATB's moderate scenario
E | With sufficient wind resource available (wind speed higher than 4-6 m/s and lower than 25-30 m/s) wind turbines can always provide down regulation, and in many cases also up regulation, provided the turbine is running in power-curtailed mode (i.e. with an output which is deliberately set below the possible power based on the available wind).
F | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 10-15% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.
G | Fixed O&M includes cost of land

## Small wind onshore
Technology
| Technology | Wind power - Small onshore wind turbines < 1 MW
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 0.85 | 0.9 | 0.95 | [5 empty] | 6
| Generating capacity for total power plant (MWe) | 12.75 | 18 | 19 | [5 empty] | 5
| Electricity efficiency, net (%), name plate | 100 | 100 | 100 |  |  |  |  | A
| Electricity efficiency, net (%), annual average | 100 | 100 | 100
| Forced outage (%) | 0.03 | 0.025 | 0.02
| Planned outage (weeks per year) | 0.16 | 0.16 | 0.16 | 0.05 | 0.26 | 0.05 | 0.26 |  | 3
| Technical lifetime (years) | 27 | 30 | 30 | 25 | 35 | 25 | 40 |  | 3
| Construction time (years) | 1 | 1 | 1 | [5 empty] | 5,6
| Space requirement (1000 m2/MWe) | 14 | 14 | 14 | [5 empty] | 1,6
Additional data for non thermal plants
| Capacity factor (%), theoretical | 28 | 32 | 36 | 15 | 35 | 15 | 40 | B | 2
| Capacity factor (%), incl. outages | 27.216 | 31.2635 | 35.1714
Ramping configurations
| Ramping (% per minute) | - | - | - |  |  |  |  | F
| Minimum load (% of full load) | - | - | - |  |  |  |  | F
| Warm start-up time (hours) | - | - | -
| Cold start-up time (hours) | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 4.2 | 3.57 | 3.024 | 3.2 | 5.3 | 2.3 | 3.8 | D,E | 5, 6
| - of which equipment | 55% | 55% | 55% |  |  |  |  | C
| - of which installation | 45% | 45% | 45% |  |  |  |  | C
| Fixed O&M ($/MWe/year) | 83448 | 70900 | 60100 | 62600 | 104300 | 75100 | 45100 | E | 4
| Variable O&M ($/MWh) | 0 | 0 | 0 | [5 empty] | 4
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0
References:
1 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
2 | Wind Energy Resources of Indonesia 2014-2017, EMD International A/S, Denmark, financed by the Environmental Support Programme 3 (ESP3) / Danida.
3 | Danish Energy Agency, 2012/2016.Technology Data on Energy Plants - Generation of Electricity and District Heating, Energy Storage and Energy Carrier Generation and Conversion
4 | IEA Wind Task 26, 2015, "Wind Technology, Cost, and Performance Trends in Denmark, Germany, Ireland, Norway, the EU, and the USA: 2007–2012".
5 | Case: Faroe Islands, Húsahagi 2014
6 | Case: Kenya, Lake Turkana, 2014-2017
Notes:
A | The efficiency is defined as 100%. The improvement in technology development is captured in capacity factor, investment cost and space requirement.
B | The capacity factor provided represent an average of good locations in Indonesia, see presentation in catalogue text. As mentioned in the description, generelly speaking, the wind resource in Indonesia is scarce.
C | Equipment: Cost of turbines including transportation. Installation: Electricical infrastructure of turbine, civil works, grid connection, planning and management. The split of cost may vary considerably from project to project.
D | The IEA expects approximately a doubling of the accumulated wind power capacity between 2020 and 2030 and 4-5 times more by 2050 compared to 2020. Assuming a learning of 12.5 % per annum this yields a cost reduction of approx. 13 % by 2030 and approx. 25 % by 2050.
E | Uncertainty (Upper/Lower) is estimated as +/- 25%.
F | With sufficient wind resource available (wind speed higher than 4-6 m/s and lower than 25-30 m/s) wind turbines can always provide down regulation, and in many cases also up regulation, provided the turbine is running in power-curtailed mode (i.e. with an output which is deliberately set below the possible power based on the available wind).

## Wind Offshore
Technology
| Technology | Wind power - Offshore
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 8 | 16 | 20 | [5 empty] | 3
| Generating capacity for total power plant (MWe) | 240 | 480 | 600
| Rotor Diameter (m) | 170.5949 | 248.4609 | 296.3269
| Hub Height (m) | 107.2974 | 146.2305 | 170.1634
| Specific Power (W/m2) | 350 | 330 | 290
| Forced outage (%) | 0.04 | 0.03 | 0.03 | [5 empty] | 3
| Planned outage (weeks per year) | 0.16 | 0.16 | 0.16 | [5 empty] | 3
| Technical lifetime (years) | 27 | 30 | 30 | 20 | 35 | 20 | 35 |  | 3
| Construction time (years) | 3 | 2.5 | 2.5 | 1.5 | 4 | 1.5 | 4 |  | 3
| Space requirement (1000 m2/MWe) | 185 | 185 | 185 | 168 | 204 | 168 | 204 |  | 3
Additional data for non thermal plants
| Capacity factor (%), theoretical | 0.35 | 0.37 | 0.41 |  |  |  |  | B | 2,6,7
| Capacity factor (%), incl. outages | 0.33497 | 0.3578 | 0.39648
Ramping configurations
| Ramping (% per minute) | - | - | - |  |  |  |  | F
| Minimum load (% of full load) | - | - | - |  |  |  |  | F
| Warm start-up time (hours) | - | - | -
| Cold start-up time (hours) | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 4.1 | 3.567 | 2.87 | 3.5 | 4.5 | 1.55 | 3.2 | D,G | 3,5
| - of which equipment | 45% | 45% | 45% |  |  |  |  | C | 3
| - of which installation | 55% | 55% | 55% |  |  |  |  | C | 3
| Fixed O&M ($/MWe/year) | 118767.888 | 99791.0473 | 81289.9276 | 109000 | 123000 | 61000 | 95000 |  | 5
| Variable O&M ($/MWh) | 5.5 | 4.8 | 3.9 | 3.4 | 5.8 | 2.7 | 4.3 |  | 4
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0
References:
1 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
2 | Wind Energy Resources of Indonesia 2014-2017, EMD International A/S, Denmark, financed by the Environmental Support Programme 3 (ESP3) / Danida.
3 | Danish Energy Agency, 2012/2016.Technology Data on Energy Plants - Generation of Electricity and District Heating, Energy Storage and Energy Carrier Generation and Conversion
4 | IEA Wind Task 26, 2015, "Wind Technology, Cost, and Performance Trends in Denmark, Germany, Ireland, Norway, the EU, and the USA: 2007–2012".
5 | NREL's Aunnual Technology Baseline ATB 2023
6 | Renewables Ninja
7 | Global Wind Atlas
Notes:
A | The efficiency is defined as 100%. The improvement in technology development is captured in capacity factor, investment cost and space requirement.
B | The capacity factor provided represent an average of the absolute best fixed-bottom offshore wind locations in Indonesia (specifically south of Papua)
C | Equipment: Cost of turbines including transportation. Installation: Electricical infrastructure of turbine, civil works, grid connection, planning and management. The split of cost may vary considerably from project to project.
D | The IEA expects approximately a doubling of the accumulated wind power capacity between 2020 and 2030 and 4-5 times more by 2050 compared to 2020. Assuming a learning of 12.5 % per annum this yields a cost reduction of approx. 13 % by 2030 and approx. 30 % by 2050.
E | Uncertainty (Upper/Lower) is estimated as +/- 25%.
F | With sufficient wind resource available (wind speed higher than 4-6 m/s and lower than 25-30 m/s) wind turbines can always provide down regulation, and in many cases also up regulation, provided the turbine is running in power-curtailed mode (i.e. with an output which is deliberately set below the possible power based on the available wind).
G | For 2023, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 10-15% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.

## Wind offshore floating
Technology
| Technology | Wind power - Floating offshore
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 7 | 16 | 20 | [5 empty] | 1,2,5
| Generating capacity for total wind farm (MWe) | 35 | 500 | 1000 | [5 empty] | 1,5
Electricity efficiency, net (%), name plate
Electricity efficiency, net (%), annual average
| Forced outage (%) | 6 | 4 | 4 | [5 empty] | 3
| Planned outage (%) | 0.6 | 0.6 | 0.6 | [5 empty] | 3
| Technical lifetime (years) | 20 | 25 | 30 | [5 empty] | 4
| Construction time (years) | 3 | 2.5 | 2.5 | [5 empty] | 4
| Space requirement (1000 m2/MWe) | 185 | 185 | 185 | [5 empty] | 4
Additional data for non thermal plants
| Capacity factor (%), theoretical | 36% | 38% | 40% | - | - | - | - | D
| Capacity factor (%), incl. outages | 33.62% | 36.25% | 38.16% | - | - | - | -
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | B
| Minimum load (% of full load) | - | - | - | - | - | - | - | B
| Warm start-up time (hours) | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | -
Environment
PM 2.5 (gram per Nm3)
SO2 (degree of desulphuring, %)
NOX (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 5.5 | 4 | 3 | 4 | 7 | 2 | 4 |  | 3,4,5
| - of which equipment | 80% | 65% | 60% |  |  |  |  | A
| - of which installation | 20% | 35% | 40% |  |  |  |  | A
| Fixed O&M ($/MWe/year) | 155000 | 125000 | 65000 | 140000 | 180000 | 52000 | 81000 | C | 4,5
| Variable O&M ($/MWh) | - | - | - |  |  |  |  | C | 4,5
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0
Technology specific data
| Rotor diameter (m) | 150 | 200 | 250 | [5 empty] | 1
| Hub height (m) | 100 | 170 | 180 | [5 empty] | 1
| Specific power (W/m2) | 396.119 | 509.2958 | 407.4367 | [5 empty] | 1
| Availability (%) | 94 | 96 | 96 | [5 empty] | 3
References:
1 | Global Wind Energy Council, 2020, "Global Offshore Wind Report 2020"
2 | BVG Associates, 2020, "Offshore wind roadmap for Vietnam"
3 | Borg M. et al., Qualification of innovative floating substructures for 10MW wind turbines and water depths greater than 50m, 2019
4 | World Bank, Offshore wind roadmap for Vietnam: Preliminary Findings, 2020.
5 | AEGIR, Vietnam site LCOE screening, 2020.
6 | M. Aquilina, 2014, "Cost Modelling of Floating Wind Farms with Upscaled Rotors in Maltese Waters"
Notes:
A | Equipment: Cost of turbines including transportation. Installation: Electricical infrastructure of turbine, civil works, grid connection, planning and management. The split of cost may vary considerably from project to project.
B | With sufficient wind resource available (wind speed higher than 4-6 m/s and lower than 25-30 m/s) wind turbines can always provide down regulation, and in many cases also up regulation, provided the turbine is running in power-curtailed mode (i.e. with an output which is deliberately set below the possible power based on the available wind).
C | Operation and maintenance is entirely allotted to the fixed part.
D | In Indonesia, floating offshore sites - further from shore - have only marginally better average wind speeds as fixed-bottom sites, which are already quite low relative to globally advantageous locations.

## Tidal Impoundment
Technology
| Technology | Tidal power - Impoundment Type
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1 | 10 | 25 | 1 | 25 | 1 | 25 | A | 3
| Generating capacity for total power plant (MWe) | 30 | 100 | 150 | 10 | 300 | 10 | 300 | B | 3
| Electricity efficiency, net (%), name plate | 90 | 90 | 90 | 85 | 95 | 85 | 95 | F | 5
| Electricity efficiency, net (%), annual average | 90 | 90 | 90 | 85 | 95 | 85 | 95 | F | 5
| Forced outage (%) | 4 | 4 | 4 | 2 | 6 | 2 | 6
Planned outage (weeks per year)
| Technical lifetime (years) | 40 | 40 | 50 | 30 | 120 | 30 | 120 | C | 2
| Construction time (years) | 5 | 5 | 4 | 4 | 6 | 4 | 6 |  | 3,5
| Space requirement (1000 m2/MWe) | 0.2 | 0.2 | 0.2 | 0.1 | 0.3 | 0.1 | 0.3 | D
Additional data for non thermal plants
| Capacity factor (%), theoretical | 35 | 35 | 40 | 35 | 40 | 35 | 40 | E
Capacity factor (%), incl. outages
Ramping configurations
| Ramping (% per minute) | 50 | 50 | 50 | 30 | 100 | 30 | 100 | G
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 | G
| Cold start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 | G
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 5.8 | 5.4 | 5.4 | 3.1 | 8 | 3.1 | 8 | E | 1,2,4
- of which equipment
- of which installation
| Fixed O&M ($/MWe/year) | 75048 | 66250 | 37842 | 24804 | 76320 | 24804 | 76320 | E | 1,2,3,4
Variable O&M ($/MWh)
Start-up costs ($/MWe/start-up)
References:
1 | DECC GOV.UK, “The UK 2050 Calculator: Tidal Range Cost Data,” 2011.
2 | Ernst & Young, “Cost of and financial support for wave, tidal stream and tidal range generation in the UK,” 2010
3 | IRENA, “Tidal Energy Technology Brief,” 2014
4 | Pacific Northwest National Laboratory (PNNL), Tethys
5 | Tatiana Montllonch Araquistain, Tidal Power: Economic and Technological assessment.
Notes:
A | Based on various projects and company datasheets. The turbine size can vary from project to project based on requirement. The Sihwa Lake project in Korea has 25.4 MW turbines.
B | The capacity is strongly dependent on resources available and shape of coastline. Although a lot of proposed plants are much larger in size, with some being over 2 GW as well, the capacity shown here is based on deployment of plants so far.
C | Actual operational life can be upto 120 years. However, lifetime is taken as 40 years, since there can be significant re-fitting costs after 40 years and discounted cash flows are insignificant after 40 years.
D | Based on information of proposed plants.
E | The projections here are assuming that with increased deployment and improved technology the values will improve within the range estimated.
F | Bulb type turbines are commonly used for tidal impoundment plants. The value here is estimated based on efficiencies of bulb type water turbines.
G | Considered as similar to Hydro

## Tidal Stream
Technology
| Technology | Tidal power - Stream Type
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1 | 2 | 2 | 0.1 | 6 | 1 | 6 | A | 3,5
| Generating capacity for total power plant (MWe) | 10 | 150 | 150 | 1 | 400 | 1 | 400 | A | 3,5
| Electricity efficiency, net (%), name plate | 90 | 92 | 95 | 87 | 97 | 87 | 97 | B | 2,3,5
| Electricity efficiency, net (%), annual average | 90 | 92 | 95 | 87 | 97 | 87 | 97 | B | 2,3,5
| Forced outage (%) | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 2
Planned outage (weeks per year)
| Technical lifetime (years) | 25 | 25 | 30 | 20 | 30 | 20 | 30 | B
| Construction time (years) | 3 | 2 | 2 |  |  |  |  | C
Space requirement (1000 m2/MWe)
Additional data for non thermal plants
| Capacity factor (%), theoretical | 33 | 35 | 37 | 33 | 40 | 35 | 40 | B | 1,2,4
| Capacity factor (%), incl. outages | 33 | 35 | 37 | 33 | 40 | 35 | 40 | B | 1,2,4
Ramping configurations
| Ramping (% per minute) | - | - | -
| Minimum load (% of full load) | - | - | -
| Warm start-up time (hours) | - | - | -
| Cold start-up time (hours) | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 5.6 | 4.9 | 3.6 | 3.2 | 7.5 | 2.1 | 7.5 | B | 1,2,3
| - of which equipment | 87% | 87% | 87% | 83% | 91% | 83% | 91% |  | 1,2
| - of which installation | 13% | 13% | 13% | 9% | 17% | 9% | 17% |  | 1,2
| Fixed O&M ($/MWe/year) | 299980 | 243800 | 120840 | 98580 | 436720 | 98580 | 436720 | B | 1,2
| Variable O&M ($/MWh) | 12 | 9 | 8 | [5 empty] | 4
Start-up costs ($/MWe/start-up)
References:
1 | Ernst & Young, “Cost of and financial support for wave, tidal stream and tidal range generation in the UK,” 2010.
2 | Ocean Energy Systems - OES (IEA), “International Levelised Cost of Energy for Ocean Energy Technologies,” 2015.
3 | SIMEC Atlantis Energy, Projects
4 | UK Govt., Electricity Generation Costs 2020 (back calculation from LCOE values)
5 | Pacific Northwest National Laboratory (PNNL), Tethys
Notes:
A | Projects are in the early stages os turbines and capacities are smaller. Larger projects are expected to be executed in smaller capacity phases.
B | The projections here are assuming that with increased deployment and improved technology the values will improve within the range estimated.
C | Estimated based on MeyGen tidal stream project

## Coal Subcritical
Technology
Pollution Prevention and Abatement Handbook, 1998: Toward Cleaner Production, Bind 777
| Technology | Subcritical coal power plant
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 150 | 150 | 150 | 7 | 660 | 100 | 660 | I | 1
| Generating capacity for total power plant (MWe) | 300 | 300 | 300 | 7 | 2640 | 100 | 2640 | I | 1
| Electricity efficiency, net (%), name plate | 35 | 36 | 37 | 30 | 38 | 33 | 39 |  | 1,2,3
| Electricity efficiency, net (%), annual average | 34 | 35 | 36 | 29 | 37 | 32 | 38 |  | 1,2,3
| Forced outage (%) | 7 | 5 | 3 | 5 | 20 | 2 | 7 | A | 1
| Planned outage (weeks per year) | 6 | 5 | 3 | 3 | 8 | 2 | 4 | A | 1
| Technical lifetime (years) | 30 | 30 | 30 | 25 | 40 | 25 | 40 |  | 1
| Construction time (years) | 3 | 3 | 3 | 2 | 4 | 2 | 4 |  | 1
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 3.5 | 3.5 | 3.5 | 2 | 4 | 2 | 4 | B | 1
| Minimum load (% of full load) | 40 | 40 | 40 | 25 | 50 | 20 | 40 | A | 1
| Warm start-up time (hours) | 3 | 3 | 3 | 1 | 5 | 1 | 5 | B | 1
| Cold start-up time (hours) | 8 | 8 | 8 | 5 | 12 | 5 | 12 | B | 1
Environment
| PM 2.5 (mg per Nm3) | 150 | 100 | 100 | 50 | 150 | 20 | 100 | A,F | 2,4
| SO2 (degree of desulphuring, %) | 73 | 80 | 95 | 73 | 95 | 73 | 95 | A,C,D | 2,4
| NOX (g per GJ fuel) | 263 | 150 | 38 | 263 | 263 | 263 | 263 | A,D | 2,4
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 1.88 | 1.82 | 1.76 | 1.14 | 1.94 | 1.14 | 1.938 | E,H | 1,3
- of which equipment
- of which installation
| Fixed O&M ($/MWe/year) | 51600 | 50000 | 48550 | 38750 | 64500 | 36500 | 60800 | G | 1,3
| Variable O&M ($/MWh) | 1.5 | 1.45 | 1.4 | 1 | 1.8 | 1 | 1.7 | G | 1,3
| Start-up costs ($/MWe/start-up) | 125.4 | 125.4 | 125.4 | 57 | 228 | 57 | 228 |  | 5
References:
1 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
2 | Platts Utility Data Institute (UDI) World Electric Power Plant Database (WEPP)
3 | Learning curve approach for the development of financial parameters.
4 | Maximum emission from Minister of Environment Regulation 21/2008
5 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
Notes:
A | Assumed gradidual improvement to international standard in 2050.
B | Assumed no improvement for regulatory capability.
C | Indonesian sulphur content in coal is up to 360 g/GJ. Conversion factor 0.35 to mg/Nm3 yields 1030 mg/Nm3. With a max of 750 mg/Nm3 then gives a % of desulphuring of 73%.
D | Calculated from a max of 750 mg/Nm3 to g/GJ (conversion factor 0.35 from Pollution Prevention and Abatement Handbook, 1998)
E | For economy of scale a proportionality factor, a, of 0.8 is suggested.
F | Uncertainty Upper is from regulation. Lower is from current standards in Japan (2020) and South Korea (2050).
G | Uncertainty (Upper/Lower) is estimated as +/- 25%.
H | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
I | Based on data collection from Indonesian projects

## Coal Supercritical
Technology
Pollution Prevention and Abatement Handbook, 1998: Toward Cleaner Production, Bind 777
| Technology | Supercritical coal power plant
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 600 | 600 | 600 | 250 | 800 | 250 | 800 | I | 1
| Generating capacity for total power plant (MWe) | 600 | 600 | 600 | 250 | 800 | 250 | 800 | I | 1
| Electricity efficiency, net (%), name plate | 38 | 39 | 40 | 33 | 40 | 35 | 42 |  | 1
| Electricity efficiency, net (%), annual average | 37 | 38 | 39 | 33 | 40 | 35 | 42 |  | 1
| Forced outage (%) | 7 | 6 | 3 | 5 | 15 | 2 | 7 | A | 1
| Planned outage (weeks per year) | 7 | 5 | 3 | 3 | 8 | 2 | 4 | A | 1
| Technical lifetime (years) | 30 | 30 | 30 | 25 | 40 | 25 | 40 |  | 1
| Construction time (years) | 4 | 3 | 3 | 3 | 5 | 2 | 4 | A | 1
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 4 | 4 | 4 | 3 | 4 | 3 | 4 | B | 1
| Minimum load (% of full load) | 40 | 40 | 40 | 25 | 50 | 20 | 40 | A | 1
| Warm start-up time (hours) | 4 | 4 | 4 | 2 | 5 | 2 | 5 | B | 1
| Cold start-up time (hours) | 12 | 12 | 12 | 6 | 15 | 6 | 12 | B | 1
Environment
| PM 2.5 (mg per Nm3) | 150 | 100 | 100 | 50 | 150 | 20 | 100 | F | 2,4
| SO2 (degree of desulphuring, %) | 73 | 73 | 73 | 73 | 95 | 73 | 95 | C,D | 2,4
| NOX (g per GJ fuel) | 263 | 263 | 263 | 263 | 263 | 263 | 263 | D | 2,4
| CH4 (g per GJ fuel) | - | - | - | - | - | - | -
| N2O (g per GJ fuel) | - | - | - | - | - | - | -
Financial data
| Nominal investment (M$/MWe) | 1.6 | 1.55 | 1.5 | 1.2 | 2 | 1.13 | 1.88 | E,G,H | 1,3,6
- of which equipment
- of which installation
| Fixed O&M ($/MWe/year) | 47000 | 45600 | 44100 | 35200 | 58700 | 33000 | 55200 | G | 1,3,6
| Variable O&M ($/MWh) | 1.4 | 1.35 | 1.3 | 1 | 1.7 | 1 | 1.6 | G | 1,3
| Start-up costs ($/MWe/start-up) | 57 | 57 | 57 | [5 empty] | 5
References:
1 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
2 | Platts Utility Data Institute (UDI) World Electric Power Plant Database (WEPP)
3 | Learning curve approach for the development of financial parameters.
4 | Maximum emission from Minister of Environment Regulation 21/2008
5 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
6 | IEA, World Energy Outlook, 2023
Notes:
A | Assumed gradidual improvement to international standard in 2050.
B | Assumed no improvement for regulatory capability.
C | Indonesian sulphur content in coal is up to 360 g/GJ. Conversion factor 0.35 to mg/Nm3 yields 1030 mg/Nm3. With a max of 750 mg/Nm3 then gives a % of desulphuring of 73%.
D | Calculated from a max of 750 mg/Nm3 to g/GJ (conversion factor 0.35 from Pollution Prevention and Abatement Handbook, 1998)
E | For economy of scale a proportionality factor, a, of 0.85 is suggested.
F | Uncertainty Upper is from regulation. Lower is from current standards in Japan (2020) and South Korea (2050).
G | Uncertainty (Upper/Lower) is estimated as +/- 25%.
H | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
I | Based on data collection from Indonesian projects

## Coal Ultra supercritical
Technology
Pollution Prevention and Abatement Handbook, 1998: Toward Cleaner Production, Bind 777
| Technology | Ultra-supercritical coal power plant
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1000 | 1000 | 1000 | 700 | 1200 | 700 | 1200 | I | 1
| Generating capacity for total power plant (MWe) | 2000 | 2000 | 2000 | 700 | 1200 | 700 | 1200 | I | 1
| Electricity efficiency, net (%), name plate | 42.5 | 44 | 45 | 40 | 45 | 42 | 47 |  | 1,3
| Electricity efficiency, net (%), annual average | 42 | 43 | 44 | 40 | 45 | 42 | 47 |  | 1,3
| Forced outage (%) | 7 | 6 | 3 | 5 | 15 | 2 | 7 | A | 1
| Planned outage (weeks per year) | 7 | 5 | 3 | 3 | 8 | 2 | 4 | A | 1
| Technical lifetime (years) | 30 | 30 | 30 | 25 | 40 | 25 | 40 |  | 1
| Construction time (years) | 4.3 | 3 | 3 | 3 | 5 | 2 | 4 | A | 1
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 5 | 5 | 5 | 4 | 5 | 4 | 5 | B | 1
| Minimum load (% of full load) | 40 | 40 | 40 | 25 | 50 | 20 | 40 | A | 1
| Warm start-up time (hours) | 4 | 4 | 4 | 2 | 5 | 2 | 5 | B | 1
| Cold start-up time (hours) | 12 | 12 | 12 | 6 | 15 | 6 | 12 | B | 1
Environment
| PM 2.5 (mg per Nm3) | 150 | 100 | 100 | 50 | 150 | 20 | 100 | F | 2,4
| SO2 (degree of desulphuring, %) | 73 | 73 | 73 | 73 | 95 | 73 | 95 | C,D | 2,4
| NOX (g per GJ fuel) | 263 | 263 | 263 | 263 | 263 | 263 | 263 | D | 2,4
| CH4 (g per GJ fuel) | - | - | - | - | - | - | -
| N2O (g per GJ fuel) | - | - | - | - | - | - | -
Financial data
| Nominal investment (M$/MWe) | 1.73 | 1.68 | 1.63 | 1.3 | 2.17 | 1.22 | 2.04 | E,G,H | 1,3,6
- of which equipment
- of which installation
| Fixed O&M ($/MWe/year) | 64500 | 62500 | 60600 | 48450 | 80700 | 45500 | 75800 | G | 1,3,6
| Variable O&M ($/MWh) | 1.25 | 1.2 | 1.15 | 0.9 | 1.6 | 0.9 | 1.5 | G | 1,3
| Start-up costs ($/MWe/start-up) | 57 | 57 | 57 | 45.6 | 114 | 45.6 | 114 |  | 5
References:
1 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
2 | Platts Utility Data Institute (UDI) World Electric Power Plant Database (WEPP)
3 | Learning curve approach for the development of financial parameters.
4 | Maximum emission from Minister of Environment Regulation 21/2008
5 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
6 | IEA, World Energy Outlook, 2023
Notes:
A | Assumed gradidual improvement to international standard in 2050.
B | Assumed no improvement for regulatory capability.
C | Indonesian sulphur content in coal is up to 360 g/GJ. Conversion factor 0.35 to mg/Nm3 yields 1030 mg/Nm3. With a max of 750 mg/Nm3 then gives a % of desulphuring of 73%.
D | Calculated from a max of 750 mg/Nm3 to g/GJ (conversion factor 0.35 from Pollution Prevention and Abatement Handbook, 1998)
E | For economy of scale a proportionality factor, a, of 0.85 is suggested.
F | Uncertainty Upper is from regulation. Lower is from current standards in Japan (2020) and South Korea (2050).
G | Uncertainty (Upper/Lower) is estimated as +/- 25%.
H | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
I | Based on data collection from Indonesian projects

## IGCC (COAL)
Technology
Pollution Prevention and Abatement Handbook, 1998: Toward Cleaner Production, Bind 777
| Technology | Coal, Integrated Gasification Combined Cycle (IGCC)
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 200 | 200 | 200 |  |  |  |  | A
| Generating capacity for total power plant (MWe) | 600 | 600 | 600 |  |  |  |  | A | 1
| Electricity efficiency, net (%), name plate | 42 | 43 | 45 |  |  |  |  | G | 1
| Electricity efficiency, net (%), annual average | 40 | 41 | 43 |  |  |  |  | G
| Cold gas efficiency (%) | 75 | 80 | 80 |  |  |  |  | B
| Forced outage (%) | 5.53 | 6 | 6 | [5 empty] | 2
| Planned outage (weeks per year) | 6.6 | 7 | 7 |  |  |  |  | C | 3
| Technical lifetime (years) | 30 | 30 | 30 | [5 empty] | 1
| Construction time (years) | 4 | 4 | 4 | [5 empty] | 4
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 3 | 3.5 | 5 |  |  |  |  | D | 5
| Minimum load (% of full load) | 50 | 40 | 30 |  |  |  |  | D | 5
| Warm start-up time (hours) | 6 | 6 | 6 | [5 empty] | 10,11
| Cold start-up time (hours) | 40 | 40 | 40 | 15 | 80 | 15 | 80 | F | 10,11
Environment
| PM 2.5 (mg per Nm3) | 115 | 100 | 100 | [5 empty] | 7,12
| SO2 (degree of desulphuring, %) | 99 | 99 | 99 | [5 empty] | 9,12
| NOX (g per GJ fuel) | 173 | 51.6796 | 49.3827 | [5 empty] | 7,12
CO (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 2.73 | 2.51 | 2.32 | 2.46 | 3.99 | 2 | 3.42 | H | 6,13
| - of which equipment | 30% | 30% | 30% | 25% | 50% | 25% | 50% |  | 6,13
| - of which installation | 70% | 70% | 70% | 50% | 75% | 50% | 75% |  | 6
| Fixed O&M ($/MWe/year) | 68400 | 66300 | 64300 | 64000 | 78000 | 64000 | 78000 |  | 6
| Variable O&M ($/MWh) | 13.7 | 13.3 | 12.9 | 18.2 | 9 | 19 | 9 |  | 6,13
| Start-up costs ($/MWe/start-up) | 114 | 114 | 114 |  |  |  |  | E
References:
1 | MDPI, 2018, "Life Cycle Analysis of Integrated Gasification Combined Cycle Power Generation in the Context of Southeast Asia,"
2 | IEEFA, 2018,"Lezna IGCC Project: High Costs and Unreliable Operations Can Be Expected"
3 | Nevile Holt - EPRI, 2004,"Coal-based IGCC Plans - Recent Operating Experience and Lessons Learned"
4 | EFDA, 2013, "Review and Update of Power Sector"
5 | Modern Power Systems, Increasing the flexibility of IGCC, https://www.modernpowersystems.com/features/featureincreasing-flexibility-of-igcc-4893259/
6 | Global CCS Institute, 2017, "Global Costs of Carbon Capture and Storage"
7 | Michael A. Mac Kinnon, University of California, 2017, "The role of natural gas and its infrastructure in mitigating greenhouse gas emissions, improving regional air quality, and renewable resource integration"
8 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
9 | United States Department of Energy National Energy Technology Laboratory, Gasification Plant Cost and Performance Optimization, 2002
10 | IEAGHG, Operating Flexibility of Power Plants with CCS
11 | EPRI, Increasing the Flexibility of IGCC Power Plants
12 | Koornneef J., 2011, Carbon Dioxide Capture and Air Quality
13 | NREL ATB 2020
Notes:
A | IGCCs use combined (gas) cycles to produce power. Their efficiency is higher for big plant sizes (economy of scale). Preliminary screenings in Sumatra and Kalimantan identify in 150-200 MW the IGCC size.
B | The cold gas efficiency is the efficiency of the gasification unit
C | Unplanned outages can be sizeable. These mainly concern corrosion and fouling in the heat exchangers, particularly the syngas coolers.
D | It is assumed that improvements in the air sepration unit (ASU) and in the gasification unit boost the cycle's ramping capabilities in the coming years
E | Start-up costs vary depending on the idle time. Warm-up of the gasification unit requires time and can be expensive, therefore start-up cost is higher than a CC plant.
F | Start-up time is the necessary time to reach minimum load. It takes a long time for IGCC to reach full-load and it can vary depending on the specific technology, hence the wide range.
G | The efficiency is strongly dependent on coal type. High-grade coal can lead to efficiencies of over 45%, but low-rank coal (3-4000 kcal/kg) used in Indonesia leads to lower efficiencies with today's technology.
H | Price for one unit. An IGCC power plant consisting of two units can be considered to have a 10% lower overnight cost

## Ammonia co-firing (Coal)
Technology
| Technology | Coal Power Plant – Steam Cycle – co-firing 20% ammonia | [9 empty] | Technology | Coal Power Plant – Steam Cycle – co-firing 100% ammonia
|  | 2023 | 2030 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref |  |  | 2030 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper |  |  |  | Energy/technical data |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | 600 | 600 | 600 | 300 | 800 | 300 | 800 |  |  |  | Generating capacity for one unit (MW) | 600 | 600 | 300 | 800 | 300 | 800
| Electricity efficiency. net (%). name plate | -1 | -1 | -1 | 0 | -2 | 0 | -2 | A,B | 1 |  | Electricity efficiency. net (%). name plate | -2 | -2 | -1 | -3 | -1 | -3 | A,B | 1
| Electricity efficiency. net (%). annual average | -1 | -1 | -1 | 0 | -2 | 0 | -2 | A,B | 1 |  | Electricity efficiency. net (%). annual average | -2 | -2 | -1 | -3 | -1 | -3 | A,B | 1
| Forced outage (%) | 0 | 0 | 0 | 0 | +1 | 0 | +1 | A |  |  | Forced outage (%) | 0 | 0 | 0 | +1 | 0 | +1 | A
| Planned outage (weeks per year) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A |  |  | Planned outage (weeks per year) | 0 | 0 | 0 | 0 | 0 | 0 | A
| Technical lifetime (years) | [10 empty] | Technical lifetime (years)
| Construction time (years) | [10 empty] | Construction time (years)
| Space requirement (1000m2/MW) | [10 empty] | Space requirement (1000m2/MW)
| Ramping configurations | [10 empty] | Ramping configuration
| Ramping (% per minute) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A |  |  | Ramping (% per minute) | 0 | 0 | 0 | 0 | 0 | 0 | A
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A |  |  | Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | A
| Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A |  |  | Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | A
| Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A |  |  | Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | A
| Environment | [10 empty] | Environment
| PM2.5 (% compared to 100% coal) | -20% | -20% | -20% | -10% | -20% | -10% | -20% | A | 1 |  | PM2.5 (% compared to 100% coal) | -100% | -100% | -70% | -100% | -70% | -100% | A | 1
| SO2 (% compared to 100% coal) | -20% | -20% | -20% | -10% | -20% | -10% | -20% | A | 1 |  | SO2 (% compared to 100% coal) | -100% | -100% | -70% | -100% | -70% | -100% | A | 1
| NOX (% compared to 100% coal) | +5% | +5% | +5% | 0% | +10% | 0% | +10% | A | 1,2,3,4 |  | NOX (% compared to 100% coal) | +30% | +30% | +20% | +50% | +20% | +50% | A | 1,2,3,4
| Financial data | [10 empty] | Financial data
| Nominal investment (M$/MWe) | 0.15 | 0.15 | 0.14 | 0.11 | 0.19 | 0.11 | 0.18 | A,C,D | 2 |  | Nominal investment (M$/MWe) | 0.34 | 0.33 | 0.26 | 0.44 | 0.25 | 0.41 | A,C,D | 2
| - of which equipment | [10 empty] | - of which equipment
| - of which installation | [10 empty] | - of which installation
| Fixed O&M (% compared to 100% coal) | +5% | +5% | +5% | +3% | +8% | +3% | +8% | A | 2 |  | Fixed O&M (% compared to 100% coal) | +10% | +10% | +5% | +15% | +5% | +15% | A | 2
| Variable O&M (% compared to 100% coal) | +5% | +5% | +5% | +3% | +8% | +3% | +8% | A | 2 |  | Variable O&M (% compared to 100% coal) | +10% | +10% | +5% | +15% | +5% | +15% | A | 2
References: | [10 empty] | References:
1 | G.Nagatani, H.Ishii, T.Ito, E.Ohno, Y.Okuma, “Development of Co-firing method of Pulverized coal and Ammonia to reduce greenhouse gas emissions”. IHI Engineering Review, Vol.53, No.1, 2020. | [9 empty] | 1 | G.Nagatani, H.Ishii, T.Ito, E.Ohno, Y.Okuma, “Development of Co-firing method of Pulverized coal and Ammonia to reduce greenhouse gas emissions”. IHI Engineering Review, Vol.53, No.1, 2020.
2 | BloombergNEF, Japan’s costly ammonia coal co-firing strategy, 2022 | [9 empty] | 2 | BloombergNEF, Japan’s costly ammonia coal co-firing strategy, 2022
3 | T. Ito, H.Ishii, J.Zhang, S..Ishihara, S.Toshiyuki (IHI Corporation), New technology of the Ammonia co-firing with pulverized coal to reduce the NOx emission. AIChE meeting 2019. | [9 empty] | 3 | T. Ito, H.Ishii, J.Zhang, S..Ishihara, S.Toshiyuki (IHI Corporation), New technology of the Ammonia co-firing with pulverized coal to reduce the NOx emission. AIChE meeting 2019.
4 | J.Tan, Y.He, R.Zhu, Y.Zhu, Z.Wang, Experimental study on co-firing characteristic of ammonia with pulverized coal in a staged combustion drop tube furnace, 2022 | [9 empty] | 4 | J.Tan, Y.He, R.Zhu, Y.Zhu, Z.Wang, Experimental study on co-firing characteristic of ammonia with pulverized coal in a staged combustion drop tube furnace, 2022
Notes: | [10 empty] | Notes:
A | Value depends on the original plant. Value indicates the estimated change from the original value (unit is the same as the parameter). | [9 empty] | A | Value depends on the original plant. Value indicates the estimated change from the original value (unit is the same as the parameter).
B | Typically, the electricity efficiency will be 1-2 % point lower than that of the plant prior to conversion. | [9 empty] | B | Typically, the electricity efficiency will be 1-2 % point lower than that of the plant prior to conversion.
C | The nominal investment assumes that exclude investment for a general lifetime extension campaign | [9 empty] | C | The nominal investment assumes that exclude investment for a general lifetime extension campaign
D | The investment cost includes, modifying existing coal plants for ammonia co-firing requires boiler modifications and investment in additional facilities like ammonia tanks and vaporizers. In general, the retrofits include (ref. 2):Modified burner; New ammonia receiving device, pipe, tank and vaporizer; Additional NOx removal device. The cost of improving pipelines outside the plant-land plot is not included. | [9 empty] | D | The investment cost includes, modifying existing coal plants for ammonia co-firing requires boiler modifications and investment in additional facilities like ammonia tanks and vaporizers. In general, the retrofits include (ref. 2):Modified burner; New ammonia receiving device, pipe, tank and vaporizer; Additional NOx removal device. The cost of improving pipelines outside the plant-land plot is not included.

## Biomass co-firing (Coal)
Technology
| Technology | Coal Power Plant – Steam Cycle – co-firing 20% biomass (wood pellets) | [9 empty] | Technology | Coal Power Plant – Steam Cycle – co-firing 100% biomass (wood pellets)
|  | 2023 | 2030 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref |  |  | 2030 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper |  |  |  | Energy/technical data |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | 600 | 600 | 600 | 300 | 800 | 300 | 800 |  |  |  | Generating capacity for one unit (MW) | 600 | 600 | 300 | 800 | 300 | 800
| Electricity efficiency. net (%). name plate | -1 | -1 | -1 | 0 | -2 | 0 | -2 | A,B | 1,3,4 |  | Electricity efficiency. net (%). name plate | -2 | -2 | -1 | -3 | -1 | -3 | A,B | 1,3,4
| Electricity efficiency. net (%). annual average | -1 | -1 | -1 | 0 | -2 | 0 | -2 | A,B | 1,3,4 |  | Electricity efficiency. net (%). annual average | -2 | -2 | -1 | -3 | -1 | -3 | A,B | 1,3,4
| Forced outage (%) | 0 | 0 | 0 | 0 | 1 | 0 | 1 | A | 1,3,4 |  | Forced outage (%) | 0 | 0 | 0 | 1 | 0 | 1 | A | 1,3,4
| Planned outage (weeks per year) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 1,3,4 |  | Planned outage (weeks per year) | 0 | 0 | 0 | 0 | 0 | 0 | A | 1,3,4
| Technical lifetime (years) | [10 empty] | Technical lifetime (years)
| Construction time (years) | [10 empty] | Construction time (years)
| Space requirement (1000m2/MW) | [7 empty] | A,C | 1,3,4 |  | Space requirement (1000m2/MW) | [6 empty] | A,C | 1,3,4
| Ramping configurations | [10 empty] | Ramping configurations
| Ramping (% per minute) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 1,3,4 |  | Ramping (% per minute) | 0 | 0 | 0 | 0 | 0 | 0 | A | 1,3,4
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 1,3,4 |  | Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | A | 1,3,4
| Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 1,3,4 |  | Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | A | 1,3,4
| Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 1,3,4 |  | Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | A | 1,3,4
| Environment | [10 empty] | Environment
| PM2.5 (% compared to 100% coal) | -10% | -10% | -10% | -5% | -20% | -5% | -20% | A | 1,2,3,4 |  | PM2.5 (% compared to 100% coal) | -70% | -70% | -50% | -90% | -50% | -90% | A | 1,2,3,4
| SO2 (% compared to 100% coal) | -10% | -10% | -10% | -5% | -20% | -5% | -20% | A | 1,2,3,4 |  | SO2 (% compared to 100% coal) | -70% | -70% | -50% | -90% | -50% | -90% | A | 1,2,3,4
| NOX (% compared to 100% coal) | -5% | -5% | -5% | 0% | -10% | 0% | -10% | A | 1,2,3,4 |  | NOX (% compared to 100% coal) | -30% | -30% | -5% | -40% | -5% | -40% | A | 1,2,3,4
| Financial data | [10 empty] | Financial data
| Nominal investment (M$/MWe) | +0.16 | +0.16 | +0.15 | +0.12 | +0.20 | +0.11 | +0.19 | A,D | 1,3,4 |  | Nominal investment (M$/MWe) | +0.36 | +0.36 | +0.28 | +0.46 | +0.26 | +0.44 | A,D | 1,3,4
| - of which equipment | [10 empty] | - of which equipment
| - of which installation | [10 empty] | - of which installation
| Fixed O&M (% compared to 100% coal) | 3% | 3% | 3% | 1% | 5% | 1% | 5% | A | 1,3,4 |  | Fixed O&M (% compared to 100% coal) | 5% | 5% | 3% | 10% | 3% | 10% | A | 1,3,4
| Variable O&M (% compared to 100% coal) | 3% | 3% | 3% | 1% | 5% | 1% | 5% | A | 1,3,4 |  | Variable O&M (% compared to 100% coal) | 5% | 5% | 3% | 10% | 3% | 10% | A | 1,3,4
References: | [10 empty] | References:
1 | “Biomass Co-firing: Technology brief,” IRENA, 2013. https://irena.org/-/media/Files/IRENA/Agency/Publication/2013/IRENA-ETSAP-Tech-Brief-E21-Biomass-Co-firing.pdf | [9 empty] | 1 | “Biomass Co-firing: Technology brief,” IRENA, 2013. https://irena.org/-/media/Files/IRENA/Agency/Publication/2013/IRENA-ETSAP-Tech-Brief-E21-Biomass-Co-firing.pdf
2 | X. Wang et al., “Experimental investigation on biomass co-firing in a 300MW pulverized coal-fired utility furnace in China,” Proceedings of the Combustion Institute, vol. 33, no. 2, pp. 2725–2733, 2011, doi: https://doi.org/10.1016/j.proci.2010.06.055. | [9 empty] | 2 | X. Wang et al., “Experimental investigation on biomass co-firing in a 300MW pulverized coal-fired utility furnace in China,” Proceedings of the Combustion Institute, vol. 33, no. 2, pp. 2725–2733, 2011, doi: https://doi.org/10.1016/j.proci.2010.06.055.
3 | Rohan Fernando, IEA Clean Coal Centre, “Cofiring high ratios of biomass with coal”, 2012 | [9 empty] | 3 | Rohan Fernando, IEA Clean Coal Centre, “Cofiring high ratios of biomass with coal”, 2012
4 | Danish Energy Agency and Energinet, “Technology Data - Energy Plants for Electricity and District heating generation”, 2016. | [9 empty] | 4 | Danish Energy Agency and Energinet, “Technology Data - Energy Plants for Electricity and District heating generation”, 2016.
Notes: | [10 empty] | Notes:
A | Value depends on the original plant. Value indicates the estimated change from the original value (unit is the same as the paramter). | [9 empty] | A | Value depends on the original plant. Value indicates the estimated change from the original value (unit is the same as the paramter).
B | Typically the electricity efficiency will be 1-2 % point lower than that of the plant prior to conversion. | [9 empty] | B | Typically the electricity efficiency will be 1-2 % point lower than that of the plant prior to conversion.
C | Some additional under roof space (or silos) will be required for storage of pellets compared to coal (estimated 50%-100% extra m3 storage). But not more floor space (m2). | [9 empty] | C | Some additional under roof space (or silos) will be required for storage of pellets compared to coal (estimated 50%-100% extra m3 storage). But not more floor space (m2).
D | The nominal investment is excluding investment for a general life time extension campaign | [9 empty] | D | The nominal investment is excluding investment for a general life time extension campaign

## Coal lifetime extension
Technology
| Technology | Lifetime extension of coal power plant
|  | 2023 | 2030 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MW) | 600 | 600 | 600 | 300 | 800 | 300 | 800
| Electricity efficiency. net (%-point). name plate | -1 | -1 | -1 | 0 | -3 | 0 | -3 | A | 1,3,4
| Electricity efficiency. net (%). annual average | -1 | -1 | -1 | 0 | -3 | 0 | -3 | A | 1,3,4
| Forced outage (%-point) | 0 | 0 | 0 | 0 | 1 | 0 | 1 | A | 3
| Planned outage (weeks per year) | 0 | 0 | 0 | 0 | 1 | 0 | 1 | A | 3
| Technical lifetime (years) | 20 | 20 | 20 | 10 | 20 | 10 | 20
Construction time (years)
Space requirement (1000m2/MW)
Ramping configurations
| Ramping (% per minute) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 2
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 2
| Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 2
| Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 2
Environment
| PM2.5 (% compared to 100% coal) | 0% | 0% | 0% | 0% | 0% | 0% | 0% | A | 3
| SO2 (% compared to 100% coal) | 0% | 0% | 0% | 0% | 0% | 0% | 0% | A | 3
| NOX (% compared to 100% coal) | 0% | 0% | 0% | 0% | 0% | 0% | 0% | A | 3
Financial data
| Nominal investment (M$/MWe) | 0.28 | 0.28 | 0.28 | 0.11 | 0.32 | 0.11 | 0.32 | AB | 1,2,3,4
- of which equipment
- of which installation
| Fixed O&M ($/MWe/year) | +3% | +3% | +3% | +1% | +5% | +1% | +5% | A | 1,3,4
| Variable O&M ($/MWh) | 0% | 0% | 0% | 0% | +3% | 0% | +3% | A | 1,3,4
References:
1 | EIA, “Generating unit annual capital and life extension cost analysis,” 2019
2 | Parsons Brinckerhoff, “Coal and Gas Assumptions,” 2014. [Online]. Available: https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/315717/coal_and_gas_assumptions.PDF.
3 | Danish Energy Agency and Energinet, “Technology Data - Energy Plants for Electricity and District heating generation”, 2016 - Updated
4 | EPRI, Generic guidelines for the life extension of fossil fuel power plants, 1986
Notes:
A | Value depends on the original plant. Value indicates the estimated change from the original value (unit is the same as the parameter).
B | Values will depend on those of the plant prior to LTE, however the average fixed O&M cost may increase slightly for the extension period compared with the original lifetime to accommodate the necessary reinvestments during the extended lifetime
C | It is assumed that plant emissions prior to the LTE are within the legal limits.
D | Investment costs will vary largely, depending on the necessary scope of work. The indicated range represents typical cases where lifetime extended to obtain additional 20 years lifetime.
E | Values will depend on those of the plant prior to LTE, however the average fixed O&M cost may increase slightly for the extension period compared with the original lifetime to accommodate the necessary reinvestments during the extended life time.

## SCGT (GAS)
Technology
Pollution Prevention and Abatement Handbook, 1998: Toward Cleaner Production, Bind 777
| Technology | Simple Cycle Gas Turbine - large system
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 40 | 40 | 40 | 15 | 150 | 15 | 150 | I | 1,3
| Generating capacity for total power plant (MWe) | 200 | 200 | 200 | 45 | 400 | 45 | 400 | I | 1,3
| Electricity efficiency, net (%), name plate | 34 | 36 | 40 | [5 empty] | 1,2
| Electricity efficiency, net (%), annual average | 33 | 35 | 39 | [5 empty] | 1,2
| Forced outage (%) | 2 | 2 | 2
| Planned outage (weeks per year) | 3 | 3 | 3
| Technical lifetime (years) | 25 | 25 | 25
| Construction time (years) | 1.5 | 1.5 | 1.5 | 1.1 | 1.9 | 1.1 | 1.9 | B | 3
| Space requirement (1000 m2/MWe) | 0.02 | 0.02 | 0.02 | 0.015 | 0.025 | 0.015 | 0.025 | B | 3
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 20 | 20 | 20 | 10 | 30 | 10 | 30 | C | 3,6
| Minimum load (% of full load) | 40 | 30 | 15 | 30 | 50 | 10 | 40 | A | 4
| Warm start-up time (hours) | 0.25 | 0.23 | 0.2 | [5 empty] | 3
| Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | [5 empty] | 3
Environment
| PM 2.5 (mg per Nm3) | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 5
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | E
| NOX (g per GJ fuel) | 86 | 60 | 20 | 20 | 86 | 20 | 86 | A,D | 3,5
| CH4 (g per GJ fuel) | - | - | - | - | - | - | -
| N2O (g per GJ fuel) | - | - | - | - | - | - | -
Financial data
| Nominal investment (M$/MWe) | 1.12 | 1.064 | 0.9856 | 0.85 | 1.75 | 0.6 | 1.25 | F,G,H | 1
| - of which equipment | 50% | 50% | 50% | 50% | 50% | 50% | 50% |  | 7
| - of which installation | 50% | 50% | 50% | 50% | 50% | 50% | 50% |  | 7
| Fixed O&M ($/MWe/year) | 26500 | 25700 | 24900 | 19000 | 33000 | 18000 | 31000 | B | 1,8
| Variable O&M ($/MWh) | 3.6 | 3.5 | 3.4 | 2.7 | 4.5 | 2.55 | 4.25 | B | 1,8
| Start-up costs ($/MWe/start-up) | 25 | 25 | 25 | 20 | 35 | 20 | 35 | B | 4
References:
1 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
2 | IEA, World Energy Outlook, 2015.
3 | Danish Energy Agency, 2015, "Technology Catalogue on Power and Heat Generation".
4 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
5 | Maximum emission from Minister of Environment Regulation 21/2008
6 | Vuorinen, A., 2008, "Planning of Optimal Power Systems".
7 | Soares, 2008, "Gas Turbines: A Handbook of Air, Land and Sea Applications".
8 | Lazard, 2023, "Levelised Cost of Energy +"
Notes:
A | Assumed gradidual improvement to international standard in 2050.
B | Uncertainty (Upper/Lower) is estimated as +/- 25%.
C | Assumed no improvement for regulatory capability.
D | Calculated from a max of 400 mg/Nm3 to g/GJ (conversion factor 0.27 from Pollution Prevention and Abatement Handbook, 1998)
E | Commercialised natural gas is practically sulphur free and produces virtually no sulphur dioxide
F | The investment cost of an aero-derivative gas turbine will be in the higher end than an industrial gas turbine (ref. 5) . Roughly 50% higher.
G | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
H | For 2020, uncertainty ranges are based on cost spans of various sources.
I | Based on data collection from Indonesian projects

## CCGT (GAS)
Technology
Pollution Prevention and Abatement Handbook, 1998: Toward Cleaner Production, Bind 777
| Technology | Combined Cycle Gas Turbine
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 100 | 100 | 100 | 40 | 300 | 40 | 300 | I | 1
| Generating capacity for total power plant (MWe) | 400 | 400 | 400 | 100 | 800 | 100 | 800 | I | 1
| Electricity efficiency, net (%), name plate | 57 | 60 | 61 | 45 | 62 | 55 | 65 |  | 1,3,5,10
| Electricity efficiency, net (%), annual average | 56 | 59 | 60 | 39 | 61 | 54 | 64
| Forced outage (%) | 5 | 5 | 5 | 3 | 10 | 3 | 10 |  | 1
| Planned outage (weeks per year) | 5 | 5 | 5 | 3 | 8 | 3 | 8 |  | 1
| Technical lifetime (years) | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 1
| Construction time (years) | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 |  | 1
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 20 | 20 | 20 | 10 | 30 | 10 | 30 | C | 1,2
| Minimum load (% of full load) | 45 | 30 | 15 | 30 | 50 | 10 | 40 | A | 5
| Warm start-up time (hours) | 2 | 1 | 1 | 1 | 3 | 0.5 | 2 | A | 1,5
| Cold start-up time (hours) | 4 | 4 | 4 | 2 | 5 | 2 | 5 |  | 1,5
Environment
| PM 2.5 (mg per Nm3) | 30 | 30 | 30
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | E
| NOX (g per GJ fuel) | 86 | 60 | 20 | 20 | 86 | 20 | 86 | A,D | 7,8
| CH4 (g per GJ fuel) | - | - | - | - | - | - | -
| N2O (g per GJ fuel) | - | - | - | - | - | - | -
Financial data
| Nominal investment (M$/MWe) | 1.09 | 1.0355 | 0.9592 | 0.74 | 1.14 | 0.63 | 1.03 | F,H | 1,3,10
| - of which equipment | 50% | 50% | 50% | 50% | 50% | 50% | 50% |  | 9
| - of which installation | 50% | 50% | 50% | 50% | 50% | 50% | 50% |  | 9
| Fixed O&M ($/MWe/year) | 26800 | 26000 | 25200 | 20000 | 33500 | 19000 | 31500 | B | 1,3
| Variable O&M ($/MWh) | 2.6 | 2.5 | 2.4 | 1.9 | 3.3 | 1.8 | 3.1 | B | 1
| Start-up costs ($/MWe/start-up) | 90 | 90 | 90 | 70 | 115 | 70 | 115 | B | 6
References:
1 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
2 | Vuorinen, A., 2008, "Planning of Optimal Power Systems".
3 | IEA, World Energy Outlook, 2015.
4 | Learning curve approach for the development of financial parameters.
5 | Siemens, 2010, "Flexible future for combined cycle".
6 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
7 | Maximum emission from Minister of Environment Regulation 21/2008
8 | Danish Energy Agency, 2015, "Technology Catalogue on Power and Heat Generation".
9 | Soares, 2008, "Gas Turbines: A Handbook of Air, Land and Sea Applications".
10 | IEA, Projected Costs of Generating Electricity, 2015.
Notes:
A | Assumed gradidual improvement to international standard in 2050.
B | Uncertainty (Upper/Lower) is estimated as +/- 25%.
C | Assumed no improvement for regulatory capability.
D | Calculated from a max of 400 mg/Nm3 to g/GJ (conversion factor 0.27 from Pollution Prevention and Abatement Handbook, 1998)
E | Commercialised natural gas is practically sulphur free and produces virtually no sulphur dioxide
F | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
H | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 10-15% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.
I | Based on data collection from Indonesian projects

## Hydrogen co-firing CCGT
Technology
| Technology | CCGT – co-firing 20% hydrogen (in term of energy) | [9 empty] | Technology | CCGT – co-firing 100% hydrogen (in term of energy)
|  | 2023 | 2030 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref |  |  | 2030 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper |  |  |  | Energy/technical data |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 100 | 100 | 100 | 40 | 300 | 40 | 300 | C | 6 |  | Generating capacity for one unit (MWe) | 100 | 100 | 40 | 300 | 40 | 300 | C | 6
| Generating capacity for total power plant (MWe) | 400 | 400 | 400 | 100 | 800 | 100 | 800 | C | 6 |  | Generating capacity for total power plant (MWe) | 400 | 400 | 100 | 800 | 100 | 800 | C | 6
| Electricity efficiency. net (%). name plate | 0 | 0 | 0 | 0 | -2 | 0 | -2 | A | 1,4 |  | Electricity efficiency. net (%). name plate | 0 | 0 | 0 | -3 | 0 | -3 | A | 1,4
| Electricity efficiency. net (%). annual average | 0 | 0 | 0 | 0 | -2 | 0 | -2 | A | 1,4 |  | Electricity efficiency. net (%). annual average | 0 | 0 | 0 | -3 | 0 | -3 | A | 1,4
| Forced outage (%) | 0 | 0 | 0 | 0 | 1 | 0 | 1 | A |  |  | Forced outage (%) | 0 | 0 | 0 | 1 | 0 | 1 | A
| Planned outage (weeks per year) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A |  |  | Planned outage (weeks per year) | 0 | 0 | 0 | 0 | 0 | 0 | A
| Technical lifetime (years) | [10 empty] | Technical lifetime (years)
| Construction time (years) | [10 empty] | Construction time (years)
| Space requirement (1000m2/MW) | [10 empty] | Space requirement (1000m2/MW)
| Ramping configurations | [10 empty] | Ramping configurations
| Ramping (% per minute) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 1,4 |  | Ramping (% per minute) | 0 | 0 | 0 | 0 | 0 | 0 | A | 1,4
| Minimum load (% of full load) | -3 | -3 | -3 | -1 | -5 | -1 | -5 | A | 1,4 |  | Minimum load (% of full load) | -5 | -5 | -3 | -10 | -3 | -10 | A | 1,4
| Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 1,4 |  | Warm start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | A | 1,4
| Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 1,4 |  | Cold start-up time (hours) | 0 | 0 | 0 | 0 | 0 | 0 | A | 1,4
| Environment | [10 empty] | Environment
| PM2.5 (% compared to 100% natural gas) | -20% | -20% | -20% | -10% | -20% | -10% | -20% | A | 4 |  | PM2.5 (% compared to 100% natural gas) | -100% | -100% | -100% | -100% | -100% | -100% | A | 4
| SO2 (% compared to 100% natural gas) | -20% | -20% | -20% | -10% | -20% | -10% | -20% | A | 4 |  | SO2 (% compared to 100% natural gas) | -100% | -100% | -100% | -100% | -100% | -100% | A | 4
| NOX (% compared to 100% natural gas) | 40% | 40% | 40% | 10% | 60% | 10% | 60% | A | 4,5 |  | NOX (% compared to 100% natural gas) | -100% | -100% | -100% | -100% | -100% | -100% | A | 4,5
| Financial data | [10 empty] | Financial data
| Nominal investment (M$/MWe) | +0.09 | +0.09 | +0.08 |  |  |  |  | A,B,D | 2 |  | Nominal investment (M$/MWe) | +0.31 | +0.29 |  |  |  |  | A,B | 2
| - of which equipment | [10 empty] | - of which equipment
| - of which installation | [10 empty] | - of which installation
| Fixed O&M (% compared to 100% natural gas) | 3% | 3% | 3% | 1% | 5% | 1% | 5% | A | 2 |  | Fixed O&M (% compared to 100% natural gas) | 5% | 5% | 3% | 10% | 3% | 10% | A | 2
| Variable O&M (% compared to 100% natural gas) | 3% | 3% | 3% | 1% | 5% | 1% | 5% | A | 2 |  | Variable O&M (% compared to 100% natural gas) | 5% | 5% | 3% | 10% | 3% | 10% | A | 2
References: | [10 empty] | References:
1 | “Hydrogen gas turbines,” ETN Global, 2020. https://etn.global/wp-content/uploads/2020/01/ETN-Hydrogen-Gas-Turbines-report.pdf. | [9 empty] | 1 | “Hydrogen gas turbines,” ETN Global, 2020. https://etn.global/wp-content/uploads/2020/01/ETN-Hydrogen-Gas-Turbines-report.pdf.
2 | S. Öberg, M. Odenberger, and F. Johnsson, “Exploring the competitiveness of hydrogen-fueled gas turbines in future energy systems,” Int. J. Hydrogen Energy, vol. 47, no. 1, pp. 624–644, 2022, doi: https://doi.org/10.1016/j.ijhydene.2021.10.035. | [9 empty] | 2 | S. Öberg, M. Odenberger, and F. Johnsson, “Exploring the competitiveness of hydrogen-fueled gas turbines in future energy systems,” Int. J. Hydrogen Energy, vol. 47, no. 1, pp. 624–644, 2022, doi: https://doi.org/10.1016/j.ijhydene.2021.10.035.
3 | EPRI, “Hydrogen-Capable Gas Turbines for Deep Decarbonization,” 2019. [Online]. Available: https://h2fcp.org/sites/default/files/3002017544_Technology-Insights-Brief_ Hydrogen_Capable-Gas-Turbines-for-Deep-Decarbonization.pdf. | [9 empty] | 3 | EPRI, “Hydrogen-Capable Gas Turbines for Deep Decarbonization,” 2019. [Online]. Available: https://h2fcp.org/sites/default/files/3002017544_Technology-Insights-Brief_ Hydrogen_Capable-Gas-Turbines-for-Deep-Decarbonization.pdf.
4 | T.Wind, F.Guthe, K.Syed, “Co-firing of hydrogen and natural gases in lean premixed conventional and reheat burners (Alstom GT26), 2014 | [9 empty] | 4 | T.Wind, F.Guthe, K.Syed, “Co-firing of hydrogen and natural gases in lean premixed conventional and reheat burners (Alstom GT26), 2014
5 | L.Wright, C.Lewis, “Emission of Nox from blending of hydrogen and natural gas in space heating boilers”, 2022 | [9 empty] | 5 | L.Wright, C.Lewis, “Emission of Nox from blending of hydrogen and natural gas in space heating boilers”, 2022
6 | PLN, 2023, data provided the System Planning Division at PLN | [9 empty] | 6 | PLN, 2023, data provided the System Planning Division at PLN
Notes: | [10 empty] | Notes:
A | Value depends on the original plant. Value indicates the estimated change from the original value (unit is the same as the paramter). | [9 empty] | A | Value depends on the original plant. Value indicates the estimated change from the original value (unit is the same as the paramter).
B | The nominal investment assumes that exclude investment for a general lifetime extension campaign | [9 empty] | B | The nominal investment assumes that exclude investment for a general lifetime extension campaign
C | Based on data collection from Indonesian projects | [9 empty] | C | Based on data collection from Indonesian projects
D | All costs for extra component needed for running the turbine with H2 and for resizing equipment in order to maintain the same power output capacity of the plant is included in the investment cost. The cost of improving pipelines outside the plant-land plot is not included. | [9 empty] | D | All costs for extra component needed for running the turbine with H2 and for resizing equipment in order to maintain the same power output capacity of the plant is included in the investment cost. The cost of improving pipelines outside the plant-land plot is not included.

## CCS - Supercritical coal
Technology
| Technology | Supercritical coal power plant with CCS, new plant
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 540 | 540 | 540 |  |  |  |  | A | 1
| Generating capacity for total power plant (MWe) | 540 | 540 | 540 |  |  |  |  | A | 1
| Electricity efficiency, net (%), name plate | 29 | 30 | 31 |  |  |  |  | A | 1,9
| Electricity efficiency, net (%), annual average | 28 | 29 | 30 |  |  |  |  | A | 1,9
| Forced outage (%) | 7 | 7 | 7
Planned outage (weeks per year)
Technical lifetime (years)
Construction time (years)
| CO2 emission reduction (%) | 90 | 90 | 90 | 50 | 95 | 70 | 99 | B | 1,9
Space requirement (1000 m2/MWe)
Additional data for non thermal plants
Capacity factor (%), theoretical
Capacity factor (%), incl. outages
Ramping configurations
| Ramping (% per minute) | 4 | 4 | 4 |  |  |  |  | C | 3
| Minimum load (% of full load) | 30 | 30 | 30 |  |  |  |  | D | 3
| Warm start-up time (hours) | 4 | 4 | 4 |  |  |  |  | E | 4
| Cold start-up time (hours) | 12 | 12 | 12 |  |  |  |  | E | 4
Environment
| PM 2.5 (mg per Nm3) | 150 | 100 | 100 | [5 empty] | 2,3
| SO2 (degree of desulphuring, %) | 97 | 97 | 97 | [5 empty] | 2,3
| NOX (g per GJ fuel) | 263 | 263 | 263 | [5 empty] | 2,3
CH4 (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 3.84 | 3.46 | 2.77 | 2.7 | 4.9 | 2 | 3.5 | F,G,H | 5,7,8
| - of which equipment | 30% | 30% | 30% | 25% | 50% | 25% | 50% |  | 1
| - of which installation | 70% | 70% | 70% | 50% | 75% | 50% | 75% |  | 1
| Fixed O&M ($/MWe/year) | 97000 | 90200 | 72800 | 67000 | 124000 | 50000 | 93000 |  | 5,7,8
| Variable O&M ($/MWh) | 4.5 | 4.2 | 3.7 | 4.2 | 5.72 | 2.63 | 4.7 |  | 5,7,8
Based on data in sheet Supercritical coal
References:
1 | Global CCS Institute, 2023, Global status of CCS
2 | Koornneef J., 2011, Carbon Dioxide Capture and Air Quality
3 | Danish Energy Agency, Technology data - Generation of electricity and district heating, 2020
4 | IEAGHG, Operating Flexibility of Power Plants with CCS
5 | IEA, 2021, The Role of Low-Carbon Fuels in the Clean Energy Transitions of the Power Sector
6 | Danish Energy Agency, Technology Data for Carbon Capture, Transport and Storage, 2023
7 | UK BEIS, Assessing the Cost Reduction Potential and Competitiveness of Novel UK Carbon Capture Technology, 2018
8 | NREL Annual Technology Baseline 2023, https://atb.nrel.gov/electricity/2023/data
9 | IRENA, Reaching Zero with Renewables Capturing Carbon, 2021
Notes:
A | The technology Supercritical CCS: Supercritical: solvent-based post combustion CO2 capture (PCCC) designed for 95% capture. The difference in ouput power represents the additional power required by the auxiliary equipment (with CCS, ~15% of the net output).
B | This figure represents the efficiency of the capture process. New technologies might remove CO2 more efficiently in the future. CO2 can be already captured at higher rates, but costs to marginally increase capture rates beyond the reported values are relatively high.
C | In principle, ramping is not affected by the presence/absence of CCS.
D | Minimum load is not affected by CCS. However, the CO2 compressor requires higher loads for smooth operability.
E | The regeneration in the post-combustion unit has a start-up time comparable to that of the power plant.
F | The total installed capacity of the newly built Super Critical coal plant with CCS is 600 MW.
G | The nominal investment cost corresponds to the cost of developing a newbuild supercritical plant with CCS facilty. The nominal investment is based on the economy of scale equation, C1/C2 = (P1/P2)^a, assuming the proportionality factor (a) is 0.6
H | The forecasted price are calculated considering the average development rates for the CCS technologies in the NREL ATB 2023

## CCS - IGCC (COAL)
Technology
| Technology | Coal, Integrated Gasification Combined Cycle IGCC with CCS, new plant
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 186 | 186 | 186 |  |  |  |  | A | 1
| Generating capacity for total power plant (MWe) | 534 | 534 | 534 |  |  |  |  | A,E | 1
| Electricity efficiency, net (%), name plate | 33 | 34 | 36 |  |  |  |  | A | 1,9
| Electricity efficiency, net (%), annual average | 31 | 32 | 34 |  |  |  |  | A | 1,9
| Forced outage (%) | 12 | 12 | 12
Planned outage (weeks per year)
| Technical lifetime (years) | -
Construction time (years)
| CO2 emission reduction (%) | 90 | 90 | 90 | 50 | 95 | 70 | 99 | B | 1,9
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 3 | 3 | 3 |  |  |  |  | C | 4
| Minimum load (% of full load) | 50 | 50 | 50 |  |  |  |  | D | 4
| Warm start-up time (hours) | 6 | 6 | 6 | [5 empty] | 3
| Cold start-up time (hours) | 50 | 50 | 50 | 15 | 80 | 15 | 80 |  | 3,5
Environment
| PM 2.5 (mg per Nm3) | 115 | 115 | 115 | [5 empty] | 2,4
| SO2 (degree of desulphuring, %) | 99 | 99 | 99 | [5 empty] | 2,4
| NOX (g per GJ fuel) | 173 | 173 | 173 | [5 empty] | 2,4
CO (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 4.77 | 4.29 | 3.43 | 3.5 | 6.5 | 2.5 | 4.7 | E,F,G | 5,7,8
| - of which equipment | 30% | 30% | 30% | 25% | 50% | 25% | 50% |  | 1
| - of which installation | 70% | 70% | 70% | 50% | 75% | 50% | 75% |  | 1
| Fixed O&M ($/MWe/year) | 123000 | 121800 | 116900 | 91000 | 213000 | 87000 | 202000 |  | 5,7,8
| Variable O&M ($/MWh) | 22 | 21.78 | 21.12 | 21.56 | 22.44 | 20.7 | 21.54 |  | 5,7,8
Based on data in sheet IGCC (Coal)
References:
1 | Global CCS Institute, 2023, Global status of CCS
2 | Koornneef J., 2011, Carbon Dioxide Capture and Air Quality
3 | IEAGHG, Operating Flexibility of Power Plants with CCS
4 | Danish Energy Agency, Technology data - Generation of electricity and district heating, 2020
5 | IEA, 2021, The Role of Low-Carbon Fuels in the Clean Energy Transitions of the Power Sector
6 | Danish Energy Agency, Technology Data for Carbon Capture, Transport and Storage, 2023
7 | UK BEIS, Assessing the Cost Reduction Potential and Competitiveness of Novel UK Casrbon Capture Technology, 2018
8 | NREL Annual Technology Baseline 2023, https://atb.nrel.gov/electricity/2023/data
9 | IRENA, Reaching Zero with Renewables Capturing Carbon, 2021
Notes:
A | The technology IGCC – CCS: SOA - slurry-fed IGCC with water-gas shift two high-hydrogen syngas-fired F-Frame combustion turbine/HRSG trains coupled to a single steam turbine, two-stage selexol acid gas removal system designed for 90% CO2 pre-combustion removal. The difference in ouput power represents the additional power required by the auxiliary equipment (with CCS, ~10-15% of the net output).
B | This figure represents the efficiency of the capture process. New technologies might remove CO2 more efficiently in the future. CO2 can be already captured at higher rates, but costs to marginally increase capture rates beyond the reported values are relatively high.
C | In principle, ramping is not affected by the presence/absence of CCS.
D | Minimum load is not affected by CCS. However, the CO2 compressor requires higher loads for smooth operability.
E | The total installed capacity of the newly bulit IGCC-CCS is 600 MW.
F | The nominal investment cost corresponds to the cost of developing an entirely new IGCC plant with CCS facility. The nominal investment is based on the economy of scale equation, C1/C2 = (P1/P2)^a, assuming the proportionality factor (a) is 0.6
G | The forecasted price are calculated considering the average development rates for the CCS technologies in the NREL ATB 2023

## CCS - CCGT (GAS)
Technology
| Technology | Natural Gas Combined Cycle with CCS, new plant
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 93 | 93 | 93 |  |  |  |  | A | 1
| Generating capacity for total power plant (MWe) | 372 | 372 | 372 |  |  |  |  | A,F | 1
| Electricity efficiency, net (%), name plate | 48 | 51 | 52 |  |  |  |  | A | 1,9
| Electricity efficiency, net (%), annual average | 47 | 50 | 51 |  |  |  |  | A | 1,9
| Forced outage (%) | 10 | 10 | 10
Planned outage (weeks per year)
| Technical lifetime (years) | -
Construction time (years)
| CO2 emission reduction (%) | 90 | 90 | 90 | 50 | 95 | 70 | 99 | B | 1,9
Space requirement (1000 m2/MWe)
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | -
| Capacity factor (%), incl. outages | - | - | -
Ramping configurations
| Ramping (% per minute) | 20 | 20 | 20 |  |  |  |  | C | 4
| Minimum load (% of full load) | 45 | 45 | 45 |  |  |  |  | D | 4
| Warm start-up time (hours) | 2 | 2 | 2 |  |  |  |  | E | 3
| Cold start-up time (hours) | 4 | 4 | 4 |  |  |  |  | E | 3
Environment
| PM 2.5 (mg per Nm3) | 30 | 30 | 30 | [5 empty] | 2,4
| SO2 (degree of desulphuring, %) | 99 | 99 | 99 | [5 empty] | 2,4
| NOX (g per GJ fuel) | 80 | 80 | 80 | [5 empty] | 2,4
| CH4 (g per GJ fuel) | - | - | -
Financial data
| Nominal investment (M$/MWe) | 2.39 | 2.15 | 1.72 | 1.3 | 2.9 | 1 | 2.1 | G,H,I | 5,7,8
| - of which equipment | 40% | 40% | 40% | 30% | 60% | 30% | 60% |  | 1
| - of which installation | 60% | 60% | 60% | 40% | 70% | 40% | 70% |  | 1
| Fixed O&M ($/MWe/year) | 59000 | 50200 | 37800 | 31000 | 65000 | 20000 | 42000 |  | 5,6,7
| Variable O&M ($/MWh) | 4.96 | 4.36 | 3.62 | 4.7 | 5.1 | 3.4 | 3.7 |  | 5,6
Based on data in sheet CCGT (GAS)
References:
1 | Global CCS Institute, 2023, Global status of CCS
2 | Koornneef J., 2011, Carbon Dioxide Capture and Air Quality
3 | IEAGHG, Operating Flexibility of Power Plants with CCS
4 | Danish Energy Agency, 2023, Technology Data – Carbon Capture, Transport and Storage
5 | IEA, 2021, The Role of Low-Carbon Fuels in the Clean Energy Transitions of the Power Sector
6 | EIA, 2020, Capital Cost and Performance Characteristic Estimates for Utility Scale Electric Power Generating Technologies
7 | Lazard, 2023, LCOE+
8 | NREL Annual Technology Baseline 2023, https://atb.nrel.gov/electricity/2023/data
9 | IRENA, 2021, Reaching Zero with Renewables Capturing Carbon
Notes:
A | The technology CCGT CCS: SOA - solvent-based post combustion CO2 capture (PCCC) designed for 95% capture. The difference in ouput power represents the additional power required by the auxiliary equipment (with CCS, ~10-15% of the net output).
B | This figure represents the efficiency of the capture process. New technologies might remove CO2 more efficiently in the future. CO2 can be already captured at higher rates, but costs to marginally increase capture rates beyond the reported values are relatively high.
C | In principle, ramping is not affected by the presence/absence of CCS.
D | Minimum load is not affected by CCS. However, the CO2 compressor requires higher loads for smooth operability.
E | The regeneration in the post-combustion unit has a start-up time comparable to that of the power plant.
F | The total installed capacity of the newly bulit CCGT-CCS is 400 MW.
G | The nominal investment cost corresponds to the cost of developing a newbuild CCS-CCGT.
H | The nominal investment cost for retrofitting corresponds to the cost of retroffiting an existing CCGT with CCS facility. The nominal investment is based on the economy of scale equation, C1/C2 = (P1/P2)^a, assuming the proportionality factor (a) is 0.6
I | The forecasted price are calculated considering the average development rates for the CCS technologies in the NREL ATB 2023

## Biomass power plant (small)
Technology
| Technology | Biomass power plant (small plant - palm oil / rice husk )
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 25 | 25 | 25 | 1 | 50 | 1 | 50 |  | 1,5
| Generating capacity for total power plant (MWe) | 25 | 25 | 25 | 1 | 50 | 1 | 50 |  | 1,5
| Electricity efficiency, net (%), name plate | 32 | 32 | 32 | 25 | 35 | 25 | 35 |  | 1,3,7
| Electricity efficiency, net (%), annual average | 31 | 31 | 31 | 25 | 35 | 25 | 35 |  | 1,3,7
| Forced outage (%) | 7 | 7 | 7 | 5.25 | 8.75 | 5.25 | 8.75 | A | 1
| Planned outage (weeks per year) | 6 | 6 | 6 | 4.5 | 7.5 | 4.5 | 7.5 | A | 1
| Technical lifetime (years) | 25 | 25 | 25 | 18.75 | 31.25 | 18.75 | 31.25 | A | 8,10
| Construction time (years) | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 | A | 10
| Space requirement (1000 m2/MWe) | 35 | 35 | 35 | 26.25 | 43.75 | 26.25 | 43.75 | A | 1,9
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 10 | 10 | 10 | [5 empty] | 3
| Minimum load (% of full load) | 30 | 30 | 30 | [5 empty] | 3
| Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | [5 empty] | 3
| Cold start-up time (hours) | 10 | 10 | 10 | [5 empty] | 3
Environment
| PM 2.5 (mg per Nm3) | 12.5 | 12.5 | 12.5 | [5 empty] | 3
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | [5 empty] | 3
| NOX (g per GJ fuel) | 125 | 125 | 125 | [5 empty] | 3
| CH4 (g per GJ fuel) | 0.94 | 0.94 | 0.94 | [5 empty] | 3
| N2O (g per GJ fuel) | 1.1 | 1.1 | 1.1 | [5 empty] | 3
Financial data
| Nominal investment (M$/MWe) | 2.28 | 2.0748 | 1.824 | 1.48 | 2.57 | 1.5 | 2.6 | B,C | 1,4-8,11
| - of which equipment | 65% | 65% | 65% | 50% | 85% | 50% | 85% |  | 1,2
| - of which installation | 35% | 35% | 35% | 15% | 50% | 15% | 15% |  | 1,2
| Fixed O&M ($/MWe/year) | 54000 | 49700 | 43200 | 43000 | 72000 | 36500 | 61000 | A | 4,5,8,11
| Variable O&M ($/MWh) | 3.4 | 3.128 | 2.72 | 2.8 | 4.6 | 2.4 | 3.9 | A | 5,11
Start-up costs ($/MWe/start-up)
References:
1 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
2 | ASEAN Centre of Energy, 2016, "Levelised cost of electricity generation of selected renewable energy technologies in the ASEAN member states".
3 | Danish Energy Agency and COWI, 2017, "Technology vatalogue for biomass to energy".
4 | IRENA, 2015, "Renewable power generation cost in 2014"
5 | IFC and BMF, 2017, "Converting biomass to energy - A guide for developmers and investors".
6 | OJK, 2014, "Clean Energy Handbook for Financial Service Institutions", Indonesia Financial Service Authority.
7 | IEA-ETSAP and IRENA, 2015, "Biomass for Heat and Power, Technology Brief".
8 | PKPPIM, 2014, "Analisis biaya dan manfaat pembiayaan investasi limbah menjadi energi melalui kredit program", Center for Climate Change and Multilateral Policy Ministry of Finance Indonesia.
9 | India Central Electricity Authority, 2007, "Report on the Land Requirement of Thermal Power Stations".
10 | IEA-ETSAP and IRENA, 2015, "Biomass for Heat and Power, Technology Brief".
11 | Learning curve approach for the development of financial parameters.
Notes:
A | Uncertainty (Upper/Lower) is estimated as +/- 25%.
B | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
C | For 2023, uncertainty ranges are based on cost spans of various sources. For 2050, the values as calcuated in the previous version are used, where we combined the base uncertainity in 2023 with an additional uncertainty span based on learning rates variying between 10-15% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.
D | The boiler in the plant is a suspension fired boiler producing steam to be used in a subsequent back pressure steam turbine. It is possible to pulverize wood pellets and use it for suspension firing but it has not been possible to find an appropriate reference. The system is optimised at DH return temperature 40°C and flow 80°C.

## MSW incineration
Technology
| Technology | Incineration Power Plant - Municipal Solid Waste
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 21.5896 | 22.3341 | 23.0786
| Generating capacity for total power plant (MWe) | 21.5896 | 22.3341 | 23.0786
| Electricity efficiency, net (%), name plate | 29 | 30 | 31 | 28 | 31.5 | 29.5 | 32.5 | A | 1
| Electricity efficiency, net (%), annual average | 28 | 29 | 29.45 | 26.6 | 29.925 | 28.025 | 30.875 |  | 1
| Forced outage (%) | 1 | 1 | 1 | [5 empty] | 1
| Planned outage (weeks per year) | 2.9 | 2.6 | 2.1 | [5 empty] | 1
| Technical lifetime (years) | 25 | 25 | 25 | [5 empty] | 1
| Construction time (years) | 2.5 | 2.5 | 2.5 | [5 empty] | 1
| Space requirement (1000 m2/MWe) | 1.5 | 1.5 | 1.5 | [5 empty] | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 10 | 10 | 10 | 7.5 | 12.5 | 7.5 | 12.5 | C | 1
| Minimum load (% of full load) | 20 | 20 | 20 | 15 | 25 | 15 | 25 | C | 1
| Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.375 | 0.625 | 0.375 | 0.625 | C | 1
| Cold start-up time (hours) | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 | C | 1
Environment
PM 2.5 (mg per Nm3)
SO2 (degree of desulphuring, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
| Nominal investment ( million $/MWe) | 5.97 | 5.5199 | 4.9432 | 4.4775 | 6.1789 | 3.7074 | 6.1789 | C | 1,2
| - of which equipment | 59% | 53.97% | 50% | 44.25% | 73.75% | 37.5% | 62.5% |  | 1
| - of which installation | 41% | 46.03% | 50% | 30.75% | 51.25% | 37.5% | 62.5% |  | 1
| Fixed O&M ($/MWe/year) | 277818 | 238288 | 205110 | 222300 | 347300 | 164100 | 256400 | C | 1
| Variable O&M ($/MWh) | 27.5 | 24.8 | 23.9 | 20.625 | 34.375 | 17.925 | 29.875 | C | 1
Start-up costs ($/MWe/start-up)
Technology specific data
| Waste treatment capacity (tonnes/h) | 27.7 | 27.7 | 27.7 |  |  |  |  | B
References:
1 | Danish Technology Catalogue “Technology Data for Energy Plants, Danish Energy Agency 2022
2 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
Notes:
A | Based on experience from the Netherlands where 30 % electric efficiency is achieve. 1 %-point efficiency subtracted to take into account higher temperature of cooling water in Indonesia (approx. +20 C).
B | A waste treatment capacity of 27,7 tonnes/h is assumed and an energy content of 10,4 GJ/ton. The specific financial data is adjusted to reflect that the plant in Indonesia runs in condensing mode and hence the electric capacity (MWe) is higher than that of a combined heat and power, backpressure plant with the same treatment capacity.
C | Uncertainty (Upper/Lower) is estimated as +/- 25%.
D | Calculated from size, fuel efficiency and an average calory value for waste of 9.7 GJ/ton.

## Landfill
Technology
| Technology | Landfill Gas Power Plant - Municipal Solid Waste
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1 | 1 | 1 | 0.5 | 10 | 0.5 | 10 |  | 1
| Generating capacity for total power plant (MWe) | 1 | 1 | 1 | 0.5 | 10 | 0.5 | 10 |  | 1
| Electricity efficiency, net (%), name plate | 35 | 35 | 35 | 25 | 37 | 25 | 37 |  | 2
| Electricity efficiency, net (%), annual average | 34 | 34 | 34 | 25 | 37 | 25 | 37 |  | 2
| Forced outage (%) | 5 | 5 | 5 | 2 | 15 | 2 | 15 |  | 4
| Planned outage (weeks per year) | 5 | 5 | 5 | 2 | 15 | 2 | 15 |  | 4
| Technical lifetime (years) | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 3
| Construction time (years) | 1.5 | 1.5 | 1.5 | 1 | 3 | 1 | 3 |  | 3
Space requirement (1000 m2/MWe)
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
Ramping (% per minute)
Minimum load (% of full load)
Warm start-up time (hours)
Cold start-up time (hours)
Environment
PM 2.5 (mg per Nm3)
SO2 (degree of desulphuring, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 2.9 | 2.9 | 2.9 | 2.6364 | 3.19 | 2.6364 | 3.335 | A | 3
| - of which equipment | 60% | 60% | 60% | 54.55% | 66% | 54.55% | 69% |  | 5
| - of which installation | 40% | 40% | 40% | 36.36% | 44% | 36.36% | 46% |  | 5
| Fixed O&M ($/MWe/year) | 142500 | 142500 | 142500 | 129550 | 156750 | 129545.4545 | 163875 | A | 3
| Variable O&M ($/MWh) | 15.4 | 15.4 | 15.4 | 13.86 | 16.94 | 13.09 | 17.71
Start-up costs ($/MWe/start-up)
References:
1 | OJK, 2014, "Clean Energy Handbook for Financial Service Institutions", Indonesia Financial Service Authority, Jakarta, Indonesia
2 | Renewables Academy" (RENAC) AG, 2014, "Biogas Technology and Biomass", Berlin, Germany.
3 | IEA-ETSAP and IRENA, 2015. "Biomass for Heat and Power, Technology Brief".
4 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
5 | MEMR, 2015, "Waste to Energy Guidebook", Jakarta, Indonesia.
Notes:
A | Uncertainty (Upper/Lower) is estimated as +/- 10-15%.

## Biogas power plant (small)
Technology
| Technology | Biogas power plant
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1 | 1 | 1 | [5 empty] | 3
| Generating capacity for total power plant (MWe) | 1 | 1 | 1 | [5 empty] | 3
| Electricity efficiency, net (%), name plate | 35 | 35 | 35 | [5 empty] | 4
| Electricity efficiency, net (%), annual average | 34 | 34 | 34 | [5 empty] | 4
| Forced outage (%) | 5 | 5 | 5 | [5 empty] | 1
| Planned outage (weeks per year) | 5 | 5 | 5 | [5 empty] | 1
| Technical lifetime (years) | 25 | 25 | 25 | [5 empty] | 7
| Construction time (years) | 1.5 | 1.5 | 1.5 | [5 empty] | 7
| Space requirement (1000 m2/MWe) | 70 | 70 | 70 | [5 empty] | 12
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 20 | 20 | 20 | 10 | 30 | 10 | 30 |  | 11
| Minimum load (% of full load) | 20 | 30 | 15 | 30 | 50 | 10 | 40 |  | 10
Warm start-up time (hours)
Cold start-up time (hours)
Environment
PM 2.5 (mg per Nm3)
SO2 (degree of desulphuring, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 2.45 | 2.0825 | 1.8375 | 1.67 | 2.31 | 1.3 | 2.2 | B | 3,5,8,9
| - of which equipment | 65% | 65% | 65% | 50% | 85% | 50% | 85% |  | 1,2
| - of which installation | 35% | 35% | 35% | 15% | 50% | 15% | 50% |  | 1,2
| Fixed O&M ($/MWe/year) | 110580 | 101700 | 88500 | 78294 | 130455 | 59043 | 98406 | A | 5,7,9
| Variable O&M ($/MWh) | 0.13 | 0.1196 | 0.104 | 0.1 | 0.2 | 0.1 | 0.1 | A | 6,9
Start-up costs ($/MWe/start-up)
References:
1 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
2 | ASEAN Centre of Energy (2016). Levelised cost of electricity generation of selected renewable energy technologies in the ASEAN member states.
3 | Winrock, 2015, "Buku Panduan Konversi POME Menjadi Biogas, Pengembangan Proyek di Indonesia", USAID – Winrock International.
4 | RENAC, 2014, "Biogas Technology and Biomass, Renewables Academy (RENAC)".
5 | IFC and BMF, 2017, Converting biomass to energy - A guide for developmers and investors".
6 | OJK, 2014, "Clean Energy Handbook for Financial Service Institutions", Indonesia Financial Service Authority.
7 | IEA-ETSAP and IRENA, 2015, "Biomass for Heat and Power, Technology Brief".
8 | PKPPIM, 2014, "Analisis biaya dan manfaat pembiayaan investasi limbah menjadi energi melalui kredit program", Center for Climate Change and Multilateral Policy Ministry of Finance Indonesia.
9 | Learning curve approach for the development of financial parameters.
10 | Vuorinen, A., 2008, "Planning of Optimal Power Systems".
11 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
12 | Chazaro Gerbang Internasional, 2004, "Utilization of Biogas Generated from the Anaerobic Treatment of Palm Oil Mills Effluent (POME) as Indigenous Energy Source for Rural Energy Supply and Electrification - A Pre-Feasibility Study Report"
Notes:
A | Uncertainty (Upper/Lower) is estimated as +/- 25%.
B | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 10-15% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.

## Diesel power plant
Technology
Pollution Prevention and Abatement Handbook, 1998: Toward Cleaner Production, Bind 777
| Technology | Diesel engine (using fuel oil)
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 3 | 3 | 3 | 0.5 | 18 | 0.5 | 18 | E | 7
| Generating capacity for total power plant (MWe) | 14 | 14 | 14 | 1 | 100 | 1 | 100 | E
| Electricity efficiency, net (%), name plate | 46 | 47 | 48 | [5 empty] | 1
| Electricity efficiency, net (%), annual average | 45 | 46 | 47 | 43 | 47 | 45 | 52 |  | 1
| Forced outage (%) | 3 | 3 | 3
| Planned outage (weeks per year) | 1 | 1 | 1 | [5 empty] | 2
| Technical lifetime (years) | 25 | 25 | 25 | [5 empty] | 2
| Construction time (years) | 1 | 1 | 1 | [5 empty] | 2
| Space requirement (1000 m2/MWe) | 0.05 | 0.05 | 0.05 | [5 empty] | 2
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | -
| Capacity factor (%), incl. outages | - | - | -
Ramping configurations
| Ramping (% per minute) | 25 | 25 | 25
| Minimum load (% of full load) | 6 | 6 | 6 |  |  |  |  | A | 1
| Warm start-up time (hours) | 0.05 | 0.05 | 0.05 | [5 empty] | 1
| Cold start-up time (hours) | 0.3 | 0.3 | 0.3
Environment
| PM 2.5 (gram per Nm3) | 20 | 20 | 20 |  |  |  |  | B,C | 3,4
| SO2 (g per GJ fuel) | 224 | 224 | 224 |  |  |  |  | C | 3,4
| NOX (g per GJ fuel) | 280 | 280 | 280 |  |  |  |  | C | 3,4
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 0.912 | 0.912 | 0.8892 | 0.798 | 1.026 | 0.741 | 0.969 | D | 6,7
- of which equipment
- of which installation
| Fixed O&M ($/MWe/year) | 9120 | 9120 | 8847 | [5 empty] | 2
| Variable O&M ($/MWh) | 7.296 | 6.84 | 6.612 | [5 empty] | 2
| Start-up costs ($/MWe/start-up) | - | - | -
References:
1 | Wärtsila, 2011, "White paper Combustion engine power plants", Niklas Haga, General Manager, Marketing & Business Development Power Plants
2 | Danish Energy Agency, 2016, "Technology Data for Energy Plants"
3 | Minister of Environment, Regulation 21/2008
4 | The International Council on Combustion Engines, 2008: Guide to diesel exhaust emissions control of NOx, SOx, particles, smoke and CO2
5 | http://www.bwsc.com/News---Press.aspx?ID=530&PID=2281&Action=1&NewsId=206
6 | BWSC once again to deliver highly efficient power plant in the Faroe Islands.
7 | PLN, 2023, data provided the System Planning Division at PLN
Notes:
A | 30 % minimum load per unit - corresponds to 6% for total plant when consisting of 5 units
B | Total particulate matter
C | Typical diesel exhaut emission according to Ref 3 (average of interval) unless this number exceeds the maximum allowed emission according to Minister of Environment Regulation 21/2008. Both SO2 and particulates are dependant on the fuel composition.
D | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
E | Based on data collection from Indonesian projects

## Nuclear PWR
Technology
| Technology | Nuclear power plant - PWR
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1000 | 1000 | 1000
| Generating capacity for total power plant (MWe) | 2000 | 2000 | 2000 |  |  |  |  | B
| Electricity efficiency, net (%), name plate | 36.53 | 38 | 42 |  |  |  |  | C | 4
| Electricity efficiency, net (%), annual average | 33.64 | 36 | 40 |  |  |  |  | C | 4
| Forced outage (%) | 2 | 2 | 2 | [5 empty] | 4
| Planned outage (weeks per year) | 9% | 8% | 6% | [5 empty] | 4
| Technical lifetime (years) | 60 | 60 | 60 | [5 empty] | 1,4
| Construction time (years) | 7.4 | 7.4 | 7.4 | 4 | 10 |  |  |  | 1,4
| Space requirement (1000 m2/MWe) | 2.6206 | 2.6206 | 2.6206 | 2.023 | 3.3663 | 2.023 | 3.3663 | D | 8,9
Additional data for non thermal plants
Capacity factor (%), theoretical
Capacity factor (%), incl. outages
Ramping configurations
| Ramping (% per minute) | 4 | 4 | 3 | 3 | 5 |  |  | A | 5,4
| Minimum load (% of full load) | 25 | 25 | 25 |  |  |  |  | A | 5
| Warm start-up time (hours) | 2 | 2 | 1 | 2 | 6 |  |  |  | 5
| Cold start-up time (hours) | 30 | 30 | 30 | 24 | 48 |  |  |  | 4
Environment
| PM 2.5 (mg per Nm3) | - | - | -
| SO2 (degree of desulphuring, %) | - | - | -
| NOx (g per GJ fuel) | - | - | -
| CH4 (g per GJ fuel) | - | - | -
| N2O (g per GJ fuel) | - | - | -
Financial data
| Nominal investment (M$/MWe) | 9 | 7.9 | 6.8 | 7 | 12 | 5 | 10 | E,F,G | 2,3,7,10
| - of which equipment | 33% | 33% | 33% |  |  |  |  | F
| - of which installation | 67% | 67% | 67% |  |  |  |  | F
| Fixed O&M ($/MWe/year) | 127000 | 120000 | 113000 | 20000 | 180000 | 20000 | 180000 |  | 2,3
| Variable O&M ($/MWh) | 2.4 | 2.3 | 2.2 | 1.8 | 3 | 1.65 | 2.75 | I | 2,3,7
| Start-up costs ($/MWe/start-up) | - | - | -
References:
1 | N. IEA, “Projected cost of generating electricity 2020 Edition,” Int. ENERGY AGENCY Nucl. ENERGY AGENCY Organ. Econ. CO-OPERATION Dev., no. January, p. 112, 2020, [Online]. Available: https://ncdc.gov.ng/themes/common/docs/protocols/111_1579986179.pdf
2 | O. NEA, “Unlocking Reductions in the Construction Costs of Nuclear: A Practical Guide for Stakeholders,” 2020. doi: 10.1787/9789264303119-en.
3 | “Economics of Nuclear Power(Updated August 2022).” https://world-nuclear.org/information-library/economic-aspects/economics-of-nuclear-power.aspx#CapitalCosts
4 | NEA, “Technical and Economic Aspects of Load Following with Nuclear Power Plants,” 2023.Nuclear Power Reactors in the World ¦ IAEA
5 | NEA, “Technical and Economic Aspects of Load Following with Nuclear Power Plants,” 2011. https://www.oecd-nea.org/upload/docs/application/pdf/2021-12/technical_and_economic_aspects_of_load_following_with_nuclear_power_plants.pdf
6 | https://www.voanews.com/a/pakistan-signs-4-8-billion-nuclear-power-plant-deal-with-china/7144967.html
7 | NREL, Annual Technology Baseline (ATB) 2023, https://atb.nrel.gov/electricity/2023/data
8 | US Dept. of Energy, Office of Nuclear Energy. The ultimate fast facts guide to Nuclear Energy.
9 | STRATA. The Footprint of Energy: Land use of US Electricity Production 2017
10 | Lazard LCOE+ April 2023
Notes:
A | Ramping and minimum load are constrained by the core stability'. Minimum requirements are usually set by the regulation.
B | A two-unit configuration is typical in nuclear power plants, but more units can be combined.
C | Generation IV reactors are expected to achieve efficiencies well above 45%. In the future, nuclear reactors are likely' to run often at partial load - thus the gap between nameplate and net efficiency
D | Nuclear power plants have a very' high energy' density' in terms of area required. The values represented here are for the area needed for the plants. However, there can be a higher requirement based on government regulation and environmental concerns F High variation in cost seen between US. EU costs and China. India costs. Moreover, this also depends on technology'. Here the chosen values are estimated based on a mix of values available along with employing the learning curve approach used for financial parameters.
E | Decommissioning costs usually are the 15% of the total investment cost, is not included in the onvestment cost
F | The CAPEX breakdown is composed by 33% share of direct cost (i.e., Equipment, Labour, Construction, Materials and Building), 37% of Indirect cost (i.e., Design services, Construction and Supervision and project management, Commissioning and startup costs), 17% of Financial costs, 10% of Owner's cost.
G | The development of the overnigth cost is based on NREL ATB 2023
H | CAPEX is in line with NREL ATB 2023 (overnight capital costs + construction financing costs)
I | Uncertainty (Upper/Lower) is estimated as +/- 25%.

## Nuclear SMR
Technology
| Technology | Nuclear power plant - SMR (Land based Water-cooled)
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data
| Generating capacity for one unit (MWe) | 80 | 80 | 80 | [5 empty] | 2,3,4
| Generating capacity for total power plant (MWe) | 300 | 300 | 300 | 10 | 300 | 10 | 300 |  | 2,3,4
| Electricity efficiency, net (%), name plate | 27 | 27 | 30 |  |  |  |  | B | 2
| Electricity efficiency, net (%), annual average | 27 | 27 | 30 |  |  |  |  | B | 2,1,4
| Forced outage (%) | 3 | 3 | 3 | [5 empty] | 2,1
| Planned outage (weeks per year) | 6.5% | 6% | 5% | 3% | 7% |  |  |  | 2
| Technical lifetime (years) | 30 | 40 | 50 | [5 empty] | 2,3
| Construction time (years) | 9 | 8 | 4 | 8 | 12 | 4 | 12 | G | 2,3, 13
| Space requirement (1000 m2/MWe) | 0.63823 | 0.63823 | 0.63823 | 0.041791 | 1.6 | 0.041791 | 1.6 | C | 11
Additional data for non thermal plants
Capacity factor (%), theoretical
Capacity factor (%), incl. outages
Ramping configurations
| Ramping (% per minute) | 1.2 | 1.2 | 1.2 |  |  |  |  | A | 2.5
| Minimum load (% of full load) | 25 | 25 | 20 |  |  |  |  | A | 1,2,5
| Warm start-up time (hours) | 1.5 | 1.5 | 1.5 | [5 empty] | 2.5
| Cold start-up time (hours) | 24 | 24 | 24
Environment
| PM 2.5 (mg per Nm3) | - | - | -
| SO2 (degree of desulphuring, %) | - | - | -
| NOx (g per GJ fuel) | - | - | -
| CH4 (g per GJ fuel) | - | - | -
| N2O(g per GJ fuel) | - | - | -
Financial data
| Nominal investment (M$/MWe) |  | 9.6 | 7.3 | 5.6 | 20 | 5 | 10 | D,E | 8,10,12,13
| - of which equipment |  | 33% | 33% | [5 empty] | 2,3,6
| - of which installation |  | 67% | 67% | [5 empty] | 2,3,6
| Fixed O&M ($/MWe/year) |  | 110000 | 102000 | [5 empty] | 2,3,6
| Variable O&M ($/MWh) |  | 2.2 | 2.1 |  |  |  |  | F | 2,3,6
Start-up costs ($/MWe/start-up)
References:
1 | WNA Word Nuclear Association, economics of Nuclear Power (Updated August 2022) - https://www.world-nuclear.org/information-library/economic-aspects/economics-of-nuclear-power.aspx#ECSArticleLink1
2 | IAEA Nuclear Energy Seiries No. Nr-T-1.18 Technology Roadmap for small Modular Reactor Deployment, 2021- https://www-pub.iaea.org/MTCD/Publications /PDF/PUB1944_web.pdf
3 | M. A. Rahmanta, A. W. Harto, A. Agung, and M. K. Ridwan, “Nuclear Power Plant to Support Indonesia’s Net Zero Emissions: A Case Study of Small Modular Reactor Technology Selection Using Technology Readiness Level and Levelized Cost of Electricity Comparing Method,” Energies, vol. 16, no. 9, p. 3752, Apr. 2023
4 | Goswami GG, Rahman U, Chowdhury M. Estimating the economic cost of setting up a nuclear power plant at Rooppur in Bangladesh. Environ Sci Pollut Res Int. 2022 May;29(23):35073-35095. doi: 10.1007/s11356-021-18129-3. Epub 2022 Jan 19. PMID: 35044606; PMCID: PMC8767363.
5 | IAEA, “Technology Roadmap for Small Modular Reactor Deployment, IAEA Nuclear Energy Series No. NR-T-1.18,” 2021, [Online]. Available: https://www-pub.iaea.org/MTCD/Publications/PDF/PUB1944_web.pdf
6 | https://iea.blob.core.windows.net/assets/ad5a93ce-3a7f-461d-a441-8a05b7601887/Nuclear_Power_in_a_Clean_Energy_System.pdf
7 | IAEA, “Advances in Small Modular Reactor Technology Developments A Supplement to: IAEA Advanced Reactors Information System (ARIS) 2022 Edition,” 2022, [Online]. Available: https://aris.iaea.org/Publications/SMR_booklet_2022.pdf - SMR_booklet_2022.pdf (iaea.org)
8 | NREL, Annual Technology Baseline (ATB) 2023, https://atb.nrel.gov/electricity/2023/data
9 | IAEA, “Advances in Small Modular Reactor Technology Developments”, 2020
10 | S. Boarin1, M. Mancini1, M. Ricotti1, G. Locatelli2, Economics and financing ofsmall modular reactors (SMRs).
11 | Giorgio Locatelli, Benito Mignacca, Small Modular Nuclear Reactors
12 | B. Mignacca, G. Locatelli, “Economics and finance of Small Modular Reactors: A systematic review and research agenda”, Renewable and Sustainable Energy Reviews (2020), (https://doi.org/10.1016/j.rser.2019.109519)
13 | Eye-popping new cost estimates released for NuScale small modular reactor, IEEFA, January 2023 https://ieefa.org/resources/eye-popping-new-cost-estimates-released-nuscale-small-modular-reactor
Notes:
A | Ramping and minimum load are constrained by the core stability'. Minimum requirements are usually set by the regulation.
B | Generation IV reactors are expected to achieve efficiencies well above 45%. In the future, nuclear reactors are likely' to run often at partial load - thus the gap between nameplate and net efficiency
C | Nuclear power plants have a ' high energy' density' in terms of area required. The values represented here are for the area needed for the plants. However, there can be a higher requirement based on government regulation and environmental concerns F High variation in cost seen between US. EU costs and China. India costs. Moreover, this also depends on technology'. Here the chosen values are estimated based on a mix of values available along with employing the learning curve approach used for financial parameters.
D | Decommissioning costs usually are the 15% of the total investment cost
E | The CAPEX breakdown is composed by 33% share of direct cost (i.e., Equipment, Labour, Construction, Materials and Building), 37% of Indirect cost (i.e., Design services, Construction and Supervision and project management, Commissioning and startup costs), 17% of Financial costs, 10% of Owner's cost.
F | The main characteristic are taken from CAREM-25
G | +109 mdr: China, however, managed to connect its first SMR, one of two 100 MW HTR-PM reactors, to the grid on 20 December 2021.Construction only began in 2012, and by then the time estimate for construction had increased to '50 months'. In reality, the first unit took almost 109 months from first concrete to mains connection, more than twice as long as expected

## Utility-scale Lithium-ion
Technology
| Technology | Batteries - Lithium-ion (utility-scale)
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Energy storage capacity for one unit (MWh) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | A, B
| Discharge time (hours) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | A, B
| Round-trip efficiency (%) AC | 90 | 92 | 92 |  |  |  |  | C | 1
| Round-trip efficiency (%) DC | 95 | 96 | 96 |  |  |  |  | C | 1
| Self-discharge rate (%/day) | 0.1 | 0.1 | 0.1 | [5 empty] | 2
| Forced outage (%) | 0.38 | 0.35 | 0.25 |  |  |  |  | M
| Planned outage (weeks per year) | 0.2 | 0.1 | 0.1 |  |  |  |  | L
| Technical lifetime (cycles) | 7500 | 10000 | 15000 |  |  |  |  | M | 3
| Technical lifetime (years) | 15 | 20 | 25 |  |  |  |  | D | 3
| Construction time (years) | 0.2 | 0.2 | 0.2
| Energy density (Wh/kg) | 150 | 200 | 300
Ramping configurations
| Response time from idle to full-rated discharge (ms) | 50 | 50 | 50 | [5 empty] | 4
| Response time from full-rated charge to discharge (sec) | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | O | 7
Financial data
| Total investment (MUSD/MWh) | 0.47127 | 0.32792 | 0.22908 | 0.3505 | 0.53575 | 0.16773 | 0.44751 | G | 1,5,6,10
| - energy component (MUSD/MWh) | 0.347 | 0.227 | 0.146 | 0.26 | 0.378 | 0.12 | 0.255 |  | 1,5,6,9,11
| - power component (MUSD/MW) | 0.329 | 0.294 | 0.25 | 0.242 | 0.351 | 0.1 | 0.27 | H | 1,5,6,9,11
| - other project costs (MUSD/MWh) | 0.042017 | 0.027423 | 0.020581 | 0.03 | 0.07 | 0.022729 | 0.12501 | N | 5,6,9
| Fixed O&M (USD/MW/year) | 15000 | 10500 | 7350 | 5000 | 50000 | 2500 | 15000 | O | 6,9,10
| Variable O&M (USD/MWh) | 2 | 1.8 | 1.6 | 2 | 2.6 | 1.6 | 2.2 | I | 7,10
Technology specific data
| Energy storage expansion cost (MUSD/MWh) | 0.277 | 0.18079 | 0.13568 |  |  |  |  | F
| Output capacity expansion cost (MUSD/MW) | 0.257 | 0.16774 | 0.12589
| Total investment (MUSD/MW) | 1.3311 | 0.95011 | 0.64496
References:
1 | NREL, Cost Projections for Utility-Scale Battery Storage: 2023 Update
2 | Fan Xiayue, "Battery technologies for grid-level large-scale electrical energy storage", Transactions of Tianjin University, Springer, 2020.
3 | Environmental end energy study institute, Energy storage factsheet, https://www.eesi.org/papers/view/energy-storage-2019.
4 | D.M. Greenwood, K.Y. Lim, C. Patsios, P.F. Lyons, Y.S. Lim, P.C. Taylor, Frequency response services designed for energy storage, Appl. Energy. 203 (2017) 115–127.
5 | Bloomberg New Energy Finance. New Energy Outlook 2022, 2022.
6 | NREL Annual Technology Baseline (ATB) 2023
7 | B. Zakeri, S. Syri, Electrical energy storage systems: A comparative life cycle cost analysis, Renew. Sustain. Energy Rev. 42 (2015) 569–596.
8 | G. Huff, A.B. Currier, B.C. Kaun, D.M. Rastler, S.B. Chen, D.T. Bradshaw, W.D. Gauntlett, DOE/EPRI electricity storage handbook in collaboration with NRECA, (2015).
9 | DEA, Technology Data for Energy Storage
10 | Lazard, 2023, Lazard's Levelised Cost of Storage Analysis - Version 8.0
11 | The-Future-of-Energy-Storage-MIT-2022
Notes:
A | A 4-hour battery has been picked as a reference, as there is more data availbe for this power-to-energy ratio in the references listed.
B | Power and energy output can be scaled linearly by utilizing many modules (up to 250 MW has been demonstrated, https://www.pv-magazine-australia.com/2023/08/10/battery-capacity-overtakes-pumped-hydro-in-nem/). Output capacity expansion can be done reprogramming the management unit without any new battery module. For Utility batteries the ratio between energy storage and capacity is in general between 1 and 10 (C-rate between 1/10 and 1) only rarly the ration will be below 1.
C | The gradual change towards lower C-rates following the transition from frequency regulation to renewable integration promotes lower C-rates. Therefore the average DC roundtrip efficiency is expected to increase slightly. The RT eff. vs. C-rate is exemplified in Figure 7 [3,51]. The AC roundtrip efficiency includes losses in the power electronics and is 2-4% lower than the DC roundtrip efficiency. The total roundtrip efficiency further includes standby losses making the total roundtrip efficiency typically ranging between 80% and 90%. [21,22]
D | Samsung SDI 2016 whitepaper on ESS solutions provide 15 year lifetime for current modules operating at C =1/2 to C=3. Steady improvement in battery lifetime due to better materials and battery management expected. Number of cycles can be a more meaningful lifetime indicator.
E | The discharge time is the amount of hours the battery can discharge at rated output capacity. It equals the Energy/Power ratio corrected for the discharge efficiency.
F | Since multi-MWh LIB systems are scalar, the energy and outputr capacity expansion costs are here estimated to be equal to the energy and output capacity components plus the “other costs”
G | Power conversion cost is strongly dependent on scalability and application.
H | The gradual change towards lower C-rates following the transition from frequency regulation to renewable integration promotes lower C-rates. Therefore the average DC roundtrip efficiency is expected to increase slightly. The RT eff. vs. C-rate is exemplified in Figure 7 [3,51]. The AC roundtrip efficiency includes losses in the power electronics and is 2-4% lower than the DC roundtrip efficiency. The total roundtrip efficiency further includes standby losses making the total roundtrip efficiency typically ranging between 80% and 90%
I | Cost per MWh of energy discharged from the battery
L | It is expected not to have any outage during lifetime of the grid-connected LIB. Only a few days during the e.g. 15 years life time is needed for service and exchanging fans and blowers for thermal management system and power conversion system. Forced outage is expected to drop with increasing robustness following the learning rate and cumulated production. Planned outage is expected to decrease after 2020 due to increased automation.
M | Cycle life specified as the number of cycles at 1C/1C to 80% state-of-health. Samsung SDI 2016 whitepaper on ESS solutions provide 15 year lifetime for current modules operating at C/2 to 3C [14]. Steady improvement in battery lifetime due to better materials and battery management is expected. Kokam ESS solutions are also rated at more than 8000-20000 cycles (80-90% DOD) based on chemistry [3]. Thus for daily full charge-discharge cycles, the batteries are designed to last for 15-50 years if supporting units are well functioning. Lifetimes are given for both graphite and LTO anode based commercial batteries from Kokam.
N | Other costs include construction costs and entrepreneur work. These costs heavily dependent on location, substrate and site access. Power cables to the site and entrepreneur work for installation of the containers are included in other costs. Therefore other costs are assumed to – roughly – correlate with the system size. Automation is expected to decrease other costs from 2030 and onwards.
O | The response time is obtained from simulated response time experiments with hardware in the loop.

## Hydro pumped storage
Technology
| Technology | Hydro pumped storage
|  | 2023 | 2030 | 2050 | Uncertainty (2023) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 250 | 250 | 250 | 100 | 500 | 100 | 500 | A | 1,6
| Generating capacity for total power plant (MWe) | 1000 | 1000 | 1000 | 100 | 4000 | 100 | 4000 |  | 1,6
| Electricity efficiency, net (%), name plate | 80 | 80 | 80 | 75 | 82 | 75 | 82 |  | 1,3,5
| Electricity efficiency, net (%), annual average | 80 | 80 | 80 | 75 | 82 | 75 | 82 |  | 1,3,5
| Forced outage (%) | 4 | 4 | 4 | 2 | 7 | 2 | 7 |  | 5
| Planned outage (weeks per year) | 3 | 3 | 3 | 2 | 6 | 2 | 6 |  | 5
| Technical lifetime (years) | 60 | 60 | 60 | 50 | 90 | 40 | 90 |  | 1
| Construction time (years) | 6 | 5 | 4 | 3 | 9 | 2 | 6 | B | 1
| Space requirement (1000 m2/MWe) | 30 | 30 | 30 | 15 | 45 | 15 | 45 |  | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | - | F
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 50 | 50 | 50 | 10 | 100 | 10 | 100 |  | 2,5
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 2
| Cold start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 2
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 1.2 | 1.2 | 1.2 | 0.6 | 6 | 0.6 | 6 | C,E | 1,3,4,8
| - of which equipment | 30% | 30% | 30% | 20% | 50% | 20% | 50% |  | 7
| - of which installation | 70% | 70% | 70% | 50% | 80% | 50% | 80% |  | 7
| Fixed O&M ($/MWe/year) | 18700 | 18700 | 18700 | 4000 | 30000 | 4000 | 30000 |  | 4
| Variable O&M ($/MWh) | 0.935 | 0.935 | 0.935 | 0.5 | 3 | 0.5 | 3 |  | 1,4
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
Technology specific data
| Size of reservoir (MWh) | 10000 | 10000 | 10000 | 3000 | 20000 | 3000 | 20000 | D | 1,6,9
| Load/unload time (hours) | 10 | 10 | 10 | 4 | 12 | 4 | 12 | D | 1,6,9
References:
1 | MEMR Focus Group Discussions with various stakeholders for the purposes of updating the Technology Catalogue in 2023
2 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".
3 | Lazard, Lazard's Levelized Cost of Storage (2023).
4 | NREL Annual Technology Baseline (ATB) 2023
5 | U.S. Department of Energy, 2015, “Hydropower Market Report”.
6 | Connolly, 2009, "A Review of Energy Storage Technologies - For the integration of fluctuating renewable energy".
7 | IRENA, 2012, "Renewable Energy Technologies: Cost Analysis Series - Hydropower".
8 | World Bank, 2021: Development of Pumped Storage Hydropower in Java Bali System Project
9 | PLN 2020, Environmental and Social Management Plan (ESMP): Upper Cisokan Pumped Storage Hydropower Project 1040 MW
Notes:
A | Size per turbine.
B | Uncertainty (Upper/Lower) is estimated as +/- 50%.
C | Numbers are very site sensitive. There will be an improvement by learning curve development, but this improvement will equalized because the best locations will be utilized first. The investment largely depends on civil work.
D | The size of the total power plant and not per unit (turbine).
E | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.