## Index
Intro | Technology Data for power and heat production plants
alldata_flat
01 Coal CHP | This file contains technology data sheets related to generation of electricity and district heating. The data sheets are continuously updated as technologies evolve, if the data changes significantly or if errors are found.
02 LTE existing plant | Dates and descriptions of updates are listed in the ammendment sheet below.
03a Coal to wood pellets exi bo
03b Coal to wood chips n. boile | Additional information about the syntax of parameters and units in the datatabels is listed below.
03c coal to wood chips exi. boi | Parameter structure: parameter name (extra info) [unit]. For financial parameters priceyear is expressed as: [priceyear-unit]
03d coal to wood chips exi. boi | Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
04 Gas turb. simple cycle, L | The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
04 Gas turb. simple cycle Sm-Me | The sheet alldata_flat contains all technology data in this catalogue in a flat format.
04 Gas turb. simple cycle Micro | All cost data is in | 2020 | EURO
05 Gas turb. CC, steam extract. | License:
05 Gas turb. CC, Back-pressure | This work is licensed under Attribution 4.0 International
06 Gas engines, natural gas
06 Gas engines, biogas | Ammendment sheet
08 WtE CHP, Large, 40 degree | Date | Sheet | Change | Notes
08 WtE CHP, Large, 50 degree | 2023-08-23 | all sheets | Update to 2020 prices
08 WtE CHP, Medium | 2022-06-01 | 40 Heat pumps | Addition of datasheet about CO2 heat pumps
08 WtE CHP, Small | 2022-06-01 | 45 Geothermal | Addition of datasheet about large scale geothermal with electric heat pump
08 WtE HOP | mar-22 | 21 Offshore and near shore turbines | Offshore and Nearshore turbines updated. Financial data now in 2020€.
09a Wood Chips, Large 40 degree | feb-22 | 22 Photovoltaics | All datasheets for PV systems updated. Financial data now in 2020€.
09a Wood Chips, Large 50 degree | apr-20 | 40 Heat pumps | Compression heat pumps (electric) updated. Datasheets now divided in 3 types and different plant sizes.
09a Wood Chips, Medium | apr-20 | 45 Geothermal | Datasheets updated and now divided in 1200 m and 2000 m depth, electric- and absorption heat pumps and 2 different district heating temperatures.
09a Wood Chips, Small | mar-20 | 09a medium and large biomass HOP | added datasheets of medium and large biomass HOP
09b Wood Pellets, Large 40 degr | mar-20 | 09 Biomass plants | minor update of existing biomass datasheets
09b Wood Pellets, Large 50 degr | jan-20 | 09 Biomass plants | datasheets updated
09b Wood Pellets, Medium | nov-19 | 22 Photovoltaics Large | Updated data sheet for large utility scale PV systems
09b Wood Pellets, Small | nov-19 | 22 Photovoltaics Tracker | New data sheet for large utility scale PV systems with single axis tracker
09c Straw, Large, 40 degree | sep-19 | 21 Near shore turbines | minor adjustment
09c Straw, Large, 50 degree | jun-19 | 03 Rebuilding large coal power plants to biomass | Added Datasheet d for rebuild coal fired plants to chips backpressure plant. Updated datasheets a and b for rebuild coal fired plants to wood pellets
09c Straw, Medium | maj-19 | 20 Wind turbines, on-shore | onshore and domestic turbines updated
09c Straw, Small | maj-19 | 21 Offshore and near shore turbines | offshore and nearshore tubrines updated
09a Wood Chips HOP, small | nov-18 | 50-52 peak plants | datasheets added for diesel engine farms, natural gas engine plant and open cycle gas turbines.
09a Wood Chips HOP, medium | okt-18 | 46 Solar District Heating | update
09a Wood Chips HOP, large | mar-18 | 08 WtE plants | datasheets added
09b Wood Pellets HOP | jan-18 | 04, 05 and 06 gas turbines and engines
09c Straw HOP | jan-18 | 11 Solid oxide fuel cell (SOFC) CHP, natural gas/biogas | datasheets added
09a Wood Chips extract. plant | jan-18 | 12 Low temperature proton exchange membrane fuel cell (LT-PEMFC) CHP, hydrogen
09b Wood Pellets extract. plant | jan-18 | 41 Electric Boiler | update
10 Stirling | jan-18 | 44 District heating boilers, Gas fired | update
11 SOFC-CHP | nov-17 | 01 Supercritical Pulverized Fuel Power Plant - Coal CHP
12 LT-PEMFC CHP
20 Onshore turbines | Version: 12, poweranddh_2022_06_21
20 Domestic turbines
21 Offshore turbines
21 Near shore turbines
22 Rooftop PV residential
22 Rooftop PV commercial & industrial
22 Utility-scale ground mounted PV
22 Utility-scale ground mounted PV tracker
23 Wave Energy
40 Comp. hp, airsource 1 MW
40 Comp. hp, airsource 3 MW
40 Comp. hp, airsource 10 MW
40 Comp. hp, excess heat 1 MW
40 Comp. hp, excess heat 3 MW
40 Comp. hp, excess heat 10 MW
40 Comp. hp, seawater 20 MW
40 Absorption heat pump, DH
40 co2. hp, seawater 50-100 MW
41 Electric boiler, small
41 Electric boiler, large
44 Natural Gas DH Only
45.1.a Geothermal DH, 1200m, E
45.1.b Geothermal DH, 2000m, E
45.2.a Geothermal DH, 1200m, A
45.2.b Geothermal DH, 2000m, A
45.3.a Geoth. DH, 1200m, E (LT)
45.3.b Geoth DH, 2000m, E (LT)
45.4 Geothermal DH, E lar scale
46 Solar District Heating
50 Diesel engine farm
51 Natural gas engine plant
52 OCGT - Natural gas
52 OCGT - Light fuel oil

## alldata_flat
ws | Technology | cat | par | unit | priceyear | note | ref | est | year | val
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | A |  | ctrl | 2015 | 0.75
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | A |  | ctrl | 2020 | 0.84
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | A |  | ctrl | 2030 | 1.01
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Construction time [years] | years |  |  | [2, 3, 3] | ctrl | 2015 | 4.5
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Construction time [years] | years |  |  | [2, 3, 3] | ctrl | 2020 | 4.5
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Construction time [years] | years |  |  | [2, 3, 3] | ctrl | 2030 | 4.5
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  | 1 | ctrl | 2015 | 0.15
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  | 1 | ctrl | 2020 | 0.15
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  | 1 | ctrl | 2030 | 0.15
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | C | [8, 7, 9, 11] | ctrl | 2015 | 0.46
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | C | [8, 7, 9, 11] | ctrl | 2020 | 0.485
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | C | [8, 7, 9, 11] | ctrl | 2030 | 0.52
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | C | [8, 7, 9, 11] | ctrl | 2050 | 0.535
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2015 | 500
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2020 | 500
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2030 | 500
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2050 | 500
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 6 | ctrl | 2015 | 25
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 6 | ctrl | 2020 | 25
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 6 | ctrl | 2030 | 25
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 6 | ctrl | 2050 | 25
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2015 | 1.5
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2020 | 1.5
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2030 | 1.5
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2050 | 1.5
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2015 | 0.8
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2020 | 0.8
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2030 | 0.8
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2050 | 0.8
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | B | [12, 5, 5, 5] | ctrl | 2015 | 38
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | B | [12, 5, 5, 5] | ctrl | 2020 | 35
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | B | [12, 5, 5, 5] | ctrl | 2030 | 35
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | B | [12, 5, 5, 5] | ctrl | 2050 | 35
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | SO2 (degree of desulphuring) [] |  |  | B | 5 | ctrl | 2015 | 0.97
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | SO2 (degree of desulphuring) [] |  |  | B | 5 | ctrl | 2020 | 0.97
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | SO2 (degree of desulphuring) [] |  |  | B | 5 | ctrl | 2030 | 0.97
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Environment | SO2 (degree of desulphuring) [] |  |  | B | 5 | ctrl | 2050 | 0.97
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2015 | 35618.9884
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2020 | 35053.6077
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2030 | 34324.4022
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2050 | 32911.1764
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2015 | 2.1824
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2020 | 2.1484
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2030 | 2.1032
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2050 | 2.0128
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2015 | 3.3357
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2020 | 3.2792
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2030 | 3.2114
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2050 | 3.0757
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | [10, 14] | ctrl | 2015 | 0.18
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | [10, 14] | ctrl | 2020 | 0.15
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | [10, 14] | ctrl | 2030 | 0.15
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | [10, 14] | ctrl | 2050 | 0.1
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | D | 14 | ctrl | 2015 | 0.05
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | D | 14 | ctrl | 2020 | 0.05
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | D | 14 | ctrl | 2030 | 0.05
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | D | 14 | ctrl | 2050 | 0.05
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 14 | ctrl | 2015 | 0.04
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 14 | ctrl | 2020 | 0.04
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 14 | ctrl | 2030 | 0.04
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 14 | ctrl | 2050 | 0.04
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Technology-specific data | Availability [] |  |  | E | 7 | ctrl | 2015 | 0.95
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Technology-specific data | Availability [] |  |  | E | 7 | ctrl | 2020 | 0.95
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Technology-specific data | Availability [] |  |  | E | 7 | ctrl | 2030 | 0.95
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Construction time [years] | years |  |  | 7 | ctrl | 2015 | 0.5
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Construction time [years] | years |  |  | 7 | ctrl | 2020 | 0.5
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Construction time [years] | years |  |  | 7 | ctrl | 2030 | 0.5
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, F] | 7 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [E, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [E, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [E, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [E, F] | 7 | lower | 2020 | -0.01
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [E, F] | 7 | upper | 2020 | 0.01
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [E, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [E, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [E, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [E, F] | 7 | lower | 2020 | -0.01
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [E, F] | 7 | upper | 2020 | 0.01
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | [A, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | [A, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | [A, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | [A, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | [A, F] | 7 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2015 | 300
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2020 | 300
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2030 | 300
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2020 | 200
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2050 | 200
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2020 | 400
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2050 | 400
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | [A, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | [A, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | [A, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | [A, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | [A, F] | 7 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, F] |  | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, F] |  | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, F] |  | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, F] |  | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, F] |  | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Technical lifetime [years] | years |  |  | [4, 5, 6, 7] | ctrl | 2015 | 15
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Technical lifetime [years] | years |  |  | [4, 5, 6, 7] | ctrl | 2020 | 15
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Energy/technical data | Technical lifetime [years] | years |  |  | [4, 5, 6, 7] | ctrl | 2030 | 15
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | CH4 (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | CH4 (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | CH4 (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | CH4 (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | CH4 (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | N2O (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | N2O (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | N2O (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | N2O (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | N2O (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | NOX (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | NOX (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | NOX (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | NOX (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | NOX (additional to existing plant) [g/GJ_i] | g/GJ_i |  | [A, F, G] | 8 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | SO2 (degree of desulphuring, additional to existing plant) [] |  |  | [A, F, G] | 8 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | SO2 (degree of desulphuring, additional to existing plant) [] |  |  | [A, F, G] | 8 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | SO2 (degree of desulphuring, additional to existing plant) [] |  |  | [A, F, G] | 8 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | SO2 (degree of desulphuring, additional to existing plant) [] |  |  | [A, F, G] | 8 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Environment | SO2 (degree of desulphuring, additional to existing plant) [] |  |  | [A, F, G] | 8 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [A, B, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [A, B, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [A, B, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [A, B, F] | 7 | ctrl | 2050 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [A, B, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [A, B, F] | 7 | lower | 2050 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [A, B, F] | 7 | upper | 2020 | 8506.9817
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [A, B, F] | 7 | upper | 2050 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, F] | [4, 5, 6, 7] | ctrl | 2015 | 0.25521
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, F] | [4, 5, 6, 7] | ctrl | 2020 | 0.25521
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, F] | [4, 5, 6, 7] | ctrl | 2030 | 0.25521
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, F] | [4, 5, 6, 7] | ctrl | 2050 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, F] | [4, 5, 6, 7] | lower | 2020 | 0.15951
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, F] | [4, 5, 6, 7] | lower | 2050 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, F] | [4, 5, 6, 7] | upper | 2020 | 0.36155
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, F] | [4, 5, 6, 7] | upper | 2050 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, D, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, D, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, D, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, D, F] | 7 | ctrl | 2050 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, D, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, D, F] | 7 | lower | 2050 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, D, F] | 7 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, D, F] | 7 | upper | 2050 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | [A, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | [A, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | [A, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | [A, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | [A, F] | 7 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, F] | 7 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, F] | 7 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, F] | 7 | upper | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, C, I] | 10 | ctrl | 2015 | -0.02
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, C, I] | 10 | ctrl | 2020 | -0.02
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, C, I] | 10 | ctrl | 2030 | -0.02
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, C, I] | 10 | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, C, I] | 10 | upper | 2020 | -0.05
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Construction time [years] | years |  | C | 10 | ctrl | 2015 | 2
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Construction time [years] | years |  | C | 10 | ctrl | 2020 | 2
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Construction time [years] | years |  | C | 10 | ctrl | 2030 | 2
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Construction time [years] | years |  | C | 10 | lower | 2020 | 1.5
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Construction time [years] | years |  | C | 10 | upper | 2020 | 2.5
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, C] | 10 | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, C] | 10 | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, C] | 10 | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, C] | 10 | lower | 2020 | -0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | [A, C] | 10 | upper | 2020 | 0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | ctrl | 2015 | -0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | ctrl | 2020 | -0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | ctrl | 2030 | -0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | upper | 2020 | -0.02
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | ctrl | 2015 | -0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | ctrl | 2020 | -0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | ctrl | 2030 | -0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, C, I] | 10 | upper | 2020 | -0.02
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | lower | 2020 | -0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | upper | 2020 | 0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2015 | 300
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2020 | 300
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2030 | 300
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2020 | 200
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2020 | 400
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | upper | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] |  | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] |  | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] |  | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] |  | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] |  | upper | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  | C | 10 | ctrl | 2015 | 15
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  | C | 10 | ctrl | 2020 | 15
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  | C | 10 | ctrl | 2030 | 15
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | lower | 2020 | 3.1
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | upper | 2020 | 3.1
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 1
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 1
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 1
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | lower | 2020 | 0.8
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | upper | 2020 | 0.8
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 20
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 21
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 18
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | lower | 2020 | 19
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | upper | 2020 | 53
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2015 | 0.3
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0.3
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0.3
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Fixed O&M [EUR/MWe/year] | EUR/MWe/year | 2020 | [A, F, K] | 10 | ctrl | 2015 | 3562.2986
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Fixed O&M [EUR/MWe/year] | EUR/MWe/year | 2020 | [A, F, K] | 10 | ctrl | 2020 | 3562.2986
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Fixed O&M [EUR/MWe/year] | EUR/MWe/year | 2020 | [A, F, K] | 10 | ctrl | 2030 | 3562.2986
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Fixed O&M [EUR/MWe/year] | EUR/MWe/year | 2020 | [A, F, K] | 10 | ctrl | 2050 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Fixed O&M [EUR/MWe/year] | EUR/MWe/year | 2020 | [A, F, K] | 10 | lower | 2020 | 1435.5532
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Fixed O&M [EUR/MWe/year] | EUR/MWe/year | 2020 | [A, F, K] | 10 | lower | 2050 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Fixed O&M [EUR/MWe/year] | EUR/MWe/year | 2020 | [A, F, K] | 10 | upper | 2020 | 5689.044
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Fixed O&M [EUR/MWe/year] | EUR/MWe/year | 2020 | [A, F, K] | 10 | upper | 2050 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E, K] | [10, 11, 12] | ctrl | 2015 | 0.53169
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E, K] | [10, 11, 12] | ctrl | 2020 | 0.53169
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E, K] | [10, 11, 12] | ctrl | 2030 | 0.53169
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E, K] | [10, 11, 12] | ctrl | 2050 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E, K] | [10, 11, 12] | lower | 2020 | 0.37218
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E, K] | [10, 11, 12] | lower | 2050 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E, K] | [10, 11, 12] | upper | 2020 | 0.8507
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E, K] | [10, 11, 12] | upper | 2050 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, F, K] | 10 | ctrl | 2015 | 0.95704
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, F, K] | 10 | ctrl | 2020 | 0.95704
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, F, K] | 10 | ctrl | 2030 | 0.95704
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, F, K] | 10 | ctrl | 2050 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, F, K] | 10 | lower | 2020 | 0.42535
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, F, K] | 10 | lower | 2050 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, F, K] | 10 | upper | 2020 | 1.4887
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | [A, F, K] | 10 | upper | 2050 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | upper | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | upper | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | upper | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | upper | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | upper | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Fixed O&M (*total, additional to existing plant) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [A, F, K] | 10 | ctrl | 2015 | 1350
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Fixed O&M (*total, additional to existing plant) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [A, F, K] | 10 | ctrl | 2020 | 1350
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Fixed O&M (*total, additional to existing plant) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [A, F, K] | 10 | ctrl | 2030 | 1350
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Fixed O&M (*total, additional to existing plant) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [A, F, K] | 10 | lower | 2020 | 550
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Fixed O&M (*total, additional to existing plant) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [A, F, K] | 10 | upper | 2020 | 2150
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Variable O&M (*total, additional to existing plantl) [EUR/MWh_i] | EUR/MWh_i | 2020 | [A, F, K] | 10 | ctrl | 2015 | 0.36
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Variable O&M (*total, additional to existing plantl) [EUR/MWh_i] | EUR/MWh_i | 2020 | [A, F, K] | 10 | ctrl | 2020 | 0.36
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Variable O&M (*total, additional to existing plantl) [EUR/MWh_i] | EUR/MWh_i | 2020 | [A, F, K] | 10 | ctrl | 2030 | 0.36
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Variable O&M (*total, additional to existing plantl) [EUR/MWh_i] | EUR/MWh_i | 2020 | [A, F, K] | 10 | lower | 2020 | 0.16
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Technology-specific data | Variable O&M (*total, additional to existing plantl) [EUR/MWh_i] | EUR/MWh_i | 2020 | [A, F, K] | 10 | upper | 2020 | 0.56
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, J] | 10 | ctrl | 2015 | -0.07
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, J] | 10 | ctrl | 2020 | -0.07
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, J] | 10 | ctrl | 2030 | -0.07
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, J] | 10 | lower | 2020 | -0.02
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, J] | 10 | upper | 2020 | -0.1
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | ctrl | 2015 | 2.5
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | ctrl | 2020 | 2.5
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | ctrl | 2030 | 2.5
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | lower | 2020 | 2
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | upper | 2020 | 3
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | ctrl | 2015 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | ctrl | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | ctrl | 2030 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | lower | 2020 | -0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | upper | 2020 | 0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, J] | 10 | ctrl | 2015 | -0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, J] | 10 | ctrl | 2020 | -0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, J] | 10 | ctrl | 2030 | -0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, J] | 10 | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, J] | 10 | upper | 2020 | -0.02
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, J] | 10 | ctrl | 2015 | -0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, J] | 10 | ctrl | 2020 | -0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, J] | 10 | ctrl | 2030 | -0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, J] | 10 | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, J] | 10 | upper | 2020 | -0.02
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | ctrl | 2015 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | ctrl | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | ctrl | 2030 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | lower | 2020 | -0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | upper | 2020 | 0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2015 | 300
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2020 | 300
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2030 | 300
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2020 | 200
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2020 | 400
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | ctrl | 2015 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | ctrl | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | ctrl | 2030 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | upper | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | ctrl | 2015 | 0.03
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | ctrl | 2020 | 0.03
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | ctrl | 2030 | 0.03
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | lower | 2020 | 0.02
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | upper | 2020 | 0.05
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  | C | 10 | ctrl | 2015 | 15
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  | C | 10 | ctrl | 2020 | 15
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  | C | 10 | ctrl | 2030 | 15
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 3
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 2
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 2
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | upper | 2020 | 0.5
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 10
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 8
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 6
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | lower | 2020 | 2
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | upper | 2020 | 20
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 30
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 24
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 20
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | lower | 2020 | 19
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | upper | 2020 | 53
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2015 | 0.3
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0.3
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0.3
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2015 | 0.98
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2020 | 0.98
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2030 | 0.98
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [F, K] | 10 | ctrl | 2015 | 78423.738
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [F, K] | 10 | ctrl | 2020 | 78423.738
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [F, K] | 10 | ctrl | 2030 | 78423.738
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [F, K] | 10 | ctrl | 2050 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [F, K] | 10 | lower | 2020 | 65131.579
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [F, K] | 10 | lower | 2050 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [F, K] | 10 | upper | 2020 | 91715.8969
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [F, K] | 10 | upper | 2050 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | [10, 12] | ctrl | 2015 | 1.712
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | [10, 12] | ctrl | 2020 | 1.712
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | [10, 12] | ctrl | 2030 | 1.712
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | [10, 12] | ctrl | 2050 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | [10, 12] | lower | 2020 | 1.4249
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | [10, 12] | lower | 2050 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | [10, 12] | upper | 2020 | 2.2863
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | [10, 12] | upper | 2050 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [F, K] | 10 | ctrl | 2015 | 2.9243
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [F, K] | 10 | ctrl | 2020 | 2.9243
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [F, K] | 10 | ctrl | 2030 | 2.9243
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [F, K] | 10 | ctrl | 2050 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [F, K] | 10 | lower | 2020 | 1.8609
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [F, K] | 10 | lower | 2050 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [F, K] | 10 | upper | 2020 | 3.9876
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [F, K] | 10 | upper | 2050 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | ctrl | 2015 | 1
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | ctrl | 2020 | 1
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | ctrl | 2030 | 1
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | upper | 2020 | 2
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | ctrl | 2015 | 0.0005
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | ctrl | 2020 | 0.0005
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | ctrl | 2030 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | upper | 2020 | 0.001
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, I] | 10 | ctrl | 2015 | -0.02
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, I] | 10 | ctrl | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, I] | 10 | ctrl | 2030 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, I] | 10 | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | [A, I] | 10 | upper | 2020 | -0.05
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, I] | 10 | ctrl | 2015 | -0.02
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, I] | 10 | ctrl | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, I] | 10 | ctrl | 2030 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, I] | 10 | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | [A, I] | 10 | upper | 2020 | -0.05
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | ctrl | 2015 | 0.5
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | ctrl | 2020 | 0.5
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | ctrl | 2030 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | [A, I] | 10 | upper | 2020 | 2
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [F, K] | 10 | ctrl | 2015 | 29500
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [F, K] | 10 | ctrl | 2020 | 29500
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [F, K] | 10 | ctrl | 2030 | 29500
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [F, K] | 10 | lower | 2020 | 24500
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | [F, K] | 10 | upper | 2020 | 34500
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | [F, K] | 10 | ctrl | 2015 | 1.1
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | [F, K] | 10 | ctrl | 2020 | 1.1
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | [F, K] | 10 | ctrl | 2030 | 1.1
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | [F, K] | 10 | lower | 2020 | 0.7
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | [F, K] | 10 | upper | 2020 | 1.5
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, I] | 10 | ctrl | 2015 | -0.07
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, I] | 10 | ctrl | 2020 | -0.07
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, I] | 10 | ctrl | 2030 | -0.07
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, I] | 10 | lower | 2020 | -0.02
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) |  |  | [A, B, I] | 10 | upper | 2020 | -0.1
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | ctrl | 2015 | 2
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | ctrl | 2020 | 2
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | ctrl | 2030 | 2
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | lower | 2020 | 1.5
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Construction time [years] | years |  | C | 10 | upper | 2020 | 2.5
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | ctrl | 2015 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | ctrl | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | ctrl | 2030 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | lower | 2020 | -0.01
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) |  |  | A | 10 | upper | 2020 | 0.01
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, I] | 10 | ctrl | 2015 | -0.03
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, I] | 10 | ctrl | 2020 | -0.03
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, I] | 10 | ctrl | 2030 | -0.03
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, I] | 10 | lower | 2020 | -0.02
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] |  |  | [A, B, I] | 10 | upper | 2020 | -0.04
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, I] | 10 | ctrl | 2015 | -0.03
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, I] | 10 | ctrl | 2020 | -0.03
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, I] | 10 | ctrl | 2030 | -0.03
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, I] | 10 | lower | 2020 | -0.02
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] |  |  | [A, B, I] | 10 | upper | 2020 | -0.04
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | ctrl | 2015 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | ctrl | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | ctrl | 2030 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | lower | 2020 | -0.01
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Forced outage (additional to existing plant) [] |  |  | A | 10 | upper | 2020 | 0.01
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2015 | 300
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2020 | 300
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2030 | 300
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2020 | 200
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2020 | 400
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | ctrl | 2015 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | ctrl | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | ctrl | 2030 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | lower | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | weeks/year |  | A | 10 | upper | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | ctrl | 2015 | 0.04
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | ctrl | 2020 | 0.04
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | ctrl | 2030 | 0.04
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | lower | 2020 | 0.03
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | 1000m2/MW_e |  | [A, D] | 10 | upper | 2020 | 0.06
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  | C | 10 | ctrl | 2015 | 15
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  | C | 10 | ctrl | 2020 | 15
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  | C | 10 | ctrl | 2030 | 15
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 3
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 2
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 2
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | lower | 2020 | 3.1
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G |  | upper | 2020 | 3.1
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 10
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 8
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 6
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | lower | 2020 | 0.8
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G |  | upper | 2020 | 0.8
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 30
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 24
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 20
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | lower | 2020 | 19
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | G |  | upper | 2020 | 53
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2015 | 0.3
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2020 | 0.3
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | G |  | ctrl | 2030 | 0.3
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G |  | ctrl | 2015 | 0.98
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G |  | ctrl | 2020 | 0.98
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G |  | ctrl | 2030 | 0.98
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 10 | ctrl | 2015 | 15073.3083
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 10 | ctrl | 2020 | 15073.3083
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 10 | ctrl | 2030 | 15073.3083
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 10 | ctrl | 2050 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 10 | lower | 2020 | 13398.4962
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 10 | lower | 2050 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 10 | upper | 2020 | 16748.1203
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 10 | upper | 2050 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 10 | ctrl | 2015 | 1.712
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 10 | ctrl | 2020 | 1.712
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 10 | ctrl | 2030 | 1.712
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 10 | ctrl | 2050 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 10 | lower | 2020 | 1.4249
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 10 | lower | 2050 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 10 | upper | 2020 | 2.2863
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 10 | upper | 2050 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | 10 | ctrl | 2015 | 1.5951
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | 10 | ctrl | 2020 | 1.5951
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | 10 | ctrl | 2030 | 1.5951
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | 10 | ctrl | 2050 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | 10 | lower | 2020 | 1.0634
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | 10 | lower | 2050 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | 10 | upper | 2020 | 2.1267
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Financial data | Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | 10 | upper | 2050 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2015 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2030 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | lower | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | hours |  | A | 10 | upper | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | ctrl | 2015 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | ctrl | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | ctrl | 2030 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | lower | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Minimum load (of full load, additional to existing plant) [] |  |  | A | 10 | upper | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | ctrl | 2015 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | ctrl | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | ctrl | 2030 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | lower | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] |  |  | A | 10 | upper | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | ctrl | 2015 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | ctrl | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | ctrl | 2030 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | lower | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] |  |  | A | 10 | upper | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2015 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | ctrl | 2030 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | lower | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | hours |  | A | 10 | upper | 2020 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | B | 13 | ctrl | 2015 | 0.35
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | B | 13 | ctrl | 2015 | 0.0027
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Energy/technical data | Forced outage [] |  |  | C | 13 | ctrl | 2015 | 0.03
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, E] | 13 | ctrl | 2015 | 70
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, E] | 13 | lower | 2020 | 50
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, E] | 13 | upper | 2020 | 90
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 13 | ctrl | 2015 | 1.56
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2015 | 15
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | C | 13 | ctrl | 2015 | 3
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | C | 13 | ctrl | 2015 | 10
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | C | 13 | ctrl | 2015 | 30
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | C | 13 | ctrl | 2015 | 0.3
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | D |  | ctrl | 2015 | 116183.3163
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | D |  | ctrl | 2020 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | D |  | ctrl | 2030 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | D |  | ctrl | 2050 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | D |  | lower | 2020 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | D |  | lower | 2050 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | D |  | upper | 2020 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | D |  | upper | 2050 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | D |  | ctrl | 2015 | 4.3279
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | D |  | ctrl | 2020 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | D |  | ctrl | 2030 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | D |  | ctrl | 2050 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | D |  | lower | 2020 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | D |  | lower | 2050 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | D |  | upper | 2020 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | D |  | upper | 2050 | 0
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  | C | 13 | ctrl | 2015 | 12
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | C | 13 | ctrl | 2015 | 0.45
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | C | 13 | ctrl | 2015 | 0.02
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 13 | ctrl | 2015 | 0.03
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | C | 13 | ctrl | 2015 | 2
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | D |  | ctrl | 2015 | 29500
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | D |  | ctrl | 2015 | 1.1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | ctrl | 2015 | 0.95
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | ctrl | 2020 | 0.96
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | ctrl | 2030 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | ctrl | 2050 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | lower | 2020 | 0.8
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | lower | 2050 | 0.8
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | upper | 2020 | 1.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | upper | 2050 | 1.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2015 | 1.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2020 | 1.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2030 | 1.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2050 | 1.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 6 | lower | 2020 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 6 | lower | 2050 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 6 | upper | 2020 | 2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 6 | upper | 2050 | 2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | ctrl | 2015 | 0.39
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | ctrl | 2020 | 0.4
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | ctrl | 2030 | 0.41
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | ctrl | 2050 | 0.43
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | lower | 2020 | 0.36
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | lower | 2050 | 0.38
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | upper | 2020 | 0.4
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | upper | 2050 | 0.42
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [6, 12] | ctrl | 2015 | 0.41
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [6, 12] | ctrl | 2020 | 0.42
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [6, 12] | ctrl | 2030 | 0.43
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [6, 12] | ctrl | 2050 | 0.45
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [6, 12] | lower | 2020 | 0.38
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [6, 12] | lower | 2050 | 0.4
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [6, 12] | upper | 2020 | 0.42
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [6, 12] | upper | 2050 | 0.44
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 6 | ctrl | 2015 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 6 | ctrl | 2020 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 6 | ctrl | 2030 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 6 | ctrl | 2050 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 6 | lower | 2020 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 6 | lower | 2050 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 6 | upper | 2020 | 0.03
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 6 | upper | 2050 | 0.03
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | lower | 2020 | 40
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | lower | 2050 | 40
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | upper | 2020 | 125
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | upper | 2050 | 125
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2015 | 3
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2020 | 3
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2030 | 2.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2050 | 2.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | lower | 2020 | 2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | lower | 2050 | 1.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | upper | 2020 | 3.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | upper | 2050 | 3
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | ctrl | 2015 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | ctrl | 2020 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | ctrl | 2030 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | ctrl | 2050 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | lower | 2020 | 0.01
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | lower | 2050 | 0.01
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | upper | 2020 | 0.03
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | upper | 2050 | 0.03
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | ctrl | 2015 | 25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | ctrl | 2020 | 25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | ctrl | 2030 | 25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | ctrl | 2050 | 25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | lower | 2020 | 25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | lower | 2050 | 25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 9 | ctrl | 2015 | 1.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 9 | ctrl | 2020 | 1.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 9 | ctrl | 2030 | 1.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 9 | ctrl | 2050 | 1.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 9 | lower | 2020 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 9 | lower | 2050 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 9 | upper | 2020 | 8
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 9 | upper | 2050 | 8
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 9 | ctrl | 2015 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 9 | ctrl | 2020 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 9 | ctrl | 2030 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 9 | ctrl | 2050 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 9 | lower | 2020 | 0.7
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 9 | lower | 2050 | 0.7
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 9 | upper | 2020 | 1.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 9 | upper | 2050 | 1.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | ctrl | 2015 | 20
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | ctrl | 2020 | 15
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | ctrl | 2030 | 10
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | ctrl | 2050 | 10
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | lower | 2020 | 10
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | lower | 2050 | 7.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | upper | 2020 | 30
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | upper | 2050 | 20
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2015 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2030 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | lower | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | lower | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | upper | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | upper | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | ctrl | 2015 | 21267.4544
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | ctrl | 2020 | 20735.768
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | ctrl | 2030 | 19778.7326
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | ctrl | 2050 | 19140.7089
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | lower | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | lower | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | upper | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | upper | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | ctrl | 2015 | 0.63802
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | ctrl | 2020 | 0.62739
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | ctrl | 2030 | 0.59549
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | ctrl | 2050 | 0.55295
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | lower | 2020 | 0.42535
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | lower | 2050 | 0.37218
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | upper | 2020 | 0.95704
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | upper | 2050 | 0.90387
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | ctrl | 2015 | 4.7852
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | ctrl | 2020 | 4.6788
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | ctrl | 2030 | 4.4662
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | ctrl | 2050 | 4.2535
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | lower | 2020 | 4.2535
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | lower | 2050 | 3.1901
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | upper | 2020 | 6.3802
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | upper | 2050 | 5.3169
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2015 | 0.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2020 | 0.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2030 | 0.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2050 | 0.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | lower | 2020 | 0.4
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | lower | 2050 | 0.4
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | upper | 2020 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | upper | 2050 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | ctrl | 2015 | 0.25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | ctrl | 2020 | 0.23
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | ctrl | 2030 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | ctrl | 2050 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | lower | 2020 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | lower | 2050 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | upper | 2020 | 0.25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | upper | 2050 | 0.25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | ctrl | 2015 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | ctrl | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | ctrl | 2030 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | ctrl | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | lower | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | lower | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | upper | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | upper | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | ctrl | 2015 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | ctrl | 2020 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | ctrl | 2030 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | ctrl | 2050 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | lower | 2020 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | lower | 2050 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | upper | 2020 | 0.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | upper | 2050 | 0.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2015 | 0.25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2020 | 0.23
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2030 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2050 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | lower | 2020 | 0.1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | lower | 2050 | 0.1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | upper | 2020 | 0.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | upper | 2050 | 0.4
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | ctrl | 2015 | 0.71
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | ctrl | 2020 | 0.73
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | ctrl | 2030 | 0.8
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | ctrl | 2050 | 0.8
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | lower | 2020 | 0.61
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | lower | 2050 | 0.7
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | upper | 2020 | 0.8
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [6, 12] | upper | 2050 | 0.9
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2015 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2020 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2030 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2050 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  |  | 6 | lower | 2020 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  |  | 6 | lower | 2050 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  |  | 6 | upper | 2020 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  |  | 6 | upper | 2050 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | ctrl | 2015 | 0.34
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | ctrl | 2020 | 0.35
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | ctrl | 2030 | 0.37
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | ctrl | 2050 | 0.38
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | lower | 2020 | 0.3
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | lower | 2050 | 0.32
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | upper | 2020 | 0.38
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [6, 11] | upper | 2050 | 0.4
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [G, H] | [6, 12] | ctrl | 2015 | 0.36
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [G, H] | [6, 12] | ctrl | 2020 | 0.37
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [G, H] | [6, 12] | ctrl | 2030 | 0.39
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [G, H] | [6, 12] | ctrl | 2050 | 0.4
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [G, H] | [6, 12] | lower | 2020 | 0.32
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [G, H] | [6, 12] | lower | 2050 | 0.34
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [G, H] | [6, 12] | upper | 2020 | 0.4
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [G, H] | [6, 12] | upper | 2050 | 0.42
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | 6 | ctrl | 2015 | 0.02
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | 6 | ctrl | 2020 | 0.02
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | 6 | ctrl | 2030 | 0.02
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | 6 | ctrl | 2050 | 0.02
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | 6 | lower | 2020 | 0.02
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | 6 | lower | 2050 | 0.02
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | 6 | upper | 2020 | 0.03
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | 6 | upper | 2050 | 0.03
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | lower | 2020 | 5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | lower | 2050 | 5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | upper | 2020 | 40
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | upper | 2050 | 40
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2015 | 3
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2020 | 2.8
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2030 | 2.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | ctrl | 2050 | 2.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | lower | 2020 | 2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | lower | 2050 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | upper | 2020 | 3.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 6 | upper | 2050 | 3
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | ctrl | 2015 | 0.04
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | ctrl | 2020 | 0.04
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | ctrl | 2030 | 0.04
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | ctrl | 2050 | 0.04
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | lower | 2020 | 0.03
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | lower | 2050 | 0.03
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | upper | 2020 | 0.07
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 7 | upper | 2050 | 0.07
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | ctrl | 2015 | 25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | ctrl | 2020 | 25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | ctrl | 2030 | 25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | ctrl | 2050 | 25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | lower | 2020 | 25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | E | [6, 7] | lower | 2050 | 25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2015 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2020 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2030 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2050 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 9 | lower | 2020 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 9 | lower | 2050 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 9 | upper | 2020 | 8
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 9 | upper | 2050 | 8
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2015 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2020 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2030 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | ctrl | 2050 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | lower | 2020 | 0.7
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | lower | 2050 | 0.7
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | upper | 2020 | 1.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 9 | upper | 2050 | 1.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | ctrl | 2015 | 20
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | ctrl | 2020 | 15
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | ctrl | 2030 | 10
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | ctrl | 2050 | 10
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | lower | 2020 | 10
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | lower | 2050 | 8
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | upper | 2020 | 30
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [7, 9] | upper | 2050 | 20
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2015 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2030 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | lower | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | lower | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | upper | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | upper | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | ctrl | 2015 | 21267.4544
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | ctrl | 2020 | 20735.768
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | ctrl | 2030 | 19778.7326
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | ctrl | 2050 | 19140.7089
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | lower | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | lower | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | upper | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 6 | upper | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | ctrl | 2015 | 0.79753
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | ctrl | 2020 | 0.77626
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | ctrl | 2030 | 0.74436
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | ctrl | 2050 | 0.72309
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | lower | 2020 | 0.63802
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | lower | 2050 | 0.58485
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | upper | 2020 | 1.0634
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [6, 10] | upper | 2050 | 1.0102
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | ctrl | 2015 | 5.8485
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | ctrl | 2020 | 5.7422
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | ctrl | 2030 | 5.4232
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | ctrl | 2050 | 4.8915
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | lower | 2020 | 5.3169
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | lower | 2050 | 4.2535
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | upper | 2020 | 7.4436
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 6 | upper | 2050 | 6.3802
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2015 | 0.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2020 | 0.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2030 | 0.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2050 | 0.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | lower | 2020 | 0.4
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | lower | 2050 | 0.4
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | upper | 2020 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 8] | upper | 2050 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | ctrl | 2015 | 0.25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | ctrl | 2020 | 0.23
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | ctrl | 2030 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | ctrl | 2050 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | lower | 2020 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | lower | 2050 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | upper | 2020 | 0.25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  | A | 6 | upper | 2050 | 0.25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | ctrl | 2015 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | ctrl | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | ctrl | 2030 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | ctrl | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | lower | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | lower | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | upper | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | I |  | upper | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | ctrl | 2015 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | ctrl | 2020 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | ctrl | 2030 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | ctrl | 2050 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | lower | 2020 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | lower | 2050 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | upper | 2020 | 0.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | 6 | upper | 2050 | 0.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2015 | 0.25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2020 | 0.23
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2030 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | ctrl | 2050 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | lower | 2020 | 0.1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | lower | 2050 | 0.1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | upper | 2020 | 0.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 6, 8] | upper | 2050 | 0.4
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [7, 13] | ctrl | 2015 | 0.6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [7, 13] | ctrl | 2020 | 0.6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [7, 13] | ctrl | 2030 | 0.6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [7, 13] | ctrl | 2050 | 0.6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [7, 13] | lower | 2020 | 0.4
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [7, 13] | lower | 2050 | 0.4
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [7, 13] | upper | 2020 | 0.85
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [7, 13] | upper | 2050 | 0.85
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Construction time [years] | years |  | L | 13 | ctrl | 2015 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Construction time [years] | years |  | L | 13 | ctrl | 2020 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Construction time [years] | years |  | L | 13 | ctrl | 2030 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Construction time [years] | years |  | L | 13 | ctrl | 2050 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Construction time [years] | years |  | L | 13 | lower | 2020 | 0.3
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Construction time [years] | years |  | L | 13 | lower | 2050 | 0.2
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Construction time [years] | years |  | L | 13 | upper | 2020 | 0.8
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Construction time [years] | years |  | L | 13 | upper | 2050 | 0.7
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  |  | ctrl | 2015 | 0.28
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  |  | ctrl | 2020 | 0.28
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  |  | ctrl | 2030 | 0.28
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  |  | ctrl | 2050 | 0.28
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  |  | lower | 2020 | 0.21
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  |  | lower | 2050 | 0.23
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  |  | upper | 2020 | 0.29
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  |  | upper | 2050 | 0.33
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | M | 7 | ctrl | 2015 | 0.3
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | M | 7 | ctrl | 2020 | 0.3
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | M | 7 | ctrl | 2030 | 0.3
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | M | 7 | ctrl | 2050 | 0.3
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | M | 7 | lower | 2020 | 0.23
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | M | 7 | lower | 2050 | 0.25
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | M | 7 | upper | 2020 | 0.32
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | M | 7 | upper | 2050 | 0.35
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.05
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.05
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.05
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.05
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2020 | 0.01
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2050 | 0.01
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2020 | 0.2
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2050 | 0.2
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 7 | ctrl | 2015 | 0.06
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 7 | ctrl | 2020 | 0.06
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 7 | ctrl | 2030 | 0.06
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 7 | ctrl | 2050 | 0.06
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 7 | lower | 2020 | 0.05
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 7 | lower | 2050 | 0.05
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 7 | upper | 2020 | 0.15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 7 | upper | 2050 | 0.15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Technical lifetime [years] | years |  | L |  | ctrl | 2015 | 15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Technical lifetime [years] | years |  | L |  | ctrl | 2020 | 15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Technical lifetime [years] | years |  | L |  | ctrl | 2030 | 15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Technical lifetime [years] | years |  | L |  | ctrl | 2050 | 15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Technical lifetime [years] | years |  | L |  | lower | 2020 | 10
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Technical lifetime [years] | years |  | L |  | lower | 2050 | 10
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Technical lifetime [years] | years |  | L |  | upper | 2020 | 20
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Energy/technical data | Technical lifetime [years] | years |  | L |  | upper | 2050 | 20
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 13 | ctrl | 2015 | 6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 13 | ctrl | 2020 | 6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 13 | ctrl | 2030 | 6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 13 | ctrl | 2050 | 6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [7, 13] | ctrl | 2015 | 10
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [7, 13] | ctrl | 2020 | 10
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [7, 13] | ctrl | 2030 | 10
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [7, 13] | ctrl | 2050 | 10
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [7, 13] | lower | 2020 | 6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [7, 13] | lower | 2050 | 6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [7, 13] | upper | 2020 | 15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [7, 13] | upper | 2050 | 15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | SO2 (degree of desulphuring) [] |  |  |  | 13 | ctrl | 2015 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | SO2 (degree of desulphuring) [] |  |  |  | 13 | ctrl | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | SO2 (degree of desulphuring) [] |  |  |  | 13 | ctrl | 2030 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | SO2 (degree of desulphuring) [] |  |  |  | 13 | ctrl | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | SO2 (degree of desulphuring) [] |  |  |  | 13 | lower | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | SO2 (degree of desulphuring) [] |  |  |  | 13 | lower | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | SO2 (degree of desulphuring) [] |  |  |  | 13 | upper | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Environment | SO2 (degree of desulphuring) [] |  |  |  | 13 | upper | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2015 | 1.276
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2020 | 1.276
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2030 | 1.1697
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2050 | 1.0634
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | lower | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | lower | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | upper | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | upper | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2015 | 0.90387
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2020 | 0.90387
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2030 | 0.8507
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2050 | 0.74436
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | lower | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | lower | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | upper | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | upper | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2015 | 0.37218
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2020 | 0.37218
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2030 | 0.31901
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | ctrl | 2050 | 0.31901
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | lower | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | lower | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | upper | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [13, 14] | upper | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 13 | ctrl | 2015 | 15.9506
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 13 | ctrl | 2020 | 15.9506
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 13 | ctrl | 2030 | 14.8872
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 13 | ctrl | 2050 | 13.8238
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 13 | lower | 2020 | 10.6337
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 13 | lower | 2050 | 8.507
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 13 | upper | 2020 | 15.9506
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 13 | upper | 2050 | 15.9506
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2015 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Minimum load (of full load) [] |  |  | L | [7, 13] | ctrl | 2015 | 0.4
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Minimum load (of full load) [] |  |  | L | [7, 13] | ctrl | 2020 | 0.4
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Minimum load (of full load) [] |  |  | L | [7, 13] | ctrl | 2030 | 0.4
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Minimum load (of full load) [] |  |  | L | [7, 13] | ctrl | 2050 | 0.4
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Minimum load (of full load) [] |  |  | L | [7, 13] | lower | 2020 | 0.3
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Minimum load (of full load) [] |  |  | L | [7, 13] | lower | 2050 | 0.25
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Minimum load (of full load) [] |  |  | L | [7, 13] | upper | 2020 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Minimum load (of full load) [] |  |  | L | [7, 13] | upper | 2050 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2015 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2030 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | lower | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | lower | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | upper | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | upper | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2015 | 0.25
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0.25
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0.25
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0.25
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2015 | 1.7
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2020 | 1.8
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2030 | 2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2050 | 2.2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2020 | 1.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2050 | 1.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2020 | 2.2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2050 | 2.4
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2015 | 2.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2020 | 2.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2030 | 2.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2050 | 2.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2020 | 2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2050 | 2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2020 | 3
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2050 | 3
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | J |  | ctrl | 2015 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | J |  | ctrl | 2020 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | J |  | ctrl | 2030 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | J |  | ctrl | 2050 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | ctrl | 2015 | 0.55
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | ctrl | 2020 | 0.56
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | ctrl | 2030 | 0.58
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | ctrl | 2050 | 0.6
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | lower | 2020 | 0.52
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | lower | 2050 | 0.55
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | upper | 2020 | 0.58
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | upper | 2050 | 0.62
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2015 | 0.58
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2020 | 0.59
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2030 | 0.61
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2050 | 0.63
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | lower | 2020 | 0.55
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | lower | 2050 | 0.58
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | upper | 2020 | 0.61
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | upper | 2050 | 0.65
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2015 | 0.03
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2020 | 0.03
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2030 | 0.03
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2050 | 0.03
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2020 | 0.02
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2050 | 0.02
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2020 | 0.04
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2050 | 0.04
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | lower | 2020 | 100
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | lower | 2050 | 100
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | upper | 2020 | 500
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | upper | 2050 | 500
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2015 | 2.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2020 | 2.3
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2030 | 2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2050 | 2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2020 | 2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2050 | 2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2020 | 4
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2050 | 4
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | ctrl | 2015 | 0.02
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | ctrl | 2020 | 0.02
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | ctrl | 2030 | 0.02
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | ctrl | 2050 | 0.02
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | lower | 2020 | 0.01
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | lower | 2050 | 0.01
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | upper | 2020 | 0.03
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | upper | 2050 | 0.03
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | ctrl | 2015 | 25
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | ctrl | 2020 | 25
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | ctrl | 2030 | 25
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | ctrl | 2050 | 25
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | lower | 2020 | 25
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | lower | 2050 | 25
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2015 | 1.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2020 | 1.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2030 | 1.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2050 | 1.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | lower | 2020 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | lower | 2050 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | upper | 2020 | 8
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | upper | 2050 | 8
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2015 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2020 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2030 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2050 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | lower | 2020 | 0.7
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | lower | 2050 | 0.7
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | upper | 2020 | 1.2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | upper | 2050 | 1.2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | ctrl | 2015 | 20
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | ctrl | 2020 | 15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | ctrl | 2030 | 10
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | ctrl | 2050 | 8
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | lower | 2020 | 10
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | lower | 2050 | 5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | upper | 2020 | 30
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | upper | 2050 | 15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2015 | 0
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2020 | 0
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2030 | 0
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2050 | 0
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | lower | 2020 | 0
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | lower | 2050 | 0
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | upper | 2020 | 0
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | upper | 2050 | 0
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | ctrl | 2015 | 31901.1815
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | ctrl | 2020 | 31156.8206
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | ctrl | 2030 | 29561.7616
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | ctrl | 2050 | 27647.6907
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | lower | 2020 | 26584.318
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | lower | 2050 | 21267.4544
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | upper | 2020 | 37218.0451
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | upper | 2050 | 31901.1815
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 8] | ctrl | 2015 | 0.95704
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 8] | ctrl | 2020 | 0.93577
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 8] | ctrl | 2030 | 0.8826
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 8] | ctrl | 2050 | 0.8507
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 8] | lower | 2020 | 0.8507
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 8] | lower | 2050 | 0.74436
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 8] | upper | 2020 | 1.276
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 8] | upper | 2050 | 1.1697
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2015 | 0.74436
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2020 | 0.72309
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2030 | 0.68056
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2050 | 0.64866
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | lower | 2020 | 0.69119
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | lower | 2050 | 0.63802
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | upper | 2020 | 1.0846
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | upper | 2050 | 1.0102
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2015 | 0.21267
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2020 | 0.21267
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2030 | 0.20204
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2050 | 0.20204
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | lower | 2020 | 0.15951
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | lower | 2050 | 0.10634
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | upper | 2020 | 0.19141
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | upper | 2050 | 0.15951
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | ctrl | 2015 | 4.7852
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | ctrl | 2020 | 4.6788
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | ctrl | 2030 | 4.4662
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | ctrl | 2050 | 4.2535
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | lower | 2020 | 3.1901
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | lower | 2050 | 3.1901
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | upper | 2020 | 7.4436
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | upper | 2050 | 7.4436
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | ctrl | 2015 | 2.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | ctrl | 2020 | 2.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | ctrl | 2030 | 2.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | ctrl | 2050 | 2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | lower | 2020 | 2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | lower | 2050 | 1.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | upper | 2020 | 5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | upper | 2050 | 5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | ctrl | 2015 | 0.4
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | ctrl | 2020 | 0.4
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | ctrl | 2030 | 0.4
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | ctrl | 2050 | 0.4
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | lower | 2020 | 0.3
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | lower | 2050 | 0.3
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | upper | 2020 | 0.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | upper | 2050 | 0.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  | [5, 3, 11] | ctrl | 2015 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  | [5, 3, 11] | ctrl | 2020 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  | [5, 3, 11] | ctrl | 2030 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  | [5, 3, 11] | ctrl | 2050 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  | [5, 3, 11] | lower | 2020 | 0.05
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  | [5, 3, 11] | lower | 2050 | 0.05
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  | [5, 3, 11] | upper | 2020 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  | [5, 3, 11] | upper | 2050 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | ctrl | 2015 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | ctrl | 2020 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | ctrl | 2030 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | ctrl | 2050 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | lower | 2020 | 0.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | lower | 2050 | 0.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | upper | 2020 | 1.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | upper | 2050 | 1.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2015 | 1.2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2020 | 1.3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2030 | 1.4
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2050 | 1.55
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2020 | 0.9
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2050 | 1.1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2020 | 1.6
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2050 | 1.7
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2015 | 2.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2020 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2030 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2050 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2020 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2050 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2020 | 3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2050 | 3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | ctrl | 2015 | 0.47
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | ctrl | 2020 | 0.48
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | ctrl | 2030 | 0.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | ctrl | 2050 | 0.52
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | lower | 2020 | 0.39
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | lower | 2050 | 0.42
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | upper | 2020 | 0.52
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  |  | [5, 9] | upper | 2050 | 0.55
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2015 | 0.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2020 | 0.51
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2030 | 0.53
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2050 | 0.55
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | lower | 2020 | 0.42
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | lower | 2050 | 0.45
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | upper | 2020 | 0.55
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | upper | 2050 | 0.58
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2015 | 0.03
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2020 | 0.03
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2030 | 0.03
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2050 | 0.03
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2020 | 0.02
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2050 | 0.02
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2020 | 0.04
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2050 | 0.04
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | lower | 2020 | 10
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | lower | 2050 | 10
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | upper | 2020 | 100
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | F |  | upper | 2050 | 100
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2015 | 2.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2020 | 2.3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2030 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2050 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2020 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2050 | 1.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2020 | 4
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2050 | 4
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | ctrl | 2015 | 0.03
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | ctrl | 2020 | 0.03
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | ctrl | 2030 | 0.03
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | ctrl | 2050 | 0.03
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | lower | 2020 | 0.02
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | lower | 2050 | 0.02
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | upper | 2020 | 0.04
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | G | 3 | upper | 2050 | 0.04
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | ctrl | 2015 | 25
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | ctrl | 2020 | 25
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | ctrl | 2030 | 25
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | ctrl | 2050 | 25
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | lower | 2020 | 25
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | E | [5, 3] | lower | 2050 | 25
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2015 | 1.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2020 | 1.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2030 | 1.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2050 | 1.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | lower | 2020 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | lower | 2050 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | upper | 2020 | 8
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 7 | upper | 2050 | 8
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2015 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2020 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2030 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | ctrl | 2050 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | lower | 2020 | 0.7
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | lower | 2050 | 0.7
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | upper | 2020 | 1.2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 7 | upper | 2050 | 1.2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | ctrl | 2015 | 20
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | ctrl | 2020 | 15
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | ctrl | 2030 | 10
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | ctrl | 2050 | 8
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | lower | 2020 | 10
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | lower | 2050 | 5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | upper | 2020 | 30
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | D | [3, 7] | upper | 2050 | 15
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2015 | 0
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2020 | 0
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2030 | 0
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2050 | 0
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | lower | 2020 | 0
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | lower | 2050 | 0
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | upper | 2020 | 0
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | upper | 2050 | 0
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | ctrl | 2015 | 31901.1815
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | ctrl | 2020 | 31156.8206
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | ctrl | 2030 | 29561.7616
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | ctrl | 2050 | 27647.6907
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | lower | 2020 | 26584.318
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | lower | 2050 | 21267.4544
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | upper | 2020 | 37218.0451
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | B | 5 | upper | 2050 | 31901.1815
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 9] | ctrl | 2015 | 1.3824
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 9] | ctrl | 2020 | 1.3824
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 9] | ctrl | 2030 | 1.276
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 9] | ctrl | 2050 | 1.1697
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 9] | lower | 2020 | 1.1697
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 9] | lower | 2050 | 0.95704
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 9] | upper | 2020 | 1.9141
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [5, 9] | upper | 2050 | 1.7014
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2015 | 1.0634
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2020 | 1.0634
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2030 | 0.95704
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2050 | 0.8507
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | lower | 2020 | 0.8507
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | lower | 2050 | 0.69119
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | upper | 2020 | 1.4887
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | upper | 2050 | 1.3292
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2015 | 0.31901
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2020 | 0.31901
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2030 | 0.31901
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | ctrl | 2050 | 0.31901
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | lower | 2020 | 0.31901
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | lower | 2050 | 0.26584
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | upper | 2020 | 0.42535
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 10 | upper | 2050 | 0.37218
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | ctrl | 2015 | 4.7852
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | ctrl | 2020 | 4.6788
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | ctrl | 2030 | 4.4662
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | ctrl | 2050 | 4.2535
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | lower | 2020 | 3.1901
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | lower | 2050 | 3.1901
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | upper | 2020 | 7.4436
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | 5 | upper | 2050 | 7.4436
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | ctrl | 2015 | 2.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | ctrl | 2020 | 2.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | ctrl | 2030 | 2.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | ctrl | 2050 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | lower | 2020 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | lower | 2050 | 1.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | upper | 2020 | 5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 6, 1, 11] | upper | 2050 | 5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | ctrl | 2015 | 0.4
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | ctrl | 2020 | 0.4
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | ctrl | 2030 | 0.4
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | ctrl | 2050 | 0.4
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | lower | 2020 | 0.3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | lower | 2050 | 0.3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | upper | 2020 | 0.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | A | [5, 3, 11] | upper | 2050 | 0.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [C, M] | [5, 3, 11] | ctrl | 2015 | 0.15
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [C, M] | [5, 3, 11] | ctrl | 2020 | 0.15
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [C, M] | [5, 3, 11] | ctrl | 2030 | 0.15
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [C, M] | [5, 3, 11] | ctrl | 2050 | 0.15
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [C, M] | [5, 3, 11] | lower | 2020 | 0.05
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [C, M] | [5, 3, 11] | lower | 2050 | 0.05
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [C, M] | [5, 3, 11] | upper | 2020 | 0.15
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [C, M] | [5, 3, 11] | upper | 2050 | 0.15
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | ctrl | 2015 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | ctrl | 2020 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | ctrl | 2030 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | ctrl | 2050 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | lower | 2020 | 0.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | lower | 2050 | 0.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | upper | 2020 | 1.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [5, 6, 1, 11] | upper | 2050 | 1.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | ctrl | 2015 | 0.9
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | ctrl | 2020 | 0.95
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | ctrl | 2030 | 0.99
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | ctrl | 2050 | 1.04
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | lower | 2020 | 0.65
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | lower | 2050 | 0.65
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | upper | 2020 | 1.02
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | upper | 2050 | 1.15
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | ctrl | 2015 | 1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | ctrl | 2020 | 1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | ctrl | 2030 | 1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | ctrl | 2050 | 1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | lower | 2020 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | lower | 2050 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | upper | 2020 | 1.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | upper | 2050 | 1.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | ctrl | 2015 | 0.44
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | ctrl | 2020 | 0.45
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | ctrl | 2030 | 0.47
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | ctrl | 2050 | 0.48
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | lower | 2020 | 0.38
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | lower | 2050 | 0.42
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | upper | 2020 | 0.46
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | upper | 2050 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | ctrl | 2015 | 0.46
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | ctrl | 2020 | 0.47
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | ctrl | 2030 | 0.48
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | ctrl | 2050 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | lower | 2020 | 0.4
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | lower | 2050 | 0.44
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | upper | 2020 | 0.48
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | upper | 2050 | 0.52
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | ctrl | 2015 | 0.03
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | ctrl | 2020 | 0.03
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | ctrl | 2030 | 0.03
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | ctrl | 2050 | 0.03
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | lower | 2020 | 0.02
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | lower | 2050 | 0.02
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | upper | 2020 | 0.05
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | upper | 2050 | 0.05
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2020 | 1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2050 | 1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2020 | 10
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2050 | 10
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | H | [5, 6] | ctrl | 2015 | 0.8
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | H | [5, 6] | ctrl | 2020 | 0.8
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | H | [5, 6] | ctrl | 2030 | 0.8
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | H | [5, 6] | ctrl | 2050 | 0.8
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.04
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.04
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.04
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.03
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.03
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.03
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.05
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.04
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | ctrl | 2015 | 25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | ctrl | 2020 | 25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | ctrl | 2030 | 25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | ctrl | 2050 | 25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | lower | 2020 | 25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | lower | 2050 | 25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2015 | 315
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2020 | 315
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2030 | 280
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2050 | 250
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2020 | 300
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2050 | 250
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2020 | 400
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2050 | 350
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | H |  | ctrl | 2015 | 0.6
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | H |  | ctrl | 2020 | 0.6
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | H |  | ctrl | 2030 | 0.6
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | H |  | ctrl | 2050 | 0.6
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2015 | 75
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2020 | 60
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2030 | 60
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2050 | 60
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2020 | 50
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2050 | 50
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2020 | 100
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2050 | 100
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 4 | ctrl | 2015 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 4 | ctrl | 2020 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 4 | ctrl | 2030 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 4 | ctrl | 2050 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 4 | lower | 2020 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 4 | lower | 2050 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 4 | upper | 2020 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 4 | upper | 2050 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | ctrl | 2015 | 10633.7272
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | ctrl | 2020 | 10367.884
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | ctrl | 2030 | 9889.3663
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | ctrl | 2050 | 9038.6681
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | lower | 2020 | 7443.609
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | lower | 2050 | 6380.2363
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | upper | 2020 | 21267.4544
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | upper | 2050 | 15950.5908
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | ctrl | 2015 | 1.0634
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | ctrl | 2020 | 1.0102
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | ctrl | 2030 | 0.95704
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | ctrl | 2050 | 0.90387
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | lower | 2020 | 0.95704
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | lower | 2050 | 0.8507
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | upper | 2020 | 1.1697
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | upper | 2050 | 1.1697
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | ctrl | 2015 | 0.69119
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | ctrl | 2020 | 0.63802
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | ctrl | 2030 | 0.58485
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | ctrl | 2050 | 0.58485
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | lower | 2020 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | lower | 2050 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | upper | 2020 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | upper | 2050 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | ctrl | 2015 | 0.37218
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | ctrl | 2020 | 0.37218
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | ctrl | 2030 | 0.37218
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | ctrl | 2050 | 0.31901
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | lower | 2020 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | lower | 2050 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | upper | 2020 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | H | [3, 5] | upper | 2050 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | ctrl | 2015 | 5.7422
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | ctrl | 2020 | 5.7422
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | ctrl | 2030 | 5.4232
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | ctrl | 2050 | 5.2105
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | lower | 2020 | 4.2535
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | lower | 2050 | 4.2535
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | upper | 2020 | 12.7605
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | upper | 2050 | 10.6337
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | ctrl | 2015 | 0.3
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | ctrl | 2020 | 0.3
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | ctrl | 2030 | 0.3
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | ctrl | 2050 | 0.3
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | lower | 2020 | 0.2
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | lower | 2050 | 0.2
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | upper | 2020 | 0.4
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | upper | 2050 | 0.4
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | ctrl | 2015 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | ctrl | 2020 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | ctrl | 2030 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | ctrl | 2050 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | lower | 2020 | 0.3
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | lower | 2050 | 0.25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | upper | 2020 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | upper | 2050 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  | 12 | ctrl | 2015 | 0.25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  | 12 | ctrl | 2020 | 0.3
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  | 12 | ctrl | 2030 | 0.35
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  | 12 | ctrl | 2050 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  | 12 | lower | 2020 | 0.1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  | 12 | lower | 2050 | 0.25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  | 12 | upper | 2020 | 0.4
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  | 12 | upper | 2050 | 1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 12, 13] | ctrl | 2015 | 0.25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 12, 13] | ctrl | 2020 | 0.3
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 12, 13] | ctrl | 2030 | 0.4
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 12, 13] | ctrl | 2050 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 12, 13] | lower | 2020 | 0.2
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 12, 13] | lower | 2050 | 0.25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 12, 13] | upper | 2020 | 1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 12, 13] | upper | 2050 | 1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | ctrl | 2015 | 0.05
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | ctrl | 2020 | 0.05
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | ctrl | 2030 | 0.05
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | ctrl | 2050 | 0.05
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | lower | 2020 | 0.01
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | lower | 2050 | 0.01
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | upper | 2020 | 0.15
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | upper | 2050 | 0.15
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | ctrl | 2015 | 0.82
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | ctrl | 2020 | 0.86
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | ctrl | 2030 | 0.92
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | ctrl | 2050 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | lower | 2020 | 0.59
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | lower | 2050 | 0.75
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | upper | 2020 | 0.96
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  | [3, 4, 7] | upper | 2050 | 1.1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | ctrl | 2015 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | ctrl | 2020 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | ctrl | 2030 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | ctrl | 2050 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | lower | 2020 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | lower | 2050 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | upper | 2020 | 1.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  | B | [3, 6] | upper | 2050 | 1.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | ctrl | 2015 | 0.4
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | ctrl | 2020 | 0.41
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | ctrl | 2030 | 0.43
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | ctrl | 2050 | 0.45
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | lower | 2020 | 0.36
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | lower | 2050 | 0.4
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | upper | 2020 | 0.42
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 4, 7] | upper | 2050 | 0.46
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | ctrl | 2015 | 0.42
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | ctrl | 2020 | 0.43
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | ctrl | 2030 | 0.45
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | ctrl | 2050 | 0.47
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | lower | 2020 | 0.38
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | lower | 2050 | 0.42
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | upper | 2020 | 0.44
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | [3, 4] | upper | 2050 | 0.48
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | ctrl | 2015 | 0.03
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | ctrl | 2020 | 0.03
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | ctrl | 2030 | 0.03
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | ctrl | 2050 | 0.03
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | lower | 2020 | 0.02
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | lower | 2050 | 0.02
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | upper | 2020 | 0.05
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Forced outage [] |  |  |  | [5, 6] | upper | 2050 | 0.05
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2020 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2050 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2020 | 10
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2050 | 10
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | H | [5, 6] | ctrl | 2015 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | H | [5, 6] | ctrl | 2020 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | H | [5, 6] | ctrl | 2030 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | H | [5, 6] | ctrl | 2050 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.04
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.04
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.04
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.03
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.03
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.03
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.05
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.05
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | ctrl | 2015 | 25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | ctrl | 2020 | 25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | ctrl | 2030 | 25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | ctrl | 2050 | 25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | lower | 2020 | 25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [4, 5, 7] | lower | 2050 | 25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2015 | 300
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2020 | 300
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2030 | 300
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2050 | 300
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2020 | 300
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2050 | 300
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2020 | 400
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2050 | 400
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J |  | ctrl | 2015 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J |  | ctrl | 2020 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J |  | ctrl | 2030 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J |  | ctrl | 2050 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2015 | 100
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2020 | 100
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2030 | 100
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | ctrl | 2050 | 100
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2020 | 90
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | lower | 2050 | 90
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2020 | 120
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 4 | upper | 2050 | 120
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | SO2 (degree of desulphuring) [] |  |  | K | 8 | lower | 2020 | 0
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | SO2 (degree of desulphuring) [] |  |  | K | 8 | lower | 2050 | 0
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | SO2 (degree of desulphuring) [] |  |  | K | 8 | upper | 2020 | 0.999
06 Gas engines, biogas | Engine - back pressure - biogas - small | Environment | SO2 (degree of desulphuring) [] |  |  | K | 8 | upper | 2050 | 0.999
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | ctrl | 2015 | 10633.7272
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | ctrl | 2020 | 10367.884
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | ctrl | 2030 | 9889.3663
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | ctrl | 2050 | 9038.6681
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | lower | 2020 | 7443.609
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | lower | 2050 | 6380.2363
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | upper | 2020 | 21267.4544
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | F | 5 | upper | 2050 | 15950.5908
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | ctrl | 2015 | 1.0634
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | ctrl | 2020 | 1.0102
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | ctrl | 2030 | 0.95704
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | ctrl | 2050 | 0.90387
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | lower | 2020 | 0.8507
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | lower | 2050 | 0.8507
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | upper | 2020 | 1.276
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5, 11] | upper | 2050 | 1.276
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | ctrl | 2015 | 0.69119
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | ctrl | 2020 | 0.63802
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | ctrl | 2030 | 0.58485
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | ctrl | 2050 | 0.58485
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | lower | 2020 | 0
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | lower | 2050 | 0
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | upper | 2020 | 0
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | upper | 2050 | 0
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | ctrl | 2015 | 0.37218
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | ctrl | 2020 | 0.37218
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | ctrl | 2030 | 0.37218
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | ctrl | 2050 | 0.31901
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | lower | 2020 | 0
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | lower | 2050 | 0
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | upper | 2020 | 0
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | [3, 5] | upper | 2050 | 0
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | ctrl | 2015 | 8.507
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | ctrl | 2020 | 7.9753
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | ctrl | 2030 | 7.4436
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | ctrl | 2050 | 6.3802
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | lower | 2020 | 6.3802
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | lower | 2050 | 4.2535
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | upper | 2020 | 13.8238
06 Gas engines, biogas | Engine - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | F | [3, 5, 11] | upper | 2050 | 12.7605
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | ctrl | 2015 | 0.3
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | ctrl | 2020 | 0.3
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | ctrl | 2030 | 0.3
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | ctrl | 2050 | 0.3
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | lower | 2020 | 0.2
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | lower | 2050 | 0.2
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | upper | 2020 | 0.4
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [6, 10] | upper | 2050 | 0.4
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | ctrl | 2015 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | ctrl | 2020 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | ctrl | 2030 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | ctrl | 2050 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | lower | 2020 | 0.3
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | lower | 2050 | 0.25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | upper | 2020 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  | 6 | upper | 2050 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J | 8 | ctrl | 2015 | 0.25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J | 8 | ctrl | 2020 | 0.3
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J | 8 | ctrl | 2030 | 0.4
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J | 8 | ctrl | 2050 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J | 8 | lower | 2020 | 0.1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J | 8 | lower | 2050 | 0.25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J | 8 | upper | 2020 | 0.4
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J | 8 | upper | 2050 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 8, 13] | ctrl | 2015 | 0.25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 8, 13] | ctrl | 2020 | 0.3
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 8, 13] | ctrl | 2030 | 0.4
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 8, 13] | ctrl | 2050 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 8, 13] | lower | 2020 | 0.2
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 8, 13] | lower | 2050 | 0.25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 8, 13] | upper | 2020 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | C | [6, 8, 13] | upper | 2050 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | ctrl | 2015 | 0.05
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | ctrl | 2020 | 0.05
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | ctrl | 2030 | 0.05
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | ctrl | 2050 | 0.05
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | lower | 2020 | 0.01
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | lower | 2050 | 0.01
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | upper | 2020 | 0.15
06 Gas engines, biogas | Engine - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | C | [6, 10] | upper | 2050 | 0.15
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2015 | 0.029099
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2020 | 0.029099
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2030 | 0.029215
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2050 | 0.02911
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | lower | 2020 | 0.021471
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | lower | 2050 | 0.017177
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | upper | 2020 | 0.031962
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | upper | 2050 | 0.032382
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2015 | 0.3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2020 | 0.3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2030 | 0.31
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2050 | 0.32
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2020 | 0.27
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2050 | 0.27
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2020 | 0.32
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2050 | 0.35
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2015 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2020 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2030 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2020 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2020 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.22357
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.22357
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.22886
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.23712
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2020 | 0.19
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2050 | 0.19
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2020 | 0.25
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2050 | 0.27
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2015 | 0.23534
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2020 | 0.23534
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2030 | 0.24091
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2050 | 0.2496
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2020 | 0.21
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2050 | 0.21
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2020 | 0.26
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2050 | 0.28
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2015 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2020 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2030 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2050 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2020 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2050 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2020 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2050 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2015 | 51.77
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2020 | 51.77
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2030 | 53
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2050 | 54.91
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | lower | 2020 | 46.98
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | lower | 2050 | 46.98
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | upper | 2020 | 56.44
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | upper | 2050 | 60.65
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2015 | 2.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2020 | 2.38
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2030 | 2.15
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2050 | 1.76
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2020 | 2.02
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2050 | 1.32
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2020 | 2.73
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2050 | 2.2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2015 | 0.77
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2020 | 0.77
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2030 | 0.75
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2050 | 0.73
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2020 | 0.66
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2050 | 0.55
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2020 | 0.89
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2050 | 0.91
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2015 | 0.3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2020 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2030 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2050 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2020 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2050 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2020 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2050 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 1.2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2015 | 80
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2020 | 60
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2030 | 20
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2050 | 10
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2020 | 10
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2050 | 10
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2020 | 60
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2050 | 60
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 0.3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 0.3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 0.3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 0.3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2015 | 0.99792
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2020 | 0.99792
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2030 | 0.99792
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2050 | 0.99792
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2020 | 0.98962
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2050 | 0.99481
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2020 | 0.99896
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2050 | 0.99896
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2015 | 243512.3524
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2020 | 197787.3255
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2030 | 185026.8529
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2050 | 157379.1623
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | lower | 2020 | 168012.8894
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | lower | 2050 | 115907.6263
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | upper | 2020 | 231815.2525
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | upper | 2050 | 195660.5801
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2015 | 8.4538
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2020 | 8.2518
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2030 | 7.8477
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2050 | 6.8694
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2020 | 7.0076
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2050 | 5.0191
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2020 | 9.6661
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2050 | 8.5389
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2015 | 5.0936
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2020 | 4.9766
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2030 | 4.7958
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2050 | 4.211
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2020 | 4.2216
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2050 | 3.02
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2020 | 5.9017
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2050 | 5.2105
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2015 | 3.3603
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2020 | 3.2752
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2030 | 3.0412
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2050 | 2.6584
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | lower | 2020 | 2.786
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | lower | 2050 | 1.9885
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | upper | 2020 | 3.7643
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | upper | 2050 | 3.3177
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2015 | 26.5737
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2020 | 26.5737
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2030 | 25.9782
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2050 | 25.0956
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | lower | 2020 | 22.6073
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | lower | 2050 | 18.8642
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | upper | 2020 | 30.6251
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | upper | 2050 | 31.3589
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2015 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2020 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2030 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2050 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | lower | 2020 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | lower | 2050 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | upper | 2020 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | upper | 2050 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2015 | 0.2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2020 | 0.2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2030 | 0.2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2050 | 0.2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | lower | 2020 | 0.2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | lower | 2050 | 0.2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | upper | 2020 | 0.2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | upper | 2050 | 0.2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2015 | 0.05
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2020 | 0.05
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2030 | 0.05
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2050 | 0.05
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | lower | 2020 | 0.05
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | lower | 2050 | 0.05
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | upper | 2020 | 0.05
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | upper | 2050 | 0.05
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2015 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2020 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2030 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2050 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | lower | 2020 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | lower | 2050 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | upper | 2020 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | upper | 2050 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2015 | 0.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2020 | 0.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2030 | 0.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2050 | 0.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | lower | 2020 | 0.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | lower | 2050 | 0.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | upper | 2020 | 0.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | upper | 2050 | 0.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2015 | 0.041506
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2020 | 0.041506
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2030 | 0.040149
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2050 | 0.037398
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2020 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2050 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2020 | 0.06
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2050 | 0.06
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2015 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2020 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2030 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2050 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | lower | 2020 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | lower | 2050 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | upper | 2020 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | upper | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2015 | 57422.1267
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2020 | 46682.0623
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2030 | 44555.3169
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2050 | 39344.7905
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2020 | 39663.8024
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2050 | 28817.4006
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2020 | 54551.0204
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2050 | 48915.145
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2015 | 21.1292
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2020 | 17.1735
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2030 | 16.4078
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2050 | 14.4725
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2020 | 14.6001
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2050 | 10.6231
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2020 | 20.0658
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2050 | 18.0135
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2015 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2020 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2030 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | lower | 2020 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | lower | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | upper | 2020 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | upper | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.80185
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.80185
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.79888
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.79566
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2020 | 0.76
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2050 | 0.73
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2020 | 0.85
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2050 | 0.87
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2015 | 0.79009
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2020 | 0.79009
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2030 | 0.78683
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2050 | 0.78318
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2020 | 0.74
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2050 | 0.71
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2020 | 0.84
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2050 | 0.86
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2015 | 74.69
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2020 | 74.69
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2030 | 74.69
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2050 | 74.69
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2020 | 74.69
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2050 | 74.69
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2020 | 74.69
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2050 | 74.69
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 1.9885
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 1.946
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 1.8928
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 1.712
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 1.6482
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 1.2548
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 2.2756
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 2.1267
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2015 | 733.7272
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2020 | 712.4597
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2030 | 691.1923
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2050 | 627.3899
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2020 | 606.1224
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2050 | 457.2503
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2020 | 840.0644
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2050 | 786.8958
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 1.2016
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 1.1697
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 1.1591
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 1.0527
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 0.99957
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 0.75499
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 1.393
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 1.2973
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2015 | 0.7869
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2020 | 0.76563
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2030 | 0.73373
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2050 | 0.65929
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2020 | 0.65929
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2050 | 0.49979
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2020 | 0.8826
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2050 | 0.82943
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2015 | 18.4176
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2020 | 18.4176
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2030 | 18.4282
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2050 | 18.4495
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2020 | 15.6741
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2050 | 13.8664
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2020 | 21.2356
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2050 | 23.0539
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2015 | 0.11697
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2020 | 0.11697
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2030 | 0.11697
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2050 | 0.1276
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2020 | 0.10634
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2050 | 0.10634
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2020 | 0.14887
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2050 | 0.15951
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2015 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2020 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2030 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2050 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | lower | 2020 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | lower | 2050 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | upper | 2020 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | upper | 2050 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2015 | 6.2526
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2020 | 6.2526
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2030 | 6.2526
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2050 | 6.2633
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2020 | 5.3169
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2050 | 4.7107
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2020 | 7.2097
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2050 | 7.8264
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2015 | 0.029566
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2020 | 0.029566
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2030 | 0.029667
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2050 | 0.029534
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | lower | 2020 | 0.021847
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | lower | 2050 | 0.017478
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | upper | 2020 | 0.032244
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | upper | 2050 | 0.032647
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [A, B] |  | ctrl | 2015 | 0.28
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [A, B] |  | ctrl | 2020 | 0.28
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [A, B] |  | ctrl | 2030 | 0.29
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [A, B] |  | ctrl | 2050 | 0.3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [A, B] |  | lower | 2020 | 0.25
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [A, B] |  | lower | 2050 | 0.25
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [A, B] |  | upper | 2020 | 0.31
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [A, B] |  | upper | 2050 | 0.34
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | [A, B] |  | ctrl | 2015 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | [A, B] |  | ctrl | 2020 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | [A, B] |  | ctrl | 2030 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | [A, B] |  | ctrl | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | [A, B] |  | lower | 2020 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | [A, B] |  | lower | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | [A, B] |  | upper | 2020 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | [A, B] |  | upper | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.20215
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.20215
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.20813
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.21654
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2020 | 0.17
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2050 | 0.17
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2020 | 0.23
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2050 | 0.25
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2015 | 0.21279
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2020 | 0.21279
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2030 | 0.21908
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2050 | 0.22793
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2020 | 0.19
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2050 | 0.19
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2020 | 0.24
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2050 | 0.26
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2015 | 0.01
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2020 | 0.01
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2030 | 0.01
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2050 | 0.01
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2020 | 0.01
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2050 | 0.01
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2020 | 0.01
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2050 | 0.01
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2015 | 46.81
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2020 | 46.81
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2030 | 48.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2050 | 50.15
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | lower | 2020 | 42.06
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | lower | 2050 | 42.06
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | upper | 2020 | 51.61
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | upper | 2050 | 55.88
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2015 | 2.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2020 | 2.38
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2030 | 2.15
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2050 | 1.76
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2020 | 2.02
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2050 | 1.32
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2020 | 2.73
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2050 | 2.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2015 | 0.85
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2020 | 0.85
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2030 | 0.83
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2050 | 0.8
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2020 | 0.73
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2050 | 0.6
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2020 | 0.98
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2015 | 0.3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2020 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2030 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2050 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2020 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2050 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2020 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2050 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 1.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2015 | 80
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2020 | 60
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2030 | 20
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2050 | 10
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2020 | 10
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2050 | 10
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2020 | 60
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2050 | 60
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 0.3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 0.3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 0.3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 0.3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2015 | 0.99792
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2020 | 0.99792
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2030 | 0.99792
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2050 | 0.99792
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2020 | 0.98962
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2050 | 0.99481
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2020 | 0.99896
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2050 | 0.99896
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2015 | 270096.6704
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2020 | 219054.7799
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2030 | 203104.1891
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2050 | 172266.3803
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | lower | 2020 | 186090.2257
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | lower | 2050 | 126541.3534
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | upper | 2020 | 256272.825
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | upper | 2050 | 214801.289
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2015 | 9.3577
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2020 | 9.1237
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2030 | 8.624
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2050 | 7.518
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2020 | 7.752
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2050 | 5.4976
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2020 | 10.6975
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2050 | 9.347
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2015 | 5.6359
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2020 | 5.4976
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2030 | 5.2743
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2050 | 4.6044
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2020 | 4.6788
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2050 | 3.3071
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2020 | 6.5291
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2050 | 5.7103
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2015 | 3.7112
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2020 | 3.6261
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2030 | 3.3496
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2050 | 2.9136
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | lower | 2020 | 3.0838
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | lower | 2050 | 2.1799
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | upper | 2020 | 4.1684
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | upper | 2050 | 3.6367
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2015 | 29.0088
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2020 | 29.0088
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2030 | 28.2006
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2050 | 27.1585
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | lower | 2020 | 24.5745
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | lower | 2050 | 20.2466
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | upper | 2020 | 33.7089
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | upper | 2050 | 34.1874
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2015 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2020 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2030 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2050 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | lower | 2020 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | lower | 2050 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | upper | 2020 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | upper | 2050 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2015 | 0.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2020 | 0.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2030 | 0.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2050 | 0.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | lower | 2020 | 0.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | lower | 2050 | 0.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | upper | 2020 | 0.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | upper | 2050 | 0.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2015 | 0.05
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2020 | 0.05
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2030 | 0.05
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2050 | 0.05
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | lower | 2020 | 0.05
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | lower | 2050 | 0.05
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | upper | 2020 | 0.05
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | upper | 2050 | 0.05
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2015 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2020 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2030 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2050 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | lower | 2020 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | lower | 2050 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | upper | 2020 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | upper | 2050 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2015 | 0.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2020 | 0.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2030 | 0.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2050 | 0.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | lower | 2020 | 0.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | lower | 2050 | 0.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | upper | 2020 | 0.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | upper | 2050 | 0.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2015 | 0.10038
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2020 | 0.10038
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2030 | 0.097086
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2050 | 0.090423
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2020 | 0.04
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2050 | 0.04
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2020 | 0.12
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2050 | 0.12
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2015 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2020 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2030 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2050 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | lower | 2020 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | lower | 2050 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | upper | 2020 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | upper | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2015 | 57422.1267
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2020 | 46682.0623
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2030 | 44555.3169
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2050 | 39344.7905
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2020 | 39663.8024
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2050 | 28817.4006
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2020 | 54551.0204
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2050 | 48915.145
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2015 | 21.1292
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2020 | 17.1735
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2030 | 16.4078
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2050 | 14.4725
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2020 | 14.6001
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2050 | 10.6231
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2020 | 20.0658
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2050 | 18.0135
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2015 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2020 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2030 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | lower | 2020 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | lower | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | upper | 2020 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | upper | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.76349
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.76349
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.76185
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.76254
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2020 | 0.72
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2050 | 0.7
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2020 | 0.85
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2050 | 0.86
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2015 | 0.75285
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2020 | 0.75285
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2030 | 0.7509
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2050 | 0.75114
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2020 | 0.7
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2050 | 0.68
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2020 | 0.84
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2050 | 0.85
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2015 | 74.69
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2020 | 74.69
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2030 | 74.69
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2050 | 74.69
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2020 | 74.69
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2050 | 74.69
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2020 | 74.69
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2050 | 74.69
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 1.9885
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 1.946
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 1.8928
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 1.712
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 1.6482
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 1.2548
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 2.2756
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 2.1267
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2015 | 733.7272
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2020 | 712.4597
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2030 | 691.1923
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2050 | 627.3899
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2020 | 606.1224
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2050 | 457.2503
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2020 | 840.0644
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2050 | 786.8958
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 1.2016
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 1.1697
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 1.1591
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 1.0527
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 0.99957
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 0.75499
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 1.393
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 1.2973
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2015 | 0.7869
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2020 | 0.76563
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2030 | 0.73373
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2050 | 0.65929
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2020 | 0.65929
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2050 | 0.49979
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2020 | 0.8826
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2050 | 0.82943
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2015 | 18.1837
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2020 | 18.1837
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2030 | 18.1943
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2050 | 18.2368
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2020 | 15.4083
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2050 | 13.6005
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2020 | 21.1292
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2050 | 22.9582
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2015 | 0.03
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2020 | 0.03
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2030 | 0.04
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2050 | 0.05
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2020 | 0.01
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2050 | 0.01
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2020 | 0.11
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2050 | 0.11
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2015 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2020 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2030 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2050 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | lower | 2020 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | lower | 2050 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | upper | 2020 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Steam reheat |  |  | O |  | upper | 2050 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2015 | 6.1676
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2020 | 6.1676
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2030 | 6.1782
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2050 | 6.1888
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2020 | 5.2318
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2050 | 4.615
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2020 | 7.1671
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2050 | 7.7945
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2015 | 0.029101
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2020 | 0.029101
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2030 | 0.029217
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2050 | 0.029112
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | lower | 2020 | 0.021472
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | lower | 2050 | 0.017178
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | upper | 2020 | 0.031965
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | upper | 2050 | 0.032684
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2015 | 0.3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2020 | 0.3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2030 | 0.3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2050 | 0.31
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2020 | 0.27
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2050 | 0.27
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2020 | 0.32
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2050 | 0.35
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 2.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 2.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 2.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 2.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 1.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2015 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2020 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2030 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2020 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2020 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.221
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.221
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.22599
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.23383
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2020 | 0.19
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2050 | 0.19
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2020 | 0.25
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2050 | 0.26
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.23263
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.23263
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.23788
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.24614
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | lower | 2020 | 0.21
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | lower | 2050 | 0.21
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | upper | 2020 | 0.26
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | upper | 2050 | 0.28
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2015 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2020 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2030 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2050 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2020 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2050 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2020 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2050 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2015 | 18.61
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2020 | 18.61
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2030 | 19.03
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2050 | 19.69
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | lower | 2020 | 16.91
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | lower | 2050 | 16.91
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | upper | 2020 | 20.24
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | upper | 2050 | 21.66
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2015 | 3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2020 | 2.85
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2030 | 2.58
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2050 | 2.11
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2020 | 2.43
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2050 | 1.58
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2020 | 3.28
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2050 | 2.64
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2015 | 1.61
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2020 | 1.61
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2030 | 1.58
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2050 | 1.52
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2020 | 1.37
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2050 | 1.14
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2020 | 1.85
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2050 | 1.9
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2015 | 0.3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2020 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2030 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2050 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2020 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2050 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2020 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2050 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 1.2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2015 | 80
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2020 | 60
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2030 | 40
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2050 | 10
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2020 | 10
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2050 | 10
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2020 | 60
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2050 | 60
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 0.3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 0.3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 0.3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 0.3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2015 | 0.99792
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2020 | 0.99792
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2030 | 0.99792
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2050 | 0.99792
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2020 | 0.98962
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2050 | 0.99481
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2020 | 0.99896
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2050 | 0.99896
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2015 | 316885.07
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2020 | 278603.6521
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2030 | 260526.3159
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2050 | 222244.8981
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | lower | 2020 | 237132.1161
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | lower | 2050 | 163759.3986
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | upper | 2020 | 325392.0517
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | upper | 2050 | 276476.9067
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2015 | 9.8362
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2020 | 9.5916
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2030 | 9.145
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2050 | 8.0178
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2020 | 8.1561
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2050 | 5.8485
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2020 | 11.2611
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2050 | 9.9638
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2015 | 5.9762
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2020 | 5.8273
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2030 | 5.6465
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2050 | 4.9553
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2020 | 4.9553
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2050 | 3.5517
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2020 | 6.9332
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2050 | 6.1463
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2015 | 3.86
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2020 | 3.7643
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2030 | 3.4985
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2050 | 3.0625
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | lower | 2020 | 3.2008
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | lower | 2050 | 2.2969
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | upper | 2020 | 4.3279
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | upper | 2050 | 3.8281
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2015 | 26.8821
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2020 | 26.8821
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2030 | 26.3078
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2050 | 25.4465
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | lower | 2020 | 22.8731
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | lower | 2050 | 19.1301
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | upper | 2020 | 30.9867
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | upper | 2050 | 31.7842
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2015 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2020 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2030 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2050 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | lower | 2020 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | lower | 2050 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | upper | 2020 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | upper | 2050 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2015 | 0.2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2020 | 0.2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2030 | 0.2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2050 | 0.2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | lower | 2020 | 0.2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | lower | 2050 | 0.2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | upper | 2020 | 0.2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | upper | 2050 | 0.2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2015 | 0.05
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2020 | 0.05
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2030 | 0.05
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | ctrl | 2050 | 0.05
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | lower | 2020 | 0.05
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | lower | 2050 | 0.05
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | upper | 2020 | 0.05
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F |  | upper | 2050 | 0.05
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2015 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2020 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2030 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2050 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | lower | 2020 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | lower | 2050 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | upper | 2020 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | upper | 2050 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2015 | 0.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2020 | 0.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2030 | 0.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2050 | 0.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | lower | 2020 | 0.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | lower | 2050 | 0.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | upper | 2020 | 0.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | upper | 2050 | 0.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2015 | 0.041506
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2020 | 0.041506
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2030 | 0.040149
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2050 | 0.037398
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2020 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2050 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2020 | 0.06
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2050 | 0.06
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Combustion air humidification |  |  | [D, P] |  | ctrl | 2015 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Combustion air humidification |  |  | [D, P] |  | ctrl | 2020 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Combustion air humidification |  |  | [D, P] |  | ctrl | 2030 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Combustion air humidification |  |  | [D, P] |  | ctrl | 2050 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Combustion air humidification |  |  | [D, P] |  | lower | 2020 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Combustion air humidification |  |  | [D, P] |  | lower | 2050 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Combustion air humidification |  |  | [D, P] |  | upper | 2020 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Combustion air humidification |  |  | [D, P] |  | upper | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2015 | 73691.7293
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2020 | 64865.7358
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2030 | 61888.2922
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2050 | 54657.3577
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2020 | 55189.044
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2050 | 40195.4887
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2020 | 75712.1375
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2050 | 68055.8539
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2015 | 27.1266
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2020 | 23.8834
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2030 | 22.7774
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2050 | 20.119
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2020 | 20.2998
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2050 | 14.7915
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2020 | 27.8604
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2050 | 25.0531
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Flue gas condensation |  |  | [D, P] |  | ctrl | 2015 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Flue gas condensation |  |  | [D, P] |  | ctrl | 2020 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Flue gas condensation |  |  | [D, P] |  | ctrl | 2030 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Flue gas condensation |  |  | [D, P] |  | ctrl | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Flue gas condensation |  |  | [D, P] |  | lower | 2020 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Flue gas condensation |  |  | [D, P] |  | lower | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Flue gas condensation |  |  | [D, P] |  | upper | 2020 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Flue gas condensation |  |  | [D, P] |  | upper | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.79986
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.79986
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.79711
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.79418
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2020 | 0.76
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2050 | 0.73
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2020 | 0.85
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2050 | 0.88
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2015 | 0.78823
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2020 | 0.78823
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2030 | 0.78521
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2050 | 0.78187
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2020 | 0.74
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2050 | 0.71
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2020 | 0.84
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2050 | 0.86
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2015 | 27.16
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2020 | 27.16
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2030 | 27.16
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2050 | 27.16
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2020 | 27.16
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2050 | 27.16
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2020 | 27.16
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2050 | 27.16
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 2.2863
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 2.2331
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 2.1799
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 1.9779
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 1.8928
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 1.4356
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 2.6159
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 2.4564
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2015 | 840.0644
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2020 | 818.797
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2030 | 797.5295
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2050 | 723.0934
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2020 | 701.826
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2050 | 531.6864
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2020 | 967.6692
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2050 | 903.8668
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 1.393
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 1.3611
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 1.3398
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 1.2229
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 1.1484
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 0.87197
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 1.6163
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 1.51
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2015 | 0.89323
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2020 | 0.87197
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2030 | 0.82943
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2050 | 0.75499
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2020 | 0.74436
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2050 | 0.56359
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2020 | 1.0102
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2050 | 0.93577
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2015 | 18.4176
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2020 | 18.4176
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2030 | 18.4282
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2050 | 18.4495
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2020 | 15.6741
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2050 | 13.8664
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2020 | 21.2356
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2050 | 23.0433
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2015 | 0.11
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2020 | 0.11
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2030 | 0.11
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2050 | 0.12
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2020 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2050 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2020 | 0.14
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2050 | 0.14
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Steam reheat |  |  | P |  | ctrl | 2015 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Steam reheat |  |  | P |  | ctrl | 2020 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Steam reheat |  |  | P |  | ctrl | 2030 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Steam reheat |  |  | P |  | ctrl | 2050 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Steam reheat |  |  | P |  | lower | 2020 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Steam reheat |  |  | P |  | lower | 2050 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Steam reheat |  |  | P |  | upper | 2020 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Steam reheat |  |  | P |  | upper | 2050 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2015 | 6.2526
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2020 | 6.2526
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2030 | 6.2526
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2050 | 6.2633
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2020 | 5.3169
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2050 | 4.7107
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2020 | 7.2097
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2050 | 7.8264
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2015 | 0.029099
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2020 | 0.029099
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2030 | 0.029216
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | ctrl | 2050 | 0.029389
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | lower | 2020 | 0.021471
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | lower | 2050 | 0.017177
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | upper | 2020 | 0.032286
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B] |  | upper | 2050 | 0.032998
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2015 | 0.29
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2020 | 0.29
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2030 | 0.29
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2050 | 0.3
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2020 | 0.26
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2050 | 0.26
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2020 | 0.31
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2050 | 0.33
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 2.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 2.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 2.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 2.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 1.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2015 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2020 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2030 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | ctrl | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2020 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | lower | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2020 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | [A, B] |  | upper | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.21592
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.21592
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.2203
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.22643
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2020 | 0.18
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2050 | 0.18
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2020 | 0.24
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2050 | 0.25
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.22729
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.22729
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.23189
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.23834
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | lower | 2020 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | lower | 2050 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | upper | 2020 | 0.25
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, B, C] |  | upper | 2050 | 0.27
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2015 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2020 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2030 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2050 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2020 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2050 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2020 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2050 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2015 | 7.96
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2020 | 7.96
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2030 | 8.12
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2050 | 8.34
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | lower | 2020 | 7.25
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | lower | 2050 | 7.25
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | upper | 2020 | 8.62
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | upper | 2050 | 9.19
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2015 | 3.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2020 | 3.33
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2030 | 3.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2050 | 2.46
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2020 | 2.83
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2050 | 1.85
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2020 | 3.83
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2050 | 3.08
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2015 | 2.51
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2020 | 2.51
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2030 | 2.46
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2050 | 2.4
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2020 | 2.14
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2050 | 1.8
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2020 | 2.89
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2050 | 3
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2015 | 0.3
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2020 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2030 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2050 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2020 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2050 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2020 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2050 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 1.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 3
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2015 | 80
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2020 | 60
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2030 | 40
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2050 | 20
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2020 | 10
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2050 | 10
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2020 | 60
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2050 | 60
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 0.3
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 0.3
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 0.3
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 0.3
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2015 | 0.99792
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2020 | 0.99792
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2030 | 0.99792
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2050 | 0.99792
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2020 | 0.98962
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2050 | 0.99481
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2020 | 0.99896
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2050 | 0.99896
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2015 | 451933.4052
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2020 | 437046.1871
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2030 | 406208.3783
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | ctrl | 2050 | 348786.2515
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | lower | 2020 | 371117.0786
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | lower | 2050 | 257336.1978
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | upper | 2020 | 508292.1592
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | L | 1 | upper | 2050 | 433856.0689
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2015 | 11.3249
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2020 | 11.0484
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2030 | 10.5699
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2050 | 9.3258
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2020 | 9.3896
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2050 | 6.795
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2020 | 12.9838
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2050 | 11.5908
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2015 | 7.0502
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2020 | 6.8694
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2030 | 6.678
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | ctrl | 2050 | 5.9017
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2020 | 5.8379
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | lower | 2050 | 4.2322
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2020 | 8.1773
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | N | 1 | upper | 2050 | 7.3054
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2015 | 4.2854
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2020 | 4.1791
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2030 | 3.8919
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | ctrl | 2050 | 3.4241
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | lower | 2020 | 3.5517
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | lower | 2050 | 2.5734
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | upper | 2020 | 4.8064
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 1 | upper | 2050 | 4.2854
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2015 | 27.5201
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2020 | 27.5201
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2030 | 26.9884
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | ctrl | 2050 | 26.2653
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | lower | 2020 | 23.4155
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | lower | 2050 | 19.7468
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | upper | 2020 | 31.6991
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | K | 1 | upper | 2050 | 32.8157
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2015 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2020 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2030 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | ctrl | 2050 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | lower | 2020 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | lower | 2050 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | upper | 2020 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | [F, G] |  | upper | 2050 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2015 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2020 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2030 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | ctrl | 2050 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | lower | 2020 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | lower | 2050 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | upper | 2020 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | [F, G] |  | upper | 2050 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2015 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2020 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2030 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | ctrl | 2050 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | lower | 2020 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | lower | 2050 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | upper | 2020 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | [F, G] |  | upper | 2050 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2015 | 0.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2020 | 0.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2030 | 0.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | ctrl | 2050 | 0.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | lower | 2020 | 0.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | lower | 2050 | 0.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | upper | 2020 | 0.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | [F, G] |  | upper | 2050 | 0.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2015 | 0.041506
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2020 | 0.041506
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2030 | 0.040149
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2050 | 0.038774
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2020 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2050 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2020 | 0.06
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2050 | 0.06
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2015 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2020 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2030 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2050 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | lower | 2020 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | lower | 2050 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | upper | 2020 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | upper | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2015 | 102615.4672
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2020 | 99319.0118
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2030 | 94214.8228
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2050 | 83049.4092
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2020 | 84431.7938
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2050 | 61356.6058
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2020 | 115375.9398
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2050 | 103466.1654
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2015 | 37.8029
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2020 | 36.5481
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2030 | 34.6766
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2050 | 30.5613
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2020 | 31.0718
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2050 | 22.5754
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2020 | 42.4924
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2050 | 38.09
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2015 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2020 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2030 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | lower | 2020 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | lower | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | upper | 2020 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | upper | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.80299
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.80299
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.80087
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.80493
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2020 | 0.77
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2050 | 0.74
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2020 | 0.86
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2050 | 0.88
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2015 | 0.79162
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2020 | 0.79162
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2030 | 0.78927
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | ctrl | 2050 | 0.79302
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2020 | 0.75
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | lower | 2050 | 0.72
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2020 | 0.85
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, B] |  | upper | 2050 | 0.86
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2015 | 11.88
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2020 | 11.88
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2030 | 11.88
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2050 | 11.88
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2020 | 11.88
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2050 | 11.88
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2020 | 11.88
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2050 | 11.88
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 2.5734
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 2.5096
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 2.4458
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 2.2224
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 2.1374
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 1.6163
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 2.9455
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 2.7648
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2015 | 946.4017
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2020 | 925.1343
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2030 | 903.8668
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2050 | 818.797
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2020 | 786.8958
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2050 | 595.4887
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2020 | 1084.6402
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2050 | 1020.8378
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 2.0204
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 1.5632
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 1.5525
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 1.4037
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 1.3292
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 1.0102
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 1.8609
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 1.7439
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2015 | 1.2335
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2020 | 0.9464
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2030 | 0.90387
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2050 | 0.8188
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2020 | 0.80816
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2050 | 0.61676
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2020 | 1.0953
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2050 | 1.0208
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2015 | 18.4176
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2020 | 18.4176
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2030 | 18.4282
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2050 | 18.4389
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2020 | 15.6741
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2050 | 13.8664
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2020 | 21.2249
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2050 | 23.0433
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2015 | 0.11
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2020 | 0.11
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2030 | 0.11
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2050 | 0.12
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2020 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2050 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2020 | 0.14
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2050 | 0.14
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2015 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2020 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2030 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Steam reheat |  |  | O |  | ctrl | 2050 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Steam reheat |  |  | O |  | lower | 2020 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Steam reheat |  |  | O |  | lower | 2050 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Steam reheat |  |  | O |  | upper | 2020 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Steam reheat |  |  | O |  | upper | 2050 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2015 | 6.2526
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2020 | 6.2526
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2030 | 6.2526
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2050 | 6.2633
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2020 | 5.3169
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2050 | 4.7107
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2020 | 7.2097
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2050 | 7.8264
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B, C] |  | ctrl | 2015 | 0.025848
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B, C] |  | ctrl | 2020 | 0.025848
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B, C] |  | ctrl | 2030 | 0.025501
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B, C] |  | ctrl | 2050 | 0.024842
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B, C] |  | lower | 2020 | 0.019033
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B, C] |  | lower | 2050 | 0.014903
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B, C] |  | upper | 2020 | 0.027727
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [A, B, C] |  | upper | 2050 | 0.027608
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 2
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 2
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 2
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 2
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 1.5
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 1.5
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 2.5
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 2.5
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2015 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2020 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2030 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2050 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2020 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | lower | 2050 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2020 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Forced outage [] |  |  |  | 1 | upper | 2050 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, B] |  | ctrl | 2015 | 36.95
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, B] |  | ctrl | 2020 | 36.95
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, B] |  | ctrl | 2030 | 37.04
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, B] |  | ctrl | 2050 | 37.21
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, B] |  | lower | 2020 | 36.26
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, B] |  | lower | 2050 | 36.26
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, B] |  | upper | 2020 | 37.92
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, B] |  | upper | 2050 | 38.08
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2015 | 1.0557
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2020 | 1.0557
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2030 | 1.0582
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | ctrl | 2050 | 1.0633
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2020 | 1.03
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | lower | 2050 | 1.03
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2020 | 1.09
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, B, C] |  | upper | 2050 | 1.09
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2015 | 1.0557
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2020 | 1.0557
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2030 | 1.0582
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, C] |  | ctrl | 2050 | 1.0633
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, C] |  | lower | 2020 | 1.03
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, C] |  | lower | 2050 | 1.03
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, C] |  | upper | 2020 | 1.09
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, C] |  | upper | 2050 | 1.09
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2015 | 3
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2020 | 2.85
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2030 | 2.58
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | ctrl | 2050 | 2.11
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2020 | 2.43
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | lower | 2050 | 1.58
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2020 | 3.28
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E | 1 | upper | 2050 | 2.64
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | 1 | ctrl | 2015 | 0.54
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | 1 | ctrl | 2020 | 0.54
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | 1 | ctrl | 2030 | 0.54
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | 1 | ctrl | 2050 | 0.54
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | 1 | lower | 2020 | 0.46
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | 1 | lower | 2050 | 0.4
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | 1 | upper | 2020 | 0.62
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | 1 | upper | 2050 | 0.67
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
08 WtE HOP | Waste boiler - boiler - waste - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2015 | 0.3
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2020 | 0.1
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2030 | 0.1
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | ctrl | 2050 | 0.1
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2020 | 0
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | lower | 2050 | 0
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2020 | 0.1
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 2 | upper | 2050 | 0.1
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 1.2
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 3
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2015 | 80
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2020 | 60
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2030 | 40
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2050 | 20
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2020 | 10
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | lower | 2050 | 10
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2020 | 60
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | [2, 3, 5] | upper | 2050 | 60
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2015 | 0.3
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2020 | 0.3
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2030 | 0.3
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | ctrl | 2050 | 0.3
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2020 | 0.1
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | lower | 2050 | 0.1
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2020 | 2
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2015 | 0.99792
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2020 | 0.99792
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2030 | 0.99792
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | ctrl | 2050 | 0.99792
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2020 | 0.98962
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | lower | 2050 | 0.99481
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2020 | 0.99896
08 WtE HOP | Waste boiler - boiler - waste - small | Environment | SO2 (degree of desulphuring) [] |  |  | H | 1 | upper | 2050 | 0.99896
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | P |  | ctrl | 2015 | 85814.1783
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | P |  | ctrl | 2020 | 82943.072
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | P |  | ctrl | 2030 | 78583.2439
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | P |  | ctrl | 2050 | 68800.2149
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | P |  | lower | 2020 | 71033.2976
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | P |  | lower | 2050 | 52530.6123
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | P |  | upper | 2020 | 97298.6037
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | P |  | upper | 2050 | 88791.622
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2015 | 1.8928
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2020 | 1.8503
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2030 | 1.8184
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2050 | 1.6376
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | lower | 2020 | 1.6163
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | lower | 2050 | 1.3079
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | upper | 2020 | 2.2437
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | upper | 2050 | 2.2437
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2015 | 1.0846
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2020 | 1.0634
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2030 | 1.0634
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2050 | 0.96767
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | lower | 2020 | 0.92513
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | lower | 2050 | 0.75499
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | upper | 2020 | 1.3079
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | upper | 2050 | 1.3079
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2015 | 0.80816
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2020 | 0.7869
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2030 | 0.74436
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | ctrl | 2050 | 0.66992
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | lower | 2020 | 0.69119
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | lower | 2050 | 0.56359
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | upper | 2020 | 0.92513
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | P |  | upper | 2050 | 0.93577
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2015 | 7.6776
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2020 | 7.8477
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2030 | 8.6771
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2050 | 9.0068
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | lower | 2020 | 6.7205
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | lower | 2050 | 7.2947
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | upper | 2020 | 8.9111
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | upper | 2050 | 10.857
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2015 | 1.7333
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2020 | 1.8928
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2030 | 2.7435
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2050 | 3.0944
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | lower | 2020 | 1.7758
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | lower | 2050 | 2.9455
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | upper | 2020 | 1.9353
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | upper | 2050 | 3.2752
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2015 | 5.9443
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2020 | 5.9443
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2030 | 5.9336
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | ctrl | 2050 | 5.9124
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | lower | 2020 | 4.934
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | lower | 2050 | 4.3492
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | upper | 2020 | 6.9864
08 WtE HOP | Waste boiler - boiler - waste - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [K, P] |  | upper | 2050 | 7.5818
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | G |  | ctrl | 2015 | 12
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | G |  | ctrl | 2020 | 12
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | G |  | ctrl | 2030 | 12
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | G |  | ctrl | 2050 | 12
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | G |  | lower | 2020 | 12
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | G |  | lower | 2050 | 12
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | G |  | upper | 2020 | 12
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Cold start-up time [hours] | hours |  | G |  | upper | 2050 | 12
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | G |  | ctrl | 2015 | 0.7
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | G |  | ctrl | 2020 | 0.7
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | G |  | ctrl | 2030 | 0.7
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | G |  | ctrl | 2050 | 0.7
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | G |  | lower | 2020 | 0.7
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | G |  | lower | 2050 | 0.7
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | G |  | upper | 2020 | 0.7
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Minimum load (of full load) [] |  |  | G |  | upper | 2050 | 0.7
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | ctrl | 2015 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | ctrl | 2020 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | ctrl | 2030 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | ctrl | 2050 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | lower | 2020 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | lower | 2050 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | upper | 2020 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G |  | upper | 2050 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | G |  | ctrl | 2015 | 8
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | G |  | ctrl | 2020 | 8
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | G |  | ctrl | 2030 | 8
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | G |  | ctrl | 2050 | 8
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | G |  | lower | 2020 | 8
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | G |  | lower | 2050 | 8
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | G |  | upper | 2020 | 8
08 WtE HOP | Waste boiler - boiler - waste - small | Regulation ability | Warm start-up time [hours] | hours |  | G |  | upper | 2050 | 8
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2015 | 0.041506
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2020 | 0.041506
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2030 | 0.040149
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | ctrl | 2050 | 0.037398
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2020 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | lower | 2050 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2020 | 0.06
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | [A, B, D] |  | upper | 2050 | 0.06
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2015 | 0
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2020 | 0
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2030 | 0
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | ctrl | 2050 | 0
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | lower | 2020 | 0
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | lower | 2050 | 0
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | upper | 2020 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Combustion air humidification |  |  | [D, O] |  | upper | 2050 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2015 | 90599.3555
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2020 | 87515.5747
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2030 | 83155.7465
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | ctrl | 2050 | 73160.043
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2020 | 74967.7766
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | lower | 2050 | 55933.4049
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2020 | 102721.8045
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | L | 1 | upper | 2050 | 94427.4973
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2015 | 33.3367
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2020 | 32.2202
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2030 | 30.6039
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | ctrl | 2050 | 26.9459
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2020 | 27.6158
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | lower | 2050 | 20.5763
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2020 | 37.8242
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Fixed O&M (*total) [EUR/t_i/y] | EUR/t_i/y | 2020 | L | [1, 4] | upper | 2050 | 34.751
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2015 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2020 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2030 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | ctrl | 2050 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | lower | 2020 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | lower | 2050 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | upper | 2020 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Flue gas condensation |  |  | [D, O] |  | upper | 2050 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2015 | 11.88
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2020 | 11.88
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2030 | 11.88
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | ctrl | 2050 | 11.88
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2020 | 11.88
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | lower | 2050 | 11.88
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2020 | 11.88
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Incineration capacity [t_i/h] | t_i/h |  | [A, B] |  | upper | 2050 | 11.88
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 1.9991
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 1.9566
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 1.9247
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 1.7439
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 1.7014
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 1.393
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 2.3607
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 2.382
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2015 | 733.7272
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2020 | 723.0934
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2030 | 701.826
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | ctrl | 2050 | 638.0236
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2020 | 627.3899
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | lower | 2050 | 510.4189
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2020 | 871.9656
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (*total) [MEUR/t_i] | MEUR/t_i | 2020 | N | 1 | upper | 2050 | 882.5994
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2015 | 1.1484
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2020 | 1.1165
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2030 | 1.1272
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | ctrl | 2050 | 1.0315
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2020 | 0.9783
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | lower | 2050 | 0.79753
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2020 | 1.3824
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | N | 1 | upper | 2050 | 1.393
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2015 | 0.8507
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2020 | 0.82943
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2030 | 0.7869
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | ctrl | 2050 | 0.71246
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2020 | 0.72309
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | lower | 2050 | 0.59549
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2020 | 0.9783
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | M | 1 | upper | 2050 | 0.98894
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2015 | 23.8834
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2020 | 24.3938
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2030 | 27.0416
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2050 | 28.2006
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2020 | 21.427
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2050 | 23.3729
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2020 | 27.2117
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2050 | 33.1347
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2015 | 0.13824
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2020 | 0.13824
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2030 | 0.14887
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | ctrl | 2050 | 0.14887
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2020 | 0.1276
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | lower | 2050 | 0.1276
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2020 | 0.18077
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, K] |  | upper | 2050 | 0.18077
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2015 | 8.1029
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2020 | 8.2837
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2030 | 9.1769
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | ctrl | 2050 | 9.5704
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2020 | 7.2735
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | lower | 2050 | 7.9328
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2020 | 9.2407
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | K | 1 | upper | 2050 | 11.2505
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (electricity cost) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2015 | 5.3807
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (electricity cost) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2020 | 5.9017
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (electricity cost) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2030 | 8.5389
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (electricity cost) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2050 | 9.6767
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (electricity cost) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2020 | 5.6784
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (electricity cost) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2050 | 9.4321
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (electricity cost) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2020 | 5.9017
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (electricity cost) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2050 | 10.0063
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (other O&M) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2015 | 18.4921
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (other O&M) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2020 | 18.4921
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (other O&M) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2030 | 18.5027
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (other O&M) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | ctrl | 2050 | 18.524
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (other O&M) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2020 | 15.7485
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (other O&M) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | lower | 2050 | 13.9408
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (other O&M) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2020 | 21.31
08 WtE HOP | Waste boiler - boiler - waste - small | Technology-specific data | Variable O&M (other O&M) [EUR/t_i] | EUR/t_i | 2020 | K | [1, 4] | upper | 2050 | 23.1284
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.029624
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.02941
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.029426
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.02935
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.021813
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.017993
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.032721
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.034321
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2015 | 0.37
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2020 | 0.37
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2030 | 0.38
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2050 | 0.37
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2020 | 0.34
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2050 | 0.35
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2020 | 0.5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2050 | 0.51
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 4.5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 4
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 5.5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 5.5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2015 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2020 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2030 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2020 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2020 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.28855
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.28915
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.29019
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.28513
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.24
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.26
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.39
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.4
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.30373
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.30437
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.30547
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.30014
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.27
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.29
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.41
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.42
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 182.24
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 182.62
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 183.28
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 180.08
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 166.32
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 174.4
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 242.89
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 251.01
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2015 | 0.08
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2020 | 0.08
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2030 | 0.08
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2050 | 0.08
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2020 | 0.07
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2050 | 0.06
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2020 | 0.09
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2050 | 0.1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 10
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 8
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 6
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 10
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 10
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 30
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 20
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 20
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 10
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 10
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 10
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 30
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 20
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 0.3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 0.3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 0.3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 0.3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 0.1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0.1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2015 | 0.9797
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2020 | 0.9797
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2030 | 0.9797
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2050 | 0.9797
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | lower | 2020 | 0.94925
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | lower | 2050 | 0.9797
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | upper | 2020 | 0.98985
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | upper | 2050 | 0.98985
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 103147.1536
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 101020.4082
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 94640.1719
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 89323.3083
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 85069.8174
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 68055.854
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 118034.3717
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 116970.999
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 3.5942
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 3.4985
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 3.3177
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 3.1263
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 2.9668
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 2.467
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 4.1897
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 4.2854
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 2.3288
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 2.265
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 2.148
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 2.0417
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.8928
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 1.5738
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 2.7435
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 2.7967
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.2654
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.2335
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.1697
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 1.074
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.074
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.89323
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.4568
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.4887
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 4.6682
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 4.6682
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 4.6469
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 4.732
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 3.3071
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 2.9562
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 5.2424
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 5.7103
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 12
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 12
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 12
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 12
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 12
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 12
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 12
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 12
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.45
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.45
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.45
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.45
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2020 | 0.45
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2050 | 0.45
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2020 | 0.45
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2050 | 0.45
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0.02
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0.02
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.02
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.02
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 0.02
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0.02
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 0.02
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0.02
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2015 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2020 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2030 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2050 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | lower | 2020 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | lower | 2050 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | upper | 2020 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | upper | 2050 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.019432
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.018691
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.018689
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.018699
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.01
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.01
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.28
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.28
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 31369.4952
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 30625.1343
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 29030.0752
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 26690.6552
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 25839.957
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 20310.4189
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 36048.3351
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 34984.9624
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.010634
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.010634
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.010634
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.010634
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.010634
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.010634
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.010634
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.010634
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.82914
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.83067
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.8296
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.83481
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.47
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.46
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.87
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.85
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.81395
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.81545
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.81433
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.8198
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.44
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.43
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.85
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.83
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.0953
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 1.0634
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 1.0102
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.93577
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.90387
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.74436
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.276
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.2867
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.70183
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.69119
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.65929
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.61676
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.57422
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.46788
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.82943
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.84006
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.38281
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.37218
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.36155
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.31901
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.32965
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.26584
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.44662
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.44662
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.22
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.22
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.22
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.22
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.22
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.22
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 1.4143
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 1.4249
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 1.4249
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 1.4249
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 1.0102
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.8826
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 1.5951
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 1.712
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.029781
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.029563
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.029578
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.029502
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.022017
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.018156
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.032889
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.034488
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2015 | 0.35
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2020 | 0.35
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2030 | 0.35
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2050 | 0.34
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2020 | 0.32
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2050 | 0.33
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2020 | 0.47
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2050 | 0.49
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 5
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 5
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 5
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 5
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 4.5
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 4
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 5.5
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 5.5
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2015 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2020 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2030 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | lower | 2020 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | lower | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | upper | 2020 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | upper | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.26842
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.26892
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.26991
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.26517
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.23
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.24
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.37
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.38
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.28255
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.28307
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.28411
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.27913
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.25
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.27
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.39
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.4
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 169.53
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 169.84
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 170.47
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 167.48
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 153.68
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 162.19
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 230.21
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 238.75
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2015 | 0.09
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2020 | 0.09
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2030 | 0.09
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2050 | 0.09
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2020 | 0.08
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2050 | 0.07
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2020 | 0.1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2050 | 0.11
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 10
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 8
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 6
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 5
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 5
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 10
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 10
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 30
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 20
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 20
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 10
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 10
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 10
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 30
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 20
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 0.3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 0.3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 0.3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 0.3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 0.1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0.1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2015 | 0.9797
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2020 | 0.9797
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2030 | 0.9797
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2050 | 0.9797
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | lower | 2020 | 0.94925
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | lower | 2050 | 0.9797
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | upper | 2020 | 0.98985
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | upper | 2050 | 0.98985
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 111654.1354
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 108464.0172
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 102083.7809
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 95703.5446
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 91450.0537
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 73372.7175
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 127604.7262
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 125477.9807
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 3.86
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 3.7537
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 3.5623
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 3.3603
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 3.1901
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 2.6478
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 4.5087
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 4.6044
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 2.4989
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 2.4351
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 2.3075
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 2.2012
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 2.0417
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 1.6908
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 2.9455
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 3.0093
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.3611
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.3292
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.2548
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 1.1591
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.1591
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.95704
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.5632
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.5951
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 4.8915
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 4.8915
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 4.8702
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 4.966
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 3.5517
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 3.1795
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 5.5189
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 6.0187
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 12
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 12
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 12
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 12
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 12
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 12
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 12
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 12
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2020 | 0.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2050 | 0.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2020 | 0.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2050 | 0.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0.02
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0.02
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.02
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.02
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 0.02
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0.02
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 0.02
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0.02
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2015 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2020 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2030 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2050 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | lower | 2020 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | lower | 2050 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | upper | 2020 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | upper | 2050 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.046395
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.044624
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.04462
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.044641
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.28
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.28
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 31369.4952
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 30625.1343
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 29030.0752
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 26690.6552
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 25839.957
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 20310.4189
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 36048.3351
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 34984.9624
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.010634
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.010634
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.010634
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.010634
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.010634
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.010634
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.010634
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.010634
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.82282
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.82553
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.82451
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.82939
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.48
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.48
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.86
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.85
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.80869
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.81138
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.8103
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.81543
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.46
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.84
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.83
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.0953
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 1.0634
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 1.0102
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.93577
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.90387
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.74436
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.276
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.2867
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.70183
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.69119
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.65929
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.61676
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.57422
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.46788
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.82943
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.84006
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.38281
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.37218
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.36155
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.31901
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.32965
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.26584
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.44662
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.44662
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.19
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.19
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.19
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.19
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.19
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.19
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 1.3824
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 1.3824
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 1.3824
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 1.3824
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 1.0102
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.8826
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 1.5632
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 1.6801
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.029611
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.029611
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.029627
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.029548
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.021853
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.017985
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.032707
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.034305
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2015 | 0.37
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2020 | 0.37
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2030 | 0.37
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2050 | 0.36
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2020 | 0.34
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2050 | 0.35
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2020 | 0.49
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2050 | 0.5
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 2.5
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 2.5
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 2.5
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 2.5
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 1.5
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2015 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2030 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | ctrl | 2015 | 0.28227
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | ctrl | 2020 | 0.28227
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | ctrl | 2030 | 0.28335
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | ctrl | 2050 | 0.27821
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | lower | 2020 | 0.24
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | lower | 2050 | 0.25
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | upper | 2020 | 0.38
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | upper | 2050 | 0.39
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2015 | 0.29713
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2020 | 0.29713
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2030 | 0.29826
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2050 | 0.29285
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | lower | 2020 | 0.27
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | lower | 2050 | 0.28
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | upper | 2020 | 0.4
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | upper | 2050 | 0.41
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 23.77
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 23.77
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 23.86
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 23.43
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 22.17
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 22.74
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 31.78
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 32.73
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.21
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.21
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.21
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.21
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.18
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.16
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.24
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.27
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 1.2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 90
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 60
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 40
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 20
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 40
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 20
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 60
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 40
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 0.3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 0.3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 0.3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 0.1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0.1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2015 | 0.9797
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2020 | 0.9797
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2030 | 0.9797
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2050 | 0.9797
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | lower | 2020 | 0.94925
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | lower | 2050 | 0.9797
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | upper | 2020 | 0.98985
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | upper | 2050 | 0.98985
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 163759.3986
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 158442.535
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 148872.1805
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 137175.0806
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 133984.9625
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 103147.1536
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 183963.4802
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 177583.2439
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 3.86
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 3.7643
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 3.5729
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 3.4028
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 3.1582
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 2.6159
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 4.4449
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 4.6576
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 2.584
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 2.5202
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 2.3926
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 2.3075
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 2.0736
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 1.7227
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 2.9774
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 3.1476
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.276
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.2441
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.1803
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 1.0846
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.0846
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.90387
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.4675
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.4994
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 4.7745
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 4.7745
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 4.7533
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 4.8383
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 3.3815
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 3.0306
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 5.3807
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 5.8592
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 8
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 8
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 8
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 8
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 8
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 8
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 8
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 8
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2020 | 0.2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2050 | 0.2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2020 | 0.2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2050 | 0.2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2015 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2020 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2030 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2050 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | lower | 2020 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | lower | 2050 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | upper | 2020 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | upper | 2050 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.019432
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.019432
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.01943
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.01944
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.01
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.01
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.26
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.28
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 48702.4705
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 47213.7487
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 44448.9796
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 40195.4887
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 39663.8024
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 30093.4479
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 54763.695
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 51892.5886
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.010634
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.010634
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.010634
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.010634
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.010634
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.010634
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.021267
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.021267
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.82723
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.82723
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.82611
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.83147
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.49
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.46
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.86
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.85
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.81237
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.81237
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.81119
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.81683
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.46
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.43
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.84
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.83
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.1484
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 1.1165
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 1.0634
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.99957
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.93577
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.76563
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.3186
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.3611
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.76563
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.75499
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.71246
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.68056
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.61676
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.49979
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.8826
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.92513
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.38281
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.37218
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.35091
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.31901
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.31901
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.26584
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.43598
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.43598
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.22
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.22
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.22
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.22
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.22
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.22
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 1.4143
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 1.4143
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 1.4143
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 1.4143
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 1.0102
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.8826
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 1.5951
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 1.712
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.02734
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.02734
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.02735
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.027299
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.020804
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.016612
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.029894
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.029899
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2015 | 0.15
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2020 | 0.15
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2030 | 0.15
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2050 | 0.15
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2020 | 0.15
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2050 | 0.14
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2020 | 0.15
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2050 | 0.15
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 1.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 1.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2015 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2030 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.13932
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.13932
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.13987
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.13713
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.12
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.12
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.15
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.15
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.14665
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.14665
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.14723
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.14435
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.14
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.13
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.15
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.15
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 2.93
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 2.93
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 2.94
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 2.89
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 2.85
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 2.79
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 2.97
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 2.98
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.68
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.68
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.68
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.69
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.58
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.52
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.78
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.87
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 20
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 10
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 8
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 4
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 4
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 16
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 16
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 1.2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 3
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 90
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 60
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 40
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 30
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 40
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 20
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 80
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 40
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0.3
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0.3
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0.3
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2015 | 0.9797
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2020 | 0.9797
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2030 | 0.9797
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2050 | 0.9797
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2020 | 0.94925
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2050 | 0.9797
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2020 | 0.98985
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2050 | 0.98985
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 303061.2246
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 298807.7338
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 290300.752
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 287110.6339
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 256272.825
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 217991.4072
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 346659.5061
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 368990.3331
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2015 | 6.8907
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2020 | 6.7205
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2030 | 6.3696
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2050 | 6.1676
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | lower | 2020 | 5.8592
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | lower | 2050 | 4.8702
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | upper | 2020 | 7.9221
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | upper | 2050 | 8.4113
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 4.2748
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 4.1684
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 3.9557
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 3.9345
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 3.6367
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 3.02
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 4.9234
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 5.3275
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 2.6053
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 2.5415
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 2.4139
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 2.2224
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 2.2224
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 1.8396
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 2.9987
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 3.0731
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 9.8468
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 9.8468
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 9.8043
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 10.0063
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 6.8588
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 6.1463
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 11.0697
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 12.0693
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2015 | 0.2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2020 | 0.2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2030 | 0.2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2050 | 0.2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | lower | 2020 | 0.2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | lower | 2050 | 0.2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | upper | 2020 | 0.2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | upper | 2050 | 0.2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2015 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2020 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2030 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2050 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2020 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2050 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2020 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2050 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.019432
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.019432
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.01943
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.01944
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.01
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.01
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.26
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.28
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 44448.9796
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 43810.956
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 42747.5832
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 41471.536
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 37537.0569
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 31475.8324
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 50829.2159
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 53274.9731
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.021267
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.021267
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.021267
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.021267
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.021267
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.010634
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.021267
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.021267
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.97318
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.97318
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.9726
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.97546
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.73
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.7
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.98
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.98
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.96585
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.96585
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.96524
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.96825
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.71
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.69
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.98
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.98
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.0102
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 0.98894
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 0.93577
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.89323
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.86133
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.70183
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.1591
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.2122
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.62739
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.61676
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.58485
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.56359
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.53169
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.43598
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.72309
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.76563
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.38281
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.37218
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.35091
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.31901
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.32965
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.26584
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.43598
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.44662
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 1.4462
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 1.4462
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 1.4462
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 1.4462
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 1.0102
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.8826
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 1.627
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 1.7439
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.032838
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.032669
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.032701
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.032701
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.024078
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.019262
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.036904
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.036921
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2015 | 0.51
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2020 | 0.51
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2030 | 0.52
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2050 | 0.52
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2020 | 0.5
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2050 | 0.5
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2020 | 0.67
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2050 | 0.67
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 5
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 5
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 5
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 5
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 4.5
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 4
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 5.5
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 5.5
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2015 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2030 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.31768
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.31837
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.31925
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.31925
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.29
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.29
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.42
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.42
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.3344
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.33512
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.33605
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.33605
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.32
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.32
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.44
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.44
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 267.52
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 268.1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 268.84
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 268.84
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 262.35
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 262.35
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 348.19
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 348.58
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.06
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.06
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.06
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.06
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.05
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.04
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.06
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.07
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 1.2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 3
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2015 | 20
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2020 | 20
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2030 | 20
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2050 | 10
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | lower | 2020 | 10
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | lower | 2050 | 10
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | upper | 2020 | 30
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | upper | 2050 | 20
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 0.3
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 0.3
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 0.3
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0.3
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0.1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0.1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2015 | 0.9825
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2020 | 0.9825
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2030 | 0.9825
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2050 | 0.9825
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | lower | 2020 | 0.95625
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | lower | 2050 | 0.9825
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | upper | 2020 | 0.99125
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | upper | 2050 | 0.99125
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 68055.854
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 65929.1085
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 62738.9904
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 57422.1268
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 56358.7541
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 44661.6542
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 76562.8357
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 75499.463
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 2.4564
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 2.3926
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 2.2756
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 2.0629
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 2.031
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 1.6695
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 2.8073
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 2.8286
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.3718
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.3398
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.2654
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 1.1591
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.1059
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.9145
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.5632
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.5738
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.0846
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.0527
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 0.99957
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 0.90387
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 0.9145
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.75499
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.2441
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.2548
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 1.829
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 1.829
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 1.8184
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 1.8184
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 1.4675
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 1.2867
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 2.0842
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 2.2544
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2015 | 12
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2020 | 12
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2030 | 12
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2050 | 12
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | lower | 2020 | 12
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | lower | 2050 | 12
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | upper | 2020 | 12
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | upper | 2050 | 12
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2015 | 0.15
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2020 | 0.15
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2030 | 0.15
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2050 | 0.15
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2020 | 0.15
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2050 | 0.15
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2020 | 0.15
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2050 | 0.15
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0.02
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0.02
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.02
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.02
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 0.02
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0.02
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 0.02
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0.02
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2015 | 2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2020 | 2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2030 | 2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2050 | 2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2020 | 2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2050 | 2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2020 | 2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2050 | 2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.0173
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.01664
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.016639
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.016639
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.01
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.01
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.13
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.13
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 22756.1762
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 22224.4898
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 21267.4544
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 19459.7207
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 18715.3598
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 14993.5553
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 25839.957
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 25414.6079
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.6682
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.66939
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.66847
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.66847
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.46
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.46
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.69
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.69
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.65148
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.65264
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.65167
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.65167
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.43
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.43
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.67
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.67
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 0.8188
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 0.79753
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 0.76563
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.69119
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.68056
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.56359
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 0.9464
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 0.9464
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.45725
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.44662
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.42535
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.38281
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.37218
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.30838
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.52105
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.53169
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.36155
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.35091
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.34028
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.30838
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.30838
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.25521
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.41472
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.42535
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.06
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.06
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.06
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.06
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.06
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.06
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 0.60612
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 0.61676
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 0.61676
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 0.61676
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 0.48915
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.43598
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 0.70183
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 0.75499
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.032976
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.032803
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.032834
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.032834
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.024257
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.019405
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.037051
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.037069
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2015 | 0.49
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2020 | 0.49
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2030 | 0.49
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2050 | 0.49
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2020 | 0.48
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2050 | 0.48
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2020 | 0.64
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2050 | 0.65
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 5
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 5
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 5
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 5
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 4.5
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 4
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 5.5
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 5.5
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2015 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2030 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | lower | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | lower | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | upper | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | upper | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.30038
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.30095
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.3018
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.3018
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.27
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.27
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.4
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.4
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.31619
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.31679
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.31769
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.31769
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.31
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.31
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.42
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.42
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 252.95
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 253.44
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 254.15
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 254.15
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 248.11
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 248.11
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 333.42
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 333.79
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.06
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.06
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.06
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.06
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.05
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.04
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.07
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.07
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 1.2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 3
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2015 | 20
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2020 | 20
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2030 | 20
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2050 | 10
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | lower | 2020 | 10
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | lower | 2050 | 10
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | upper | 2020 | 30
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | upper | 2050 | 20
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 0.3
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 0.3
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 0.3
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0.3
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0.1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0.1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2015 | 0.9825
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2020 | 0.9825
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2030 | 0.9825
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2050 | 0.9825
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | lower | 2020 | 0.95625
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | lower | 2050 | 0.9825
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | upper | 2020 | 0.99125
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | upper | 2050 | 0.99125
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 72309.3448
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 70182.5994
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 66992.4812
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 61675.6176
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 59548.8722
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 47851.7723
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 81879.6993
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 79752.9539
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 2.5946
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 2.5308
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 2.4032
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 2.1799
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 2.148
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 1.7652
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 2.9668
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 2.9881
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.4462
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.4143
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.3398
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 1.2229
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.1697
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.96767
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.6589
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.6589
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.1484
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.1165
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.0634
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 0.95704
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 0.9783
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.79753
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.3186
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.3186
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 1.829
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 1.8396
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 1.829
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 1.829
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 1.5525
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 1.3611
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 2.1055
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 2.2863
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2015 | 12
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2020 | 12
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2030 | 12
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2050 | 12
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | lower | 2020 | 12
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | lower | 2050 | 12
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | upper | 2020 | 12
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | upper | 2050 | 12
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2015 | 0.15
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2020 | 0.15
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2030 | 0.15
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2050 | 0.15
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2020 | 0.15
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2050 | 0.15
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2020 | 0.15
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2050 | 0.15
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0.02
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0.02
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.02
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.02
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 0.02
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0.02
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 0.02
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0.02
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2015 | 2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2020 | 2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2030 | 2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2050 | 2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2020 | 2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2050 | 2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2020 | 2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2050 | 2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.041302
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.039725
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.039721
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.039721
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.13
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.13
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 22756.1762
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 22224.4898
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 21267.4544
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 19459.7207
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 18715.3598
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 14993.5553
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 25839.957
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 25414.6079
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.6614
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.66365
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.66276
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.66276
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.47
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.47
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.69
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.69
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.64559
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.64781
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.64688
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.64688
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.43
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.43
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.67
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.67
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 0.8188
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 0.79753
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 0.76563
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.69119
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.68056
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.56359
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 0.9464
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 0.9464
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.45725
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.44662
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.42535
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.38281
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.37218
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.30838
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.52105
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.53169
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.36155
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.35091
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.34028
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.30838
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.30838
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.25521
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.41472
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.42535
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 0.57422
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 0.58485
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 0.58485
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 0.58485
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 0.48915
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.43598
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 0.66992
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 0.72309
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.025131
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.025131
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.025143
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.025081
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.019147
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.015273
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.029424
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.03051
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2015 | 0.46
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2020 | 0.46
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2030 | 0.46
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2050 | 0.45
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2020 | 0.44
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2050 | 0.44
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2020 | 0.62
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2050 | 0.63
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 2.5
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 2.5
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 2.5
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 2.5
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 1.5
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2015 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2030 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | ctrl | 2015 | 0.29303
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | ctrl | 2020 | 0.29303
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | ctrl | 2030 | 0.29389
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | ctrl | 2050 | 0.2898
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | lower | 2020 | 0.26
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | lower | 2050 | 0.26
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | upper | 2020 | 0.4
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H, F] | 1 | upper | 2050 | 0.41
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2015 | 0.30845
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2020 | 0.30845
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2030 | 0.30936
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2050 | 0.30505
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | lower | 2020 | 0.29
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | lower | 2050 | 0.29
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | upper | 2020 | 0.42
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | upper | 2050 | 0.43
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 24.68
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 24.68
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 24.75
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 24.4
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 23.84
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 23.78
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 33.36
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 34.03
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.18
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.18
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.18
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.18
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.16
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.14
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.21
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.23
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 1.2
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 80
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 50
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 40
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 20
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 40
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 10
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 50
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 40
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 2
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0.3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0.3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0.3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 2
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2015 | 0.9825
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2020 | 0.9825
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2030 | 0.9825
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2050 | 0.9825
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2020 | 0.95625
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2050 | 0.9825
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2020 | 0.99125
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2050 | 0.99125
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 136111.7079
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 131858.217
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 124414.608
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 114844.2535
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 110590.7627
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 86133.1902
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 153125.6714
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 148872.1805
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 3.2752
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 3.2008
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 3.0306
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 2.8817
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 2.6584
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 2.2012
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 3.775
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 3.9451
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 2.0948
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 2.0417
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.9353
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 1.8822
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.6589
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 1.3718
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 2.4032
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 2.5627
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.1803
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.1591
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.0953
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 0.99957
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.0102
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.82943
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.3611
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.393
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 1.9779
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 1.9779
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 1.9672
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 1.9991
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 1.5951
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 1.4143
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 2.265
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 2.4777
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 8
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 8
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 8
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 8
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 8
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 8
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 8
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 8
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.15
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.15
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.15
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.15
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2020 | 0.15
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2050 | 0.15
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2020 | 0.15
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2050 | 0.15
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2015 | 0.25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2020 | 0.25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2030 | 0.25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2050 | 0.25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | lower | 2020 | 0.25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | lower | 2050 | 0.25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | upper | 2020 | 0.25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | upper | 2050 | 0.25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.01729
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.01729
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.017288
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.017298
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.01
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.01
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.11
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.13
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 42003.2223
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 40727.1751
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 38494.0924
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 35197.6369
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 34134.2642
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 26158.9689
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 47213.7487
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 45406.015
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.69234
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.69234
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.69144
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.69571
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.47
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.45
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.73
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.73
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2015 | 0.67691
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2020 | 0.67691
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2030 | 0.67597
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | ctrl | 2050 | 0.68046
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | lower | 2020 | 0.44
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | lower | 2050 | 0.42
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | upper | 2020 | 0.71
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [A, H, F] | 1 | upper | 2050 | 0.71
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.0102
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 0.98894
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 0.93577
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.8826
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.8188
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.66992
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.1591
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.2016
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.64866
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.62739
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.59549
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.57422
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.51042
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.41472
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.74436
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.77626
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.36155
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.35091
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.34028
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.30838
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.30838
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.25521
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.42535
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.42535
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.06
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.06
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.06
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.06
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.06
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.06
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 0.60612
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 0.60612
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 0.60612
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 0.60612
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 0.48915
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.43598
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 0.70183
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 0.75499
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.022902
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.022902
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.022911
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.02287
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.01744
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.013926
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.025032
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.025037
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2015 | 0.18
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2020 | 0.18
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2030 | 0.19
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2050 | 0.18
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2020 | 0.18
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2050 | 0.18
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2020 | 0.19
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2050 | 0.19
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 1.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 1.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2015 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2030 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.1464
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.1464
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.14683
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.14466
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.13
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.13
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.15
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.15
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.1541
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.1541
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.15456
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.15227
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.15
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.14
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.16
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.16
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 3.08
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 3.08
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 3.09
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 3.05
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 3
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 2.95
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 3.12
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 3.12
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.49
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.49
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.49
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.49
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.41
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.37
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.56
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.62
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2015 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2030 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2015 | 1.2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2030 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2020 | 3
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2015 | 90
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2020 | 50
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2030 | 40
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2050 | 30
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2020 | 40
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2050 | 20
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2020 | 70
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2050 | 40
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2015 | 2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2020 | 0.3
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2030 | 0.3
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2050 | 0.3
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2020 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2050 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2020 | 2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | ctrl | 2015 | 0.9825
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | ctrl | 2020 | 0.9825
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | ctrl | 2030 | 0.9825
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | ctrl | 2050 | 0.9825
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | lower | 2020 | 0.95625
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | lower | 2050 | 0.9825
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | upper | 2020 | 0.99125
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | upper | 2050 | 0.99125
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 292427.4975
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 288174.0066
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 277540.2794
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 269033.2977
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 246702.4706
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 204167.5619
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 333899.0335
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 345596.1334
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2015 | 6.6142
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2020 | 6.444
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2030 | 6.1144
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2050 | 5.8911
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | lower | 2020 | 5.6146
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | lower | 2050 | 4.6576
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | upper | 2020 | 7.6031
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | upper | 2050 | 8.0285
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 4.3173
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 4.211
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 3.9876
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 3.9345
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 3.6686
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 3.0412
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 4.9553
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 5.3381
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 2.2969
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 2.2437
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 2.1267
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 1.946
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.9566
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 1.6163
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 2.6478
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 2.701
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 4.1365
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 4.1365
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 4.1259
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 4.1897
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 3.1795
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 2.8392
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 4.7107
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 5.1467
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2015 | 0.2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2020 | 0.2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2030 | 0.2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2050 | 0.2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | lower | 2020 | 0.2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | lower | 2050 | 0.2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | upper | 2020 | 0.2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | upper | 2050 | 0.2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2015 | 0.25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2020 | 0.25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2030 | 0.25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2050 | 0.25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2020 | 0.25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2050 | 0.25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2020 | 0.25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2050 | 0.25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.01729
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.01729
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.017288
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.017298
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.01
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.01
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.11
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.13
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 45193.3405
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 44342.6423
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 42853.9205
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 40939.8496
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 37962.406
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 31050.4834
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 51467.2395
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 52636.9495
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.84204
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.84204
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.84158
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.84385
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.74
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.72
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.86
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.86
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.83433
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.83433
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.83386
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.83624
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.72
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.71
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.85
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.85
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | ctrl | 2015 | 1.0208
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | ctrl | 2020 | 0.98894
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | ctrl | 2030 | 0.9464
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | ctrl | 2050 | 0.89323
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | lower | 2020 | 0.86133
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | lower | 2050 | 0.71246
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | upper | 2020 | 1.1697
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | upper | 2050 | 1.2229
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.65929
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.64866
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.61676
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.59549
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.56359
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.45725
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.76563
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.80816
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.35091
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.34028
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.32965
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.29774
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.29774
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.24458
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.40408
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.41472
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.06
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.06
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.06
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.06
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.06
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.06
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 0.63802
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 0.63802
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 0.63802
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 0.63802
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 0.48915
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.43598
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 0.72309
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 0.7869
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.028381
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.028381
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.028399
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.028399
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.020912
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.017287
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.031371
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.032976
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2015 | 0.45
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2020 | 0.45
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2030 | 0.46
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2050 | 0.46
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2020 | 0.43
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2050 | 0.44
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2020 | 0.6
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2050 | 0.61
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2.5
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3.5
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3.5
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2015 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2030 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.29936
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.29936
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.30028
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.30028
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.26
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.27
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.4
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.41
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.31511
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.31511
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.31609
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.31609
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.29
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.42
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.43
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 41.59
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 41.59
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 41.72
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 41.72
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 39.48
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 40.62
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 54.62
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 55.84
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.24
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.24
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.24
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.24
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.18
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.28
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 1.2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 40
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 30
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 30
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 20
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 20
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 10
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 40
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 30
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 0.3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0.3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0.3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0.3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0.1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0.1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2015 | 0.9545
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2020 | 0.9636
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2030 | 0.9909
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2050 | 0.99818
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2020 | 0.909
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2050 | 0.9545
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2020 | 0.99818
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2050 | 0.99909
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2015 | 133984.9625
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2020 | 129731.4716
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2030 | 122287.8626
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2050 | 109527.39
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | lower | 2020 | 109527.39
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | lower | 2050 | 84006.4447
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | upper | 2020 | 150998.926
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | upper | 2050 | 141428.5715
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 3.6793
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 3.5942
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 3.4134
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 3.0944
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 3.0412
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 2.4989
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 4.2216
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 4.2429
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2015 | 2.2756
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2020 | 2.2224
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2030 | 2.1055
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2050 | 1.9141
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | lower | 2020 | 1.8396
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | lower | 2050 | 1.5206
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | upper | 2020 | 2.6053
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | upper | 2050 | 2.6159
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2015 | 1.4143
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2020 | 1.3718
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2030 | 1.3079
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2050 | 1.1803
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | lower | 2020 | 1.2016
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | lower | 2050 | 0.9783
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | upper | 2020 | 1.6163
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | upper | 2050 | 1.627
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 2.2437
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 2.2437
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 2.2331
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 2.2331
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 1.7227
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 1.51
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 2.5521
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 2.7435
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 8
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 8
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 8
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 8
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 8
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 8
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 8
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 8
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.4
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.4
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.4
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.4
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2020 | 0.4
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2050 | 0.4
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2020 | 0.4
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2050 | 0.4
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0.02
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0.02
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.02
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.02
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 0.02
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0.02
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 0.02
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0.02
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2015 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2020 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2030 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2050 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | lower | 2020 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | lower | 2050 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | upper | 2020 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | upper | 2050 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.017679
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.017679
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.017677
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.017677
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.01
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.01
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.15
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.15
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2015 | 42215.8969
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2020 | 40939.8496
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2030 | 38600.4296
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2050 | 34453.276
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | lower | 2020 | 34559.6133
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | lower | 2050 | 26477.9807
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | upper | 2020 | 47426.4232
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | upper | 2050 | 44555.3169
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.063802
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.063802
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.063802
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.053169
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.063802
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.053169
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.074436
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.08507
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.70927
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.70927
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.70831
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.70831
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.48
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.47
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.74
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.73
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.69351
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.69351
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.69251
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.69251
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.45
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.44
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.72
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.71
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.1591
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 1.1378
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 1.074
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.9783
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.95704
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.7869
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.3292
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.3398
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.71246
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.70183
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.66992
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.60612
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.58485
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.47852
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.8188
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.82943
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.44662
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.43598
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.41472
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.37218
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.38281
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.30838
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.51042
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.51042
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.09
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.09
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.09
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.09
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.09
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.09
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 0.70183
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 0.70183
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 0.70183
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 0.70183
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 0.54232
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.47852
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 0.80816
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 0.87197
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.028554
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.028554
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.028572
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.028572
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.021147
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.017474
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.031556
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.03316
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2015 | 0.43
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2020 | 0.43
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2030 | 0.43
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2050 | 0.43
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2020 | 0.41
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2050 | 0.42
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2020 | 0.57
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2050 | 0.59
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2.5
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3.5
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3.5
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2015 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2030 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | lower | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | lower | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | upper | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | upper | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.28061
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.28061
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.2815
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.2815
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.25
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.25
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.38
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.39
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.29538
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.29538
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.29632
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.29632
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.27
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.28
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.4
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.41
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 38.99
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 38.99
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 39.11
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 39.11
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 36.88
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 38.07
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 52.01
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 53.28
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.26
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.26
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.26
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.26
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.22
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.19
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.29
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.32
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 1.2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 40
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 30
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 30
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 20
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 20
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 10
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 40
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 30
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 0.3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0.3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0.3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0.3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0.1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0.1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2015 | 0.9545
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2020 | 0.9636
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2030 | 0.9909
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2050 | 0.99818
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2020 | 0.909
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2050 | 0.9545
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2020 | 0.99818
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2050 | 0.99909
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2015 | 142491.9442
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2020 | 138238.4533
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2030 | 130794.8443
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2050 | 115907.6263
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | lower | 2020 | 116970.999
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | lower | 2050 | 89323.3083
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | upper | 2020 | 160569.2804
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | upper | 2050 | 150998.926
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 3.9345
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 3.8388
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 3.6367
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 3.3071
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 3.2433
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 2.6584
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 4.5087
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 4.53
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2015 | 2.4245
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2020 | 2.3713
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2030 | 2.2544
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2050 | 2.0417
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | lower | 2020 | 1.9672
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | lower | 2050 | 1.6163
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | upper | 2020 | 2.7754
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | upper | 2050 | 2.786
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2015 | 1.4994
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2020 | 1.4675
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2030 | 1.393
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | ctrl | 2050 | 1.2548
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | lower | 2020 | 1.276
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | lower | 2050 | 1.0421
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | upper | 2020 | 1.7333
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] |  | upper | 2050 | 1.7333
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 2.2756
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 2.2756
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 2.2756
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 2.2756
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 1.8396
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 1.6163
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 2.6159
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 2.8179
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 8
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 8
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 8
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 8
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 8
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 8
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 8
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 8
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.4
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.4
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.4
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.4
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2020 | 0.4
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2050 | 0.4
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2020 | 0.4
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2050 | 0.4
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0.02
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0.02
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.02
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.02
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 0.02
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0.02
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 0.02
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0.02
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2015 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2020 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2030 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2050 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | lower | 2020 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | lower | 2050 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | upper | 2020 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | upper | 2050 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.042201
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.042201
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.042197
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.042197
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.15
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.15
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2015 | 42215.8969
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2020 | 40939.8496
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2030 | 38600.4296
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2050 | 34453.276
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | lower | 2020 | 34559.6133
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | lower | 2050 | 26477.9807
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | upper | 2020 | 47426.4232
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | upper | 2050 | 44555.3169
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.063802
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.063802
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.063802
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.053169
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.063802
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.053169
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.074436
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.08507
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.70348
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.70348
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.70257
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.70257
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.49
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.49
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.73
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.72
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.68871
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.68871
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.68775
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.68775
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.47
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.46
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.71
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.7
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.1591
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 1.1378
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 1.074
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.9783
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.95704
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.7869
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.3292
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.3398
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.71246
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.70183
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.66992
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.60612
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.58485
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.47852
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.8188
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.82943
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.44662
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.43598
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.41472
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.37218
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.38281
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.30838
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.51042
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.51042
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.06
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.06
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.06
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.06
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.06
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.06
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 0.66992
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 0.66992
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 0.66992
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 0.66992
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 0.54232
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.47852
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 0.77626
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 0.84006
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.02847
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.02847
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.028488
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.028396
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.02091
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.017285
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.031682
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.032112
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2015 | 0.46
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2020 | 0.46
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2030 | 0.46
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2050 | 0.45
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2020 | 0.43
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2050 | 0.44
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2020 | 0.47
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2050 | 0.47
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 2.5
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 2.5
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 2.5
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 2.5
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 1.5
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2015 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2020 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2030 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2020 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2020 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.30027
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.30027
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.3012
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.29677
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.26
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.27
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.31
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.31
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.31607
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.31607
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.31706
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.31239
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.29
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.3
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.33
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.33
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 25.29
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 25.29
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 25.36
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 24.99
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 23.67
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 24.33
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 25.72
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 25.84
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 3.4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 3
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 4.6
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 5
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.28
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.28
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.28
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.28
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.24
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.21
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.32
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.35
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 1.2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 3
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 90
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 70
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 50
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 30
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 20
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 10
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 90
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 50
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0.3
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0.3
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0.3
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0.1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0.1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2020 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2015 | 0.9545
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2020 | 0.9636
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2030 | 0.9909
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | ctrl | 2050 | 0.99818
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2020 | 0.909
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | lower | 2050 | 0.9545
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2020 | 0.99818
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2] | upper | 2050 | 0.99909
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | 1 | ctrl | 2015 | 156315.7895
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | 1 | ctrl | 2020 | 152062.2987
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | 1 | ctrl | 2030 | 142491.9442
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | 1 | ctrl | 2050 | 131858.217
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | 1 | lower | 2020 | 127604.7262
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | 1 | lower | 2050 | 101020.4082
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | 1 | upper | 2020 | 178646.6166
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J | 1 | upper | 2050 | 170139.6349
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 3.8919
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 3.7962
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 3.6048
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 3.4134
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 3.1901
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 2.7435
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 4.5831
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 4.6682
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 2.3607
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 2.2969
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 2.1799
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 2.1055
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 1.8822
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 1.6589
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 2.8073
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 2.8711
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 1.5419
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 1.4994
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 1.4249
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 1.3079
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 1.3079
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 1.0846
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 1.7652
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 1.8077
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L | 1 | ctrl | 2015 | 2.2331
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L | 1 | ctrl | 2020 | 2.2331
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L | 1 | ctrl | 2030 | 2.2224
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L | 1 | ctrl | 2050 | 2.2544
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L | 1 | lower | 2020 | 1.712
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L | 1 | lower | 2050 | 1.5313
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L | 1 | upper | 2020 | 2.5415
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L | 1 | upper | 2050 | 2.7754
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 8
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 8
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 8
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 8
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 8
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 8
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 8
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 8
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2020 | 0.4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2050 | 0.4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2020 | 0.4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2050 | 0.4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2015 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2020 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2030 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | ctrl | 2050 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | lower | 2020 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | lower | 2050 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | upper | 2020 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Regulation ability | Warm start-up time [hours] | hours |  | E | 1 | upper | 2050 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.017669
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.017669
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.017667
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.017677
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.01
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.01
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.15
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.15
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2015 | 49553.1686
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2020 | 48064.4468
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2030 | 45299.6778
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2050 | 41152.5242
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | lower | 2020 | 40408.1633
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | lower | 2050 | 31475.8324
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | upper | 2020 | 56358.754
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | upper | 2050 | 53062.2986
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.074436
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.074436
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.063802
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.063802
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.063802
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.053169
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.08507
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.08507
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.70205
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.70205
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.70107
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.70573
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.56
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.56
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.74
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.73
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.68625
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.68625
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.68522
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.69011
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.53
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.53
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.72
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.71
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.2335
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 1.2016
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 1.1378
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 1.0634
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 1.0102
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.86133
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.4462
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.4568
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.74436
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.72309
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.69119
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.65929
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.59549
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.52105
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.89323
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.89323
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.48915
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.47852
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.44662
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.40408
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.41472
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.34028
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.56359
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.56359
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.09
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.09
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.09
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.09
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.09
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.09
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 0.70183
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 0.70183
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 0.70183
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 0.70183
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 0.54232
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.47852
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 0.80816
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 0.87197
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2015 | 0.023732
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2020 | 0.023732
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2030 | 0.023741
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | ctrl | 2050 | 0.023698
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2020 | 0.018068
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | lower | 2050 | 0.014428
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2020 | 0.025941
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  | 1 | upper | 2050 | 0.025902
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2015 | 0.18
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2020 | 0.18
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2030 | 0.18
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | ctrl | 2050 | 0.18
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2020 | 0.17
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | lower | 2050 | 0.17
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2020 | 0.18
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cb coefficient (40°C/80°C) |  |  |  |  | upper | 2050 | 0.18
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 1.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 1.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2015 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2030 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | ctrl | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | lower | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Cv coefficient (40°C/80°C) |  |  | I |  | upper | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.14486
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.14486
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.14532
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.14304
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.13
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.13
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.15
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.15
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.15249
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.15249
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.15297
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.15057
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.14
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.14
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.16
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.16
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.04
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.04
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.04
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.04
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.04
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.04
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.04
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.04
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 3.05
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 3.05
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 3.06
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 3.01
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 2.97
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 2.92
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 3.09
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 3.04
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 4
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 4
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 4
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 4
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 3.4
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 3
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 4.6
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.98
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.98
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.98
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.84
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.75
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 1.13
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 1.25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
09c Straw, Small | Biomass CHP - back pressure - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2015 | 16
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2020 | 11
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2030 | 8
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2050 | 4
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2020 | 4
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2050 | 2
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2020 | 16
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2050 | 16
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2015 | 1.2
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2030 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2050 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2020 | 3
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2015 | 90
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2020 | 70
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2030 | 50
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2050 | 40
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2020 | 50
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2050 | 40
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2020 | 90
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2050 | 50
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2015 | 2
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2020 | 0.3
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2030 | 0.3
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | ctrl | 2050 | 0.3
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2020 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | lower | 2050 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2020 | 2
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | 1 | upper | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | ctrl | 2015 | 0.9545
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | ctrl | 2020 | 0.9636
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | ctrl | 2030 | 0.9909
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | ctrl | 2050 | 0.99818
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | lower | 2020 | 0.909
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | lower | 2050 | 0.9545
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | upper | 2020 | 0.99818
09c Straw, Small | Biomass CHP - back pressure - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | F | 1 | upper | 2050 | 0.99909
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2015 | 338152.5243
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2020 | 332835.6607
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2030 | 321138.5608
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | ctrl | 2050 | 311568.2064
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | lower | 2020 | 284983.8884
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | lower | 2050 | 241385.607
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | upper | 2020 | 384940.9239
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | J |  | upper | 2050 | 398764.7693
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2015 | 7.2841
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2020 | 7.1033
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2030 | 6.7418
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | ctrl | 2050 | 6.4759
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | lower | 2020 | 6.1995
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | lower | 2050 | 5.4126
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | upper | 2020 | 8.3794
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, J, K] | 1 | upper | 2050 | 8.8366
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 4.1153
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 4.0089
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 3.8069
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 3.775
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 3.4985
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 3.1795
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 4.732
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 5.1148
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 3.1689
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 3.0944
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 2.9349
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 2.701
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 2.701
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 2.2331
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 3.6474
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 3.7218
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 4.8064
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 4.8064
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 4.7852
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 4.8596
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 3.5517
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 3.1795
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 5.4445
09c Straw, Small | Biomass CHP - back pressure - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 5.9336
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2015 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2020 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2030 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | ctrl | 2050 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | lower | 2020 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | lower | 2050 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | upper | 2020 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | D | 1 | upper | 2050 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2015 | 0.25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2020 | 0.25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2030 | 0.25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2050 | 0.25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2020 | 0.25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2050 | 0.25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2020 | 0.25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2050 | 0.25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.017669
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.017669
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.017667
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.017677
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.01
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.01
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.14
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.15
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2015 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2030 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | ctrl | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2020 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | lower | 2050 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Combustion air humidification |  |  | [C, M] |  | upper | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2015 | 51679.9141
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2020 | 50722.8786
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2030 | 49021.4823
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | ctrl | 2050 | 46894.7368
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | lower | 2020 | 43385.6069
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | lower | 2050 | 36367.3469
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | upper | 2020 | 58804.5113
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 | J |  | upper | 2050 | 60080.5585
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2015 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2030 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | ctrl | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2020 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | lower | 2050 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Flue gas condensation |  |  | [C, M] |  | upper | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.08507
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.08507
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.074436
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.074436
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.074436
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.063802
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.095704
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.095704
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.86339
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.86339
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.86291
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.86529
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2020 | 0.73
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | lower | 2050 | 0.72
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2020 | 0.88
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, annual average) [] |  |  | [B, H] | 1 | upper | 2050 | 0.88
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2015 | 0.85576
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2020 | 0.85576
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2030 | 0.85526
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | ctrl | 2050 | 0.85776
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2020 | 0.72
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | lower | 2050 | 0.71
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2020 | 0.87
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Heat efficiency (net, name plate) [] |  |  | [B, H] | 1 | upper | 2050 | 0.87
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | ctrl | 2015 | 1.1059
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | ctrl | 2020 | 1.0846
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | ctrl | 2030 | 1.0315
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | ctrl | 2050 | 0.9783
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | lower | 2020 | 0.9464
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | lower | 2050 | 0.8188
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | upper | 2020 | 1.276
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [E, J, K] | 1 | upper | 2050 | 1.3292
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.62739
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.61676
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.58485
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.56359
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.53169
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.47852
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.72309
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.76563
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.48915
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.46788
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.44662
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.40408
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.41472
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.34028
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.55295
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.56359
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.09
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.09
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.09
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.09
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.09
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.09
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 0.73373
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 0.73373
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 0.73373
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 0.73373
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 0.54232
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.47852
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 0.82943
09c Straw, Small | Biomass CHP - back pressure - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 0.89323
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2015 | 0.022162
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2020 | 0.022162
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2030 | 0.022162
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2050 | 0.022162
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | lower | 2020 | 0.021135
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | lower | 2050 | 0.01691
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | upper | 2020 | 0.024723
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | upper | 2050 | 0.024702
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 1.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 1.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2015 | 6.84
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2020 | 6.84
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2030 | 6.84
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2050 | 6.84
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2020 | 5.34
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2050 | 5.34
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2020 | 6.86
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2050 | 6.87
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.1401
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.1401
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.1401
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.1401
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2020 | 0.89
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2050 | 0.89
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2020 | 1.15
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2050 | 1.15
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.1401
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.1401
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.1401
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.1401
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2020 | 0.89
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2050 | 0.89
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2020 | 1.15
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2050 | 1.15
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 1.7
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 1.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 2.3
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 2.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2015 | 0.22
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2020 | 0.22
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2030 | 0.22
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2050 | 0.22
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | lower | 2020 | 0.19
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | lower | 2050 | 0.16
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | upper | 2020 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | upper | 2050 | 0.27
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2015 | 16
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2020 | 11
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2030 | 8
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2050 | 4
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2020 | 4
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2050 | 2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2020 | 16
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2050 | 16
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2015 | 4
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2020 | 3
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2030 | 3
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2050 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2020 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2050 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2020 | 4
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2050 | 4
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2015 | 90
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2020 | 60
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2030 | 50
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2050 | 40
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2020 | 40
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2050 | 30
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2020 | 80
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2050 | 40
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2015 | 2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2020 | 0.3
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2030 | 0.3
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2050 | 0.3
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2020 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2050 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2020 | 2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2050 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2015 | 0.9797
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2020 | 0.9797
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2030 | 0.9797
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2050 | 0.9797
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2020 | 0.8985
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2050 | 0.9797
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2020 | 0.98985
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2050 | 0.98985
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2015 | 35091.2997
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2020 | 34559.6133
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2030 | 33496.2406
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2050 | 31475.8325
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | lower | 2020 | 29561.7616
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | lower | 2050 | 24244.898
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | upper | 2020 | 40089.1515
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | upper | 2050 | 40408.1633
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.75499
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.73373
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.70183
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.62739
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.63802
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.52105
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.86133
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.87197
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.43598
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.42535
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.40408
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.36155
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.37218
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.29774
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.49979
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.49979
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.31901
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.30838
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.29774
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.26584
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.26584
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.22331
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.36155
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.37218
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2015 | 2.7541
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 2.8924
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 3.6474
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 4.0195
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2020 | 2.4883
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 3.4985
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2020 | 3.9451
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 5.5508
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2015 | 1.4887
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 1.627
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 2.382
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 2.7541
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2020 | 1.6057
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 2.7222
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2020 | 2.1161
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 3.5942
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2015 | 1.2654
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 1.2654
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 1.2654
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 1.2654
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2020 | 0.8826
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 0.77626
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2020 | 1.829
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 1.9566
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2015 | 0.2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2020 | 0.2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2030 | 0.2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2050 | 0.2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | lower | 2020 | 0.2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | lower | 2050 | 0.2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | upper | 2020 | 0.2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | upper | 2050 | 0.2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2015 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2020 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2030 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2050 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2020 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2050 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2020 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2050 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2015 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2020 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2030 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2050 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2020 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2050 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2020 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2050 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2015 | 0.019432
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2020 | 0.019432
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2030 | 0.019432
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2050 | 0.019432
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2020 | 0.01
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2050 | 0.01
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2020 | 0.26
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2050 | 0.26
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2015 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2020 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2030 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2050 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | lower | 2020 | 0
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | lower | 2050 | 0
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | upper | 2020 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | upper | 2050 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 40089.1515
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 39451.1278
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 38175.0806
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 35835.6606
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 33708.9151
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 27647.6907
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 45618.6896
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 46044.0387
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2015 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2020 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2030 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2050 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | lower | 2020 | 0
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | lower | 2050 | 0
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | upper | 2020 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | upper | 2050 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2015 | 0.021267
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2020 | 0.021267
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2030 | 0.021267
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2050 | 0.021267
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | lower | 2020 | 0.021267
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | lower | 2050 | 0.010634
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | upper | 2020 | 0.021267
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | upper | 2050 | 0.021267
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | ctrl | 2015 | 0.86133
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | ctrl | 2020 | 0.84006
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | ctrl | 2030 | 0.79753
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | ctrl | 2050 | 0.72309
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | lower | 2020 | 0.73373
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | lower | 2050 | 0.59549
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | upper | 2020 | 0.98894
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | upper | 2050 | 0.99957
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2015 | 0.49979
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2020 | 0.48915
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2030 | 0.45725
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2050 | 0.41472
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2020 | 0.42535
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2050 | 0.34028
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2020 | 0.57422
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2050 | 0.57422
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2015 | 0.36155
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2020 | 0.35091
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2030 | 0.34028
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2050 | 0.30838
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2020 | 0.30838
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2050 | 0.25521
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2020 | 0.41472
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2050 | 0.41472
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2015 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2020 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2030 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2050 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | lower | 2020 | 0
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | lower | 2050 | 0
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | upper | 2020 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | upper | 2050 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2015 | 3.1369
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2020 | 3.2965
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2030 | 4.1578
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2050 | 4.5831
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | lower | 2020 | 2.8498
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | lower | 2050 | 4.0089
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | upper | 2020 | 3.5091
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | upper | 2050 | 4.9447
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2015 | 0.022039
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2020 | 0.022039
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2030 | 0.022039
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2050 | 0.022026
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | lower | 2020 | 0.02098
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | lower | 2050 | 0.017093
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | upper | 2020 | 0.024587
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | upper | 2050 | 0.024549
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 1.5
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 1.5
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 2.5
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 2.5
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2015 | 51.64
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2020 | 51.64
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2030 | 51.64
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2050 | 51.64
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2020 | 40.38
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2050 | 39.66
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2020 | 51.81
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2050 | 51.86
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.1475
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.1475
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.1475
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.1475
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2020 | 0.89
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2050 | 0.88
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2020 | 1.16
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2050 | 1.16
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.1475
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.1475
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.1475
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.1475
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2020 | 0.89
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2050 | 0.88
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2020 | 1.16
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2050 | 1.16
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 1.7
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 1.5
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 2.3
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 2.5
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2015 | 0.06
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2020 | 0.06
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2030 | 0.06
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2050 | 0.06
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | lower | 2020 | 0.05
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | lower | 2050 | 0.04
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | upper | 2020 | 0.07
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | upper | 2050 | 0.07
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2015 | 16
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2020 | 11
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2030 | 8
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2050 | 4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2020 | 4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2050 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2020 | 16
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2050 | 16
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2015 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2020 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2030 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2050 | 0
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2020 | 0
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2050 | 0
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2020 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2050 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2015 | 90
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2020 | 60
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2030 | 40
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2050 | 30
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2020 | 40
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2050 | 20
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2020 | 80
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2050 | 40
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2015 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2020 | 0.3
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2030 | 0.3
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | ctrl | 2050 | 0.3
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2020 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | lower | 2050 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2020 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | I | 2 | upper | 2050 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2015 | 0.9797
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2020 | 0.9797
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2030 | 0.9797
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2050 | 0.9797
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2020 | 0.94925
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2050 | 0.9797
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2020 | 0.98985
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2050 | 0.98985
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2015 | 45512.3523
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2020 | 44661.6542
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2030 | 43066.5951
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2050 | 40620.8378
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | lower | 2020 | 38068.7433
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | lower | 2050 | 30625.1343
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | upper | 2020 | 51573.5768
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | upper | 2050 | 51573.5768
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.54232
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.52105
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.49979
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.47852
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.45725
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.37218
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.61676
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.65929
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.39345
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.38281
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.36155
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.36155
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.32965
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.27648
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.45725
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.48915
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.14887
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.13824
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.13824
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.11697
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.1276
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.095704
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.17014
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.17014
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2015 | 2.7329
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 2.8711
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 3.6261
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 3.9983
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2020 | 2.4777
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 3.4772
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2020 | 3.9132
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 5.604
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2015 | 1.4781
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 1.6163
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 2.3713
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 2.7435
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2020 | 1.5951
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 2.7116
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2020 | 2.1055
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 3.6261
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2015 | 1.2548
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 1.2548
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 1.2548
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 1.2548
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2020 | 0.87197
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 0.76563
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2020 | 1.8077
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 1.9779
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 8
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 8
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 8
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 8
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 8
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 8
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 8
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 8
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2015 | 0.4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2020 | 0.4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2030 | 0.4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2050 | 0.4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2020 | 0.4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2050 | 0.4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2020 | 0.4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2050 | 0.4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2015 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2020 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2030 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2050 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2020 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2050 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2020 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2050 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2015 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2020 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2030 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2050 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2020 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2050 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2020 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2050 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2015 | 0.019432
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2020 | 0.019432
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2030 | 0.019432
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2050 | 0.019442
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2020 | 0.01
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2050 | 0.01
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2020 | 0.26
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2050 | 0.28
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2015 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2020 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2030 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2050 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | lower | 2020 | 0
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | lower | 2050 | 0
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | upper | 2020 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | upper | 2050 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 52211.6004
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 51254.565
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 49340.4941
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 46682.0623
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 43704.6187
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 35091.2997
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 59123.5231
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 59229.8604
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2015 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2020 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2030 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2050 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | lower | 2020 | 0
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | lower | 2050 | 0
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | upper | 2020 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | upper | 2050 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2015 | 0.021267
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2020 | 0.021267
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2030 | 0.021267
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2050 | 0.010634
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | lower | 2020 | 0.010634
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | lower | 2050 | 0.010634
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | upper | 2020 | 0.021267
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | upper | 2050 | 0.021267
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | ctrl | 2015 | 0.61676
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | ctrl | 2020 | 0.60612
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | ctrl | 2030 | 0.57422
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | ctrl | 2050 | 0.55295
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | lower | 2020 | 0.52105
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | lower | 2050 | 0.42535
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | upper | 2020 | 0.71246
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | upper | 2050 | 0.75499
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2015 | 0.44662
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2020 | 0.43598
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2030 | 0.41472
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2050 | 0.41472
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2020 | 0.38281
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2050 | 0.31901
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2020 | 0.52105
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2050 | 0.56359
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2015 | 0.17014
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2020 | 0.15951
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2030 | 0.14887
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2050 | 0.13824
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2020 | 0.13824
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2050 | 0.11697
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2020 | 0.19141
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2050 | 0.19141
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2015 | 0.25
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2020 | 0.25
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2030 | 0.25
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2050 | 0.25
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | lower | 2020 | 0
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | lower | 2050 | 0
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | upper | 2020 | 0.25
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | upper | 2050 | 0.25
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2015 | 3.1369
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2020 | 3.2965
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2030 | 4.1578
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2050 | 4.5938
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | lower | 2020 | 2.8498
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | lower | 2050 | 4.0089
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | upper | 2020 | 3.5091
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | upper | 2050 | 4.9447
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2015 | 0.022012
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2020 | 0.022012
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2030 | 0.022012
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2050 | 0.021998
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | lower | 2020 | 0.020946
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | lower | 2050 | 0.017064
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | upper | 2020 | 0.024556
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | upper | 2050 | 0.024519
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 2.5
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 2.5
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 2.5
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 2.5
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 3
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 3
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2015 | 103.43
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2020 | 103.43
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2030 | 103.43
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2050 | 103.42
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2020 | 80.92
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2050 | 79.47
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2020 | 103.78
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2050 | 103.87
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.1492
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.1492
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.1492
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.1492
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2020 | 0.89
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2050 | 0.88
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2020 | 1.16
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2050 | 1.16
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.1492
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.1492
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.1492
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.1492
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2020 | 0.89
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2050 | 0.88
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2020 | 1.16
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2050 | 1.16
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 1.7
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 1.5
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 2.3
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 2.5
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2015 | 0.05
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2020 | 0.05
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2030 | 0.05
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2050 | 0.05
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | lower | 2020 | 0.04
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | lower | 2050 | 0.04
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | upper | 2020 | 0.06
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | upper | 2050 | 0.06
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2015 | 3
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2020 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2030 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2050 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2020 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2050 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2020 | 3
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2050 | 3
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2015 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2020 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2030 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2050 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2020 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2050 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2020 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2050 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [2, 3] | ctrl | 2015 | 90
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [2, 3] | ctrl | 2020 | 60
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [2, 3] | ctrl | 2030 | 40
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [2, 3] | ctrl | 2050 | 20
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [2, 3] | lower | 2020 | 40
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [2, 3] | lower | 2050 | 20
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [2, 3] | upper | 2020 | 60
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [2, 3] | upper | 2050 | 40
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2015 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2020 | 0.3
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2030 | 0.3
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2050 | 0.3
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2020 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 3 | lower | 2050 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2020 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 3 | upper | 2050 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2015 | 0.9797
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2020 | 0.9797
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2030 | 0.9797
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2050 | 0.9797
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2020 | 0.94925
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2050 | 0.9797
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2020 | 0.98985
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2050 | 0.98985
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2015 | 37430.7197
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2020 | 36792.696
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2030 | 35410.3115
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | ctrl | 2050 | 33389.9033
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | lower | 2020 | 31369.4952
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | lower | 2050 | 25095.5961
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | upper | 2020 | 42428.5714
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 |  | upper | 2050 | 42428.5714
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.47852
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.46788
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.44662
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.42535
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.40408
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.32965
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.55295
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.58485
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.36155
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.35091
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.32965
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.32965
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.30838
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.25521
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.41472
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.44662
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.11697
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.11697
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.10634
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.095704
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.095704
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.08507
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.13824
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.13824
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2015 | 2.7329
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 2.8711
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 3.6261
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 3.9983
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2020 | 2.467
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 3.4772
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2020 | 3.9026
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 5.5933
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2015 | 1.4781
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 1.6163
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 2.3607
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 2.7329
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2020 | 1.5951
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 2.7116
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2020 | 2.1055
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 3.6261
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2015 | 1.2548
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 1.2548
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 1.2548
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 1.2548
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2020 | 0.87197
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 0.76563
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2020 | 1.8077
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 1.9779
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 8
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 8
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 8
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 8
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 8
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 8
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 8
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 8
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2015 | 0.4
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2020 | 0.4
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2030 | 0.4
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2050 | 0.4
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2020 | 0.4
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2050 | 0.4
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2020 | 0.4
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2050 | 0.4
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2015 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2020 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2030 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2050 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2020 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2050 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2020 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2050 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2015 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2020 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2030 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2050 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2020 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2050 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2020 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2050 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2015 | 0.019432
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2020 | 0.019432
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2030 | 0.019432
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2050 | 0.019442
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2020 | 0.01
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2050 | 0.01
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2020 | 0.26
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2050 | 0.28
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2015 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2020 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2030 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2050 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | lower | 2020 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | lower | 2050 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | upper | 2020 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | upper | 2050 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 43066.5951
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 42215.8969
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 40620.8378
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 38387.7551
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 36048.3351
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 28923.7379
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 48808.8077
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 48702.4705
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2015 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2020 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2030 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2050 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | lower | 2020 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | lower | 2050 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | upper | 2020 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | upper | 2050 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2015 | 0.010634
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2020 | 0.010634
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2030 | 0.010634
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2050 | 0.010634
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | lower | 2020 | 0.010634
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | lower | 2050 | 0.010634
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | upper | 2020 | 0.021267
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | upper | 2050 | 0.021267
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | ctrl | 2015 | 0.55295
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | ctrl | 2020 | 0.53169
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | ctrl | 2030 | 0.51042
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | ctrl | 2050 | 0.48915
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | lower | 2020 | 0.46788
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | lower | 2050 | 0.38281
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | upper | 2020 | 0.63802
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | L | 1 | upper | 2050 | 0.66992
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2015 | 0.41472
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2020 | 0.40408
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2030 | 0.38281
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2050 | 0.38281
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2020 | 0.35091
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2050 | 0.28711
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2020 | 0.47852
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2050 | 0.51042
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2015 | 0.13824
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2020 | 0.1276
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2030 | 0.1276
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2050 | 0.11697
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2020 | 0.11697
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2050 | 0.095704
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2020 | 0.15951
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2050 | 0.15951
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2015 | 0.25
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2020 | 0.25
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2030 | 0.25
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2050 | 0.25
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | lower | 2020 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | lower | 2050 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | upper | 2020 | 0.25
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | upper | 2050 | 0.25
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2015 | 3.1369
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2020 | 3.2965
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2030 | 4.1578
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2050 | 4.5938
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | lower | 2020 | 2.8498
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | lower | 2050 | 4.0089
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | upper | 2020 | 3.5091
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | upper | 2050 | 4.9447
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2015 | 0.020554
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2020 | 0.020554
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2030 | 0.020554
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | ctrl | 2050 | 0.020554
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | lower | 2020 | 0.017045
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | lower | 2050 | 0.013836
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | upper | 2020 | 0.022952
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, K] |  | upper | 2050 | 0.022915
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 1.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 1.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2015 | 6.07
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2020 | 6.07
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2030 | 6.07
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2050 | 6.07
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2020 | 5.45
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2050 | 5.37
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2020 | 6.09
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2050 | 6.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.0117
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.0117
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.0117
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.0117
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2020 | 0.9
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2050 | 0.89
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2020 | 1.02
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2050 | 1.02
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.0117
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.0117
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.0117
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.0117
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2020 | 0.9
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2050 | 0.89
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2020 | 1.02
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2050 | 1.02
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.55
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.45
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.75
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2015 | 0.16
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2020 | 0.16
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2030 | 0.16
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2050 | 0.16
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | lower | 2020 | 0.14
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | lower | 2050 | 0.12
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | upper | 2020 | 0.19
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | upper | 2050 | 0.21
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2015 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2020 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2030 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2050 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2020 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2050 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2020 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2050 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2015 | 1.2
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2020 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2030 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2050 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2020 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2050 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2020 | 3
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2050 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2015 | 90
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2020 | 50
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2030 | 40
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2050 | 40
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2020 | 40
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2050 | 20
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2020 | 70
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2050 | 40
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2015 | 2
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2020 | 0.3
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2030 | 0.3
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2050 | 0.3
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2020 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2050 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2020 | 2
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2050 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2015 | 0.9825
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2020 | 0.9825
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2030 | 0.9825
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2050 | 0.9825
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2020 | 0.9125
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2050 | 0.9825
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2020 | 0.99125
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2050 | 0.99125
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2015 | 35729.3233
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2020 | 34772.2879
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2030 | 32964.5543
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2050 | 29668.0988
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | lower | 2020 | 29774.4361
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | lower | 2050 | 23075.188
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | upper | 2020 | 40301.826
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | upper | 2050 | 39451.1278
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.77626
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.75499
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.72309
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.64866
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.65929
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.54232
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.89323
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.95704
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.46788
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.45725
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.43598
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.39345
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.40408
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.32965
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.54232
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.60612
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2015 | 0.30838
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2020 | 0.29774
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2030 | 0.28711
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | ctrl | 2050 | 0.25521
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2020 | 0.25521
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | lower | 2050 | 0.21267
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2020 | 0.35091
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, L] |  | upper | 2050 | 0.35091
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2015 | 1.9566
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2020 | 2.0842
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2030 | 2.786
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2050 | 3.1369
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | lower | 2020 | 1.9247
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | lower | 2050 | 2.9136
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | upper | 2020 | 2.4458
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | upper | 2050 | 3.7431
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2015 | 1.3718
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2020 | 1.51
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2030 | 2.2118
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2050 | 2.5521
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | lower | 2020 | 1.4887
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | lower | 2050 | 2.5202
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | upper | 2020 | 1.712
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | upper | 2050 | 2.9455
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2015 | 0.57422
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2020 | 0.57422
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2030 | 0.57422
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | ctrl | 2050 | 0.57422
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | lower | 2020 | 0.43598
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | lower | 2050 | 0.38281
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | upper | 2020 | 0.73373
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, M] |  | upper | 2050 | 0.79753
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2015 | 0.4
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2020 | 0.4
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2030 | 0.4
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2050 | 0.4
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | lower | 2020 | 0.4
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | lower | 2050 | 0.4
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | upper | 2020 | 0.4
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | upper | 2050 | 0.4
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2015 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2020 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2030 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2050 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2020 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2050 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2020 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2050 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2015 | 0.25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2020 | 0.25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2030 | 0.25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2050 | 0.25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2020 | 0.25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2050 | 0.25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2020 | 0.25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2050 | 0.25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2015 | 0.01729
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2020 | 0.01729
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2030 | 0.01729
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2050 | 0.01729
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2020 | 0.01
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2050 | 0.01
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2020 | 0.11
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2050 | 0.13
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2015 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2020 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2030 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | ctrl | 2050 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | lower | 2020 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | lower | 2050 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | upper | 2020 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Combustion air humidification |  |  | [D, N] |  | upper | 2050 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 36154.6724
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 35197.6369
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 33283.5661
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 30093.4479
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 30093.4479
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 23287.8625
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 40727.1751
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 39876.4769
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2015 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2020 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2030 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | ctrl | 2050 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | lower | 2020 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | lower | 2050 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | upper | 2020 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Flue gas condensation |  |  | [D, N] |  | upper | 2050 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2015 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2020 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2030 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | ctrl | 2050 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | lower | 2020 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | lower | 2050 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | upper | 2020 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | L |  | upper | 2050 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | ctrl | 2015 | 0.7869
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | ctrl | 2020 | 0.76563
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | ctrl | 2030 | 0.73373
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | ctrl | 2050 | 0.65929
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | lower | 2020 | 0.66992
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | lower | 2050 | 0.55295
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | upper | 2020 | 0.90387
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, L] | 1 | upper | 2050 | 0.96767
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2015 | 0.47852
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2020 | 0.46788
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2030 | 0.44662
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2050 | 0.40408
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2020 | 0.40408
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2050 | 0.32965
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2020 | 0.55295
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2050 | 0.60612
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2015 | 0.30838
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2020 | 0.29774
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2030 | 0.28711
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | ctrl | 2050 | 0.25521
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2020 | 0.26584
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | lower | 2050 | 0.21267
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2020 | 0.36155
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | L |  | upper | 2050 | 0.36155
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2015 | 0.06
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2020 | 0.06
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2030 | 0.06
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | ctrl | 2050 | 0.06
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | lower | 2020 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | lower | 2050 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | upper | 2020 | 0.06
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | D |  | upper | 2050 | 0.06
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2015 | 1.9779
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2020 | 2.1055
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2030 | 2.8179
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | ctrl | 2050 | 3.1689
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | lower | 2020 | 1.9566
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | lower | 2050 | 2.9562
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | upper | 2020 | 2.2224
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | M |  | upper | 2050 | 3.3496
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, J] |  | ctrl | 2015 | 0.020956
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, J] |  | ctrl | 2020 | 0.020956
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, J] |  | ctrl | 2030 | 0.020956
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, J] |  | ctrl | 2050 | 0.020956
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, J] |  | lower | 2020 | 0.018096
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, J] |  | lower | 2050 | 0.014478
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, J] |  | upper | 2020 | 0.02338
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | [C, J] |  | upper | 2050 | 0.023357
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 1.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 1.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2015 | 6.19
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2020 | 6.19
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2030 | 6.19
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | ctrl | 2050 | 6.19
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2020 | 5.34
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | lower | 2050 | 5.34
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2020 | 6.22
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A | 1 | upper | 2050 | 6.22
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.0323
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.0323
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.0323
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.0323
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2020 | 0.88
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | lower | 2050 | 0.88
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2020 | 1.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [B, C] | 1 | upper | 2050 | 1.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2015 | 1.0323
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2020 | 1.0323
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2030 | 1.0323
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | ctrl | 2050 | 1.0323
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2020 | 0.88
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | lower | 2050 | 0.88
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2020 | 1.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [B, C] | 1 | upper | 2050 | 1.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 4
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 4
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 4
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 4
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 3.4
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 3
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 4.6
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 5
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.24
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.24
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.24
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.24
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.21
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.18
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.28
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.3
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 20
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 35
09c Straw HOP | Biomass boiler - boiler - straw - small | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2015 | 16
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2020 | 11
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2030 | 8
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2050 | 4
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2020 | 4
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2050 | 2
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2020 | 16
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2050 | 16
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2015 | 4
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2020 | 3
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2030 | 2
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2050 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2020 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2050 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2020 | 4
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | N2O [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2050 | 4
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2015 | 90
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2020 | 70
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2030 | 70
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2050 | 70
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2020 | 40
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2050 | 20
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2020 | 90
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | NOX [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2050 | 70
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2015 | 2
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2020 | 0.3
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2030 | 0.3
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | ctrl | 2050 | 0.3
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2020 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | lower | 2050 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2020 | 2
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | Particles [g/GJ_i] | g/GJ_i |  | G | 1 | upper | 2050 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2015 | 0.9545
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2020 | 0.9636
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2030 | 0.9909
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | ctrl | 2050 | 0.99818
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2020 | 0.909
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | lower | 2050 | 0.9545
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2020 | 0.99818
09c Straw HOP | Biomass boiler - boiler - straw - small | Environment | SO2 (degree of desulphuring) [] |  |  | G | 1 | upper | 2050 | 0.99909
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2015 | 55614.3932
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2020 | 54019.3341
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2030 | 50935.5532
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2050 | 45618.6896
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | lower | 2020 | 46150.376
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | lower | 2050 | 34878.6252
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | upper | 2020 | 63377.014
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | upper | 2050 | 59229.8604
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2015 | 0.95704
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2020 | 0.93577
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2030 | 0.8826
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2050 | 0.79753
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | lower | 2020 | 0.80816
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | lower | 2050 | 0.65929
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | upper | 2020 | 1.1484
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | upper | 2050 | 1.1591
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2015 | 0.46788
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2020 | 0.45725
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2030 | 0.42535
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2050 | 0.39345
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | lower | 2020 | 0.39345
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | lower | 2050 | 0.31901
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | upper | 2020 | 0.58485
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | upper | 2050 | 0.58485
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2015 | 0.48915
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2020 | 0.47852
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2030 | 0.45725
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | ctrl | 2050 | 0.41472
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | lower | 2020 | 0.41472
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | lower | 2050 | 0.34028
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | upper | 2020 | 0.56359
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | [F, K] |  | upper | 2050 | 0.57422
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2015 | 2.1161
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2020 | 2.2437
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2030 | 2.9562
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2050 | 3.3177
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | lower | 2020 | 2.0417
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | lower | 2050 | 3.0412
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | upper | 2020 | 2.7541
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | upper | 2050 | 4.0834
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2015 | 1.4037
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2020 | 1.5419
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2030 | 2.2544
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2050 | 2.6053
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | lower | 2020 | 1.5206
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | lower | 2050 | 2.5734
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | upper | 2020 | 1.8184
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | upper | 2050 | 3.0838
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2015 | 0.71246
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2020 | 0.71246
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2030 | 0.71246
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | ctrl | 2050 | 0.71246
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | lower | 2020 | 0.52105
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | lower | 2050 | 0.45725
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | upper | 2020 | 0.93577
09c Straw HOP | Biomass boiler - boiler - straw - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | [F, L] |  | upper | 2050 | 0.99957
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2015 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2020 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2030 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | ctrl | 2050 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | lower | 2020 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | lower | 2050 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | upper | 2020 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Minimum load (of full load) [] |  |  | E | 1 | upper | 2050 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2015 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2020 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2030 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | ctrl | 2050 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2020 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | lower | 2050 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2020 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | E | 1 | upper | 2050 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2015 | 0.25
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2020 | 0.25
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2030 | 0.25
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | ctrl | 2050 | 0.25
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2020 | 0.25
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | lower | 2050 | 0.25
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2020 | 0.25
09c Straw HOP | Biomass boiler - boiler - straw - small | Regulation ability | Warm start-up time [hours] | hours |  | H | 1 | upper | 2050 | 0.25
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2015 | 0.017669
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2020 | 0.017669
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2030 | 0.017669
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | ctrl | 2050 | 0.017669
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2020 | 0.01
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | lower | 2050 | 0.01
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2020 | 0.15
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | D | 1 | upper | 2050 | 0.15
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Combustion air humidification |  |  | [D, M] |  | ctrl | 2015 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Combustion air humidification |  |  | [D, M] |  | ctrl | 2020 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Combustion air humidification |  |  | [D, M] |  | ctrl | 2030 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Combustion air humidification |  |  | [D, M] |  | ctrl | 2050 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Combustion air humidification |  |  | [D, M] |  | lower | 2020 | 0
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Combustion air humidification |  |  | [D, M] |  | lower | 2050 | 0
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Combustion air humidification |  |  | [D, M] |  | upper | 2020 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Combustion air humidification |  |  | [D, M] |  | upper | 2050 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 57422.1267
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 55720.7304
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 52530.6122
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 47001.0741
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 47639.0977
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 36048.3351
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 65503.7594
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 61143.9313
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Flue gas condensation |  |  | [D, M] |  | ctrl | 2015 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Flue gas condensation |  |  | [D, M] |  | ctrl | 2020 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Flue gas condensation |  |  | [D, M] |  | ctrl | 2030 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Flue gas condensation |  |  | [D, M] |  | ctrl | 2050 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Flue gas condensation |  |  | [D, M] |  | lower | 2020 | 0
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Flue gas condensation |  |  | [D, M] |  | lower | 2050 | 0
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Flue gas condensation |  |  | [D, M] |  | upper | 2020 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Flue gas condensation |  |  | [D, M] |  | upper | 2050 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.08507
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.08507
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.074436
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.074436
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.074436
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.063802
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.095704
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.095704
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [I, K] | 1 | ctrl | 2015 | 0.98894
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [I, K] | 1 | ctrl | 2020 | 0.95704
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [I, K] | 1 | ctrl | 2030 | 0.9145
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [I, K] | 1 | ctrl | 2050 | 0.82943
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [I, K] | 1 | lower | 2020 | 0.84006
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [I, K] | 1 | lower | 2050 | 0.68056
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [I, K] | 1 | upper | 2020 | 1.191
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [I, K] | 1 | upper | 2050 | 1.191
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.47852
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.46788
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.44662
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.40408
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.40408
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.32965
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.60612
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.60612
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.51042
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.48915
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.46788
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.42535
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.43598
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.35091
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.58485
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.58485
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, L] |  | ctrl | 2015 | 0.09
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, L] |  | ctrl | 2020 | 0.09
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, L] |  | ctrl | 2030 | 0.09
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, L] |  | ctrl | 2050 | 0.09
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, L] |  | lower | 2020 | 0
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, L] |  | lower | 2050 | 0
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, L] |  | upper | 2020 | 0.09
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Output of recovered condensate [t/MWh_i] | t/MWh_i |  | [D, L] |  | upper | 2050 | 0.09
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 2.1799
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 2.3182
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 3.0519
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 3.4241
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 2.1161
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 3.1476
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 2.4458
09c Straw HOP | Biomass boiler - boiler - straw - small | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 3.6367
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2015 | 0.44
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2020 | 0.45
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2030 | 0.42
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2050 | 0.4
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2020 | 0.42
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2050 | 0.43
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2020 | 0.41
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2050 | 0.44
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  |  | ctrl | 2015 | 0.14
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  |  | ctrl | 2020 | 0.14
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  |  | ctrl | 2030 | 0.14
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  |  | ctrl | 2050 | 0.13
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  |  | lower | 2020 | 0.13
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  |  | lower | 2050 | 0.13
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  |  | upper | 2020 | 0.13
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  |  |  | upper | 2050 | 0.14
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.408
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.409
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.41
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.394
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.378
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.385
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.41
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.414
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.43
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.43
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.432
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.414
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.398
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.404
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.431
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.436
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 257.7
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 258.2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 259.7
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 248.6
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 238.8
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 242.6
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 258.6
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 261.3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.6
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.8
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2015 | 0.06
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2020 | 0.06
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2030 | 0.06
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2050 | 0.06
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2020 | 0.06
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2050 | 0.06
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2020 | 0.06
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2050 | 0.06
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 25
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 25
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 25
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 25
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 10
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 8
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 6
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 10
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 10
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 30
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 20
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 20
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 10
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 10
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 10
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 30
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 20
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 0.3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 0.3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 0.3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 0.3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 0.1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0.1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | Particles [g/GJ_i] | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2015 | 0.975
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2020 | 0.975
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2030 | 0.975
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | ctrl | 2050 | 0.975
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | lower | 2020 | 0.975
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | lower | 2050 | 0.975
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | upper | 2020 | 0.975
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Environment | SO2 (degree of desulphuring) [] |  |  | F | [1, 2, 3] | upper | 2050 | 0.975
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 74436.0903
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 73372.7175
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 68055.854
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 65929.1085
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 70182.5994
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 60612.2449
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 85069.8174
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 84006.4447
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 2.7648
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 2.6584
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 2.5521
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 2.4458
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 2.5521
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 2.3394
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 3.2965
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 3.5091
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.7014
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.7014
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.5951
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 1.4887
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.5951
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 1.4887
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 2.0204
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 2.2331
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.0634
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 0.95704
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 0.95704
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 0.8507
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 0.8507
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.8507
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.1697
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.276
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 2.7648
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 2.7648
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 2.7648
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 2.8711
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 2.9774
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 2.8711
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 2.7648
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 2.6584
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 12
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 12
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 12
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 12
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2020 | 12
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | lower | 2050 | 12
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2020 | 12
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | upper | 2050 | 12
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.45
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.45
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.45
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.45
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2020 | 0.45
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2050 | 0.45
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2020 | 0.45
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2050 | 0.45
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2015 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2020 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2030 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | ctrl | 2050 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | lower | 2020 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | lower | 2050 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | upper | 2020 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Regulation ability | Warm start-up time [hours] | hours |  | [E, G] | 1 | upper | 2050 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2015 | 0.041
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2020 | 0.041
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2030 | 0.041
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.041
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2020 | 0.041
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | lower | 2050 | 0.041
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.041
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.041
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Combustion air humidification |  |  | M |  | ctrl | 2015 | 0
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Combustion air humidification |  |  | M |  | ctrl | 2020 | 0
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Combustion air humidification |  |  | M |  | ctrl | 2030 | 0
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Combustion air humidification |  |  | M |  | ctrl | 2050 | 0
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Combustion air humidification |  |  | M |  | lower | 2020 | 0
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Combustion air humidification |  |  | M |  | lower | 2050 | 0
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Combustion air humidification |  |  | M |  | upper | 2020 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Combustion air humidification |  |  | M |  | upper | 2050 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 32113.8561
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 31369.4952
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 29668.0988
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 27116.0043
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 28073.0397
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 24670.247
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 36580.0215
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 36367.3469
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Flue gas condensation |  |  | M |  | ctrl | 2015 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Flue gas condensation |  |  | M |  | ctrl | 2020 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Flue gas condensation |  |  | M |  | ctrl | 2030 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Flue gas condensation |  |  | M |  | ctrl | 2050 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Flue gas condensation |  |  | M |  | lower | 2020 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Flue gas condensation |  |  | M |  | lower | 2050 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Flue gas condensation |  |  | M |  | upper | 2020 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Flue gas condensation |  |  | M |  | upper | 2050 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0.021267
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0.021267
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0.021267
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0.021267
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0.021267
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0.021267
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0.021267
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0.021267
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.1697
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 1.1484
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 1.0846
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.99957
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.99957
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.93577
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.4037
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.5313
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.73373
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.71246
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.66992
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.62739
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.62739
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.58485
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.89323
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.9783
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.44662
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.43598
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.42535
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.38281
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.37218
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.35091
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.51042
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.55295
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 1.1803
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 1.1803
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 1.1803
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 1.1803
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 1.1803
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 1.1803
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 1.1803
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 1.1803
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2015 | 0.59
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2020 | 0.59
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2030 | 0.59
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | ctrl | 2050 | 0.52
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2020 | 0.57
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | lower | 2050 | 0.59
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2020 | 0.52
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cb coefficient (50°C/100°C) |  |  |  |  | upper | 2050 | 0.53
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2015 | 5
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2020 | 5
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 5
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 5
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2020 | 5
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2020 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2015 | 0.17
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2020 | 0.17
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2030 | 0.17
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | ctrl | 2050 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | lower | 2020 | 0.17
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | lower | 2050 | 0.17
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | upper | 2020 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Cv coefficient (50°C/100°C) |  |  | I |  | upper | 2050 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.423
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.425
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.426
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.426
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2020 | 0.412
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | lower | 2050 | 0.418
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2020 | 0.427
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | [A, H] | 1 | upper | 2050 | 0.433
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2015 | 0.445
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2020 | 0.447
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2030 | 0.448
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | ctrl | 2050 | 0.448
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2020 | 0.434
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | lower | 2050 | 0.44
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2020 | 0.449
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [A, H] | 1 | upper | 2050 | 0.455
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.03
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.03
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.03
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.03
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 356.4
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 357.6
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 358.7
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 358.4
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2020 | 347.3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | lower | 2050 | 351.7
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2020 | 359.4
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | upper | 2050 | 364.4
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 2.6
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 2.3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 3.5
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 3.8
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2015 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2020 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2020 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2020 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 25
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 25
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2020 | 25
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 25
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2020 | 25
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 25
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2015 | 20
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2020 | 20
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2030 | 20
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2050 | 10
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | lower | 2020 | 10
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | lower | 2050 | 10
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | upper | 2020 | 30
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | NOX [g/GJ_i] | g/GJ_i |  | [C, F] | [1, 2] | upper | 2050 | 20
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 0.3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 0.3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 0.3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0.3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0.1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0.1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2015 | 0.975
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2020 | 0.975
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2030 | 0.975
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | ctrl | 2050 | 0.975
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | lower | 2020 | 0.975
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | lower | 2050 | 0.975
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | upper | 2020 | 0.975
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Environment | SO2 (degree of desulphuring) [] |  |  |  | [1, 2] | upper | 2050 | 0.975
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 60612.2449
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 58485.4995
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 55295.3813
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 52105.2632
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 54232.0086
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 48915.145
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 66992.4812
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 66992.4812
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2015 | 2.3607
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2020 | 2.2863
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2030 | 2.1693
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | ctrl | 2050 | 2.0204
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2020 | 2.0523
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | lower | 2050 | 1.9141
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2020 | 2.7541
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [J, K] | 1 | upper | 2050 | 2.9562
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 1.4249
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 1.3824
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 1.3079
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 1.2335
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 1.2335
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 1.1484
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.6801
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.8077
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2015 | 0.93577
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2020 | 0.9145
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2030 | 0.86133
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | ctrl | 2050 | 0.7869
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2020 | 0.8188
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | lower | 2050 | 0.75499
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2020 | 1.0634
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | K |  | upper | 2050 | 1.1484
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2015 | 1.1697
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2020 | 1.1697
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2030 | 1.1697
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | ctrl | 2050 | 1.1697
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2020 | 1.276
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | lower | 2050 | 1.276
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2020 | 1.1697
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | L |  | upper | 2050 | 1.1697
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2015 | 12
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2020 | 12
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2030 | 12
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | ctrl | 2050 | 12
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | lower | 2020 | 12
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | lower | 2050 | 12
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | upper | 2020 | 12
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Cold start-up time [hours] | hours |  | E | 1 | upper | 2050 | 12
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2015 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2020 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2030 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | ctrl | 2050 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2020 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | lower | 2050 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2020 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Minimum load (of full load) [] |  |  |  | 1 | upper | 2050 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0.02
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0.02
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.02
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.02
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 0.02
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0.02
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 0.02
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0.02
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2015 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2020 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2030 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | ctrl | 2050 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2020 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | lower | 2050 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2020 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | D | 1 | upper | 2050 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2015 | 2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2020 | 2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2030 | 2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | ctrl | 2050 | 2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2020 | 2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | lower | 2050 | 2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2020 | 2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Regulation ability | Warm start-up time [hours] | hours |  | G | 1 | upper | 2050 | 2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | ctrl | 2050 | 0.036
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2020 | 0.036
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] |  |  | C | 1 | upper | 2050 | 0.036
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | M |  | ctrl | 2015 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | M |  | ctrl | 2020 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | M |  | ctrl | 2030 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | M |  | ctrl | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | M |  | lower | 2020 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | M |  | lower | 2050 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | M |  | upper | 2020 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Combustion air humidification |  |  | M |  | upper | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2015 | 26796.9925
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2020 | 26158.9689
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2030 | 24989.2589
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | ctrl | 2050 | 23287.8625
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2020 | 23606.8743
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | lower | 2050 | 21267.4544
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2020 | 30093.4479
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fixed O&M (*total) [EUR/MW_i/y] | EUR/MW_i/y | 2020 |  |  | upper | 2050 | 30412.4597
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | M |  | ctrl | 2015 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | M |  | ctrl | 2020 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | M |  | ctrl | 2030 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | M |  | ctrl | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | M |  | lower | 2020 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | M |  | lower | 2050 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | M |  | upper | 2020 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Flue gas condensation |  |  | M |  | upper | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2015 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2020 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2030 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | ctrl | 2050 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2020 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | lower | 2050 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2020 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | MEUR/MW_i/storageday | 2020 | K |  | upper | 2050 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2015 | 1.0527
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2020 | 1.0208
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2030 | 0.9783
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | ctrl | 2050 | 0.90387
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2020 | 0.89323
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | lower | 2050 | 0.84006
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2020 | 1.2335
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (*total) [MEUR/MW_i] | MEUR/MW_i | 2020 | [J, K] | 1 | upper | 2050 | 1.3398
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.62739
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.61676
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.58485
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.55295
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.54232
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.51042
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.75499
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (equipment) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.8188
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2015 | 0.41472
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2020 | 0.40408
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2030 | 0.38281
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | ctrl | 2050 | 0.35091
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2020 | 0.35091
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | lower | 2050 | 0.32965
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2020 | 0.47852
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Nominal investment (installation) [MEUR/MW_i] | MEUR/MW_i | 2020 | K |  | upper | 2050 | 0.52105
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2015 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2020 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2030 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | ctrl | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2020 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | lower | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2020 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Steam reheat |  |  | M |  | upper | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2015 | 0.54232
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2020 | 0.54232
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2030 | 0.54232
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | ctrl | 2050 | 0.54232
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2020 | 0.54232
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | lower | 2050 | 0.54232
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2020 | 0.54232
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Technology-specific data | Variable O&M (*total) [EUR/MWh_i] | EUR/MWh_i | 2020 | L |  | upper | 2050 | 0.54232
10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Construction time [years] | years |  | B | 1 | ctrl | 2015 | 0.4
10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Construction time [years] | years |  | B | 1 | ctrl | 2020 | 0.3
10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | 1 | ctrl | 2015 | 0.2
10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | 1 | ctrl | 2020 | 0.22
10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2015 | 0.04
10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Forced outage [] |  |  |  | 1 | ctrl | 2020 | 0.03
10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  | 1 | ctrl | 2015 | 0.04
10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  | 1 | ctrl | 2020 | 0.04
10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | ctrl | 2015 | 3
10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | ctrl | 2020 | 2
10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2015 | 15
10 Stirling | Stirling engine - back pressure - biomass - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2020 | 15
10 Stirling | Stirling engine - back pressure - biomass - medium | Environment | CH4 [ppm] | ppm |  |  | 1 | ctrl | 2015 | 0
10 Stirling | Stirling engine - back pressure - biomass - medium | Environment | CH4 [ppm] | ppm |  |  | 1 | ctrl | 2020 | 0
10 Stirling | Stirling engine - back pressure - biomass - medium | Environment | N2O [ppm] | ppm |  |  | 1 | ctrl | 2015 | 0
10 Stirling | Stirling engine - back pressure - biomass - medium | Environment | N2O [ppm] | ppm |  |  | 1 | ctrl | 2020 | 0
10 Stirling | Stirling engine - back pressure - biomass - medium | Environment | NOX [ppm] | ppm |  |  | 1 | ctrl | 2015 | 130
10 Stirling | Stirling engine - back pressure - biomass - medium | Environment | NOX [ppm] | ppm |  |  | 1 | ctrl | 2020 | 100
10 Stirling | Stirling engine - back pressure - biomass - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  | 1 | ctrl | 2015 | 0
10 Stirling | Stirling engine - back pressure - biomass - medium | Environment | SO2 (degree of desulphuring) [] |  |  |  | 1 | ctrl | 2020 | 0
10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [D, E] | 1 | ctrl | 2015 | 34027.927
10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [D, E] | 1 | ctrl | 2020 | 34027.927
10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [D, E] | 1 | ctrl | 2030 | 0
10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [D, E] | 1 | ctrl | 2050 | 0
10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 1 | ctrl | 2015 | 5.3169
10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 1 | ctrl | 2020 | 4.0408
10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 1 | ctrl | 2030 | 0
10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, E] | 1 | ctrl | 2050 | 0
10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [D, E] | 1 | ctrl | 2015 | 27.6477
10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [D, E] | 1 | ctrl | 2020 | 22.3308
10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [D, E] | 1 | ctrl | 2030 | 0
10 Stirling | Stirling engine - back pressure - biomass - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | [D, E] | 1 | ctrl | 2050 | 0
10 Stirling | Stirling engine - back pressure - biomass - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2015 | 1
10 Stirling | Stirling engine - back pressure - biomass - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2020 | 1
10 Stirling | Stirling engine - back pressure - biomass - medium | Technology-specific data | Generating capacity for one unit [MW_h] | MW_h |  |  | 1 | ctrl | 2015 | 0.12
10 Stirling | Stirling engine - back pressure - biomass - medium | Technology-specific data | Generating capacity for one unit [MW_h] | MW_h |  |  | 1 | ctrl | 2020 | 0.12
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [C, L] | [, *, *, *] | ctrl | 2020 | 1.67
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [C, L] | [, *, *, *] | ctrl | 2030 | 1.61
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | [C, L] | [, *, *, *] | ctrl | 2050 | 1.61
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2015 | 1
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 1
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 1
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 1
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | B | [3, *, *, *] | ctrl | 2015 | 0.56
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | B | [3, *, *, *] | ctrl | 2020 | 0.58
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | B | [3, *, *, *] | ctrl | 2030 | 0.6
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | B | [3, *, *, *] | ctrl | 2050 | 0.6
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | B | [3, *, *, *] | lower | 2020 | 0.52
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | B | [3, *, *, *] | lower | 2050 | 0.56
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | B | [3, *, *, *] | upper | 2020 | 0.6
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | B | [3, *, *, *] | upper | 2050 | 0.62
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  |  | ctrl | 2015 | 0.56
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  |  | ctrl | 2020 | 0.58
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  |  | ctrl | 2030 | 0.6
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  |  | ctrl | 2050 | 0.6
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | [3, *, *, *] | ctrl | 2015 | 0.25
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | [3, *, *, *] | ctrl | 2020 | 2.5
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | [3, *, *, *] | ctrl | 2030 | 10
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | [3, *, *, *] | ctrl | 2050 | 20
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [6, 6, *, *] | ctrl | 2015 | 15
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [6, 6, *, *] | ctrl | 2020 | 20
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [6, 6, *, *] | ctrl | 2030 | 20
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Energy/technical data | Technical lifetime [years] | years |  | D | [6, 6, *, *] | ctrl | 2050 | 20
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 7 | ctrl | 2015 | 1.25
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 7 | ctrl | 2020 | 1.25
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 7 | ctrl | 2030 | 1.25
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 7 | ctrl | 2050 | 1.25
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2015 | 1.3
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2020 | 1.4
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2030 | 1.5
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 3 | ctrl | 2050 | 1.6
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 3 | ctrl | 2015 | 1
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 3 | ctrl | 2020 | 1
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 3 | ctrl | 2030 | 1
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Environment | SO2 (degree of desulphuring) [] |  |  |  | 3 | ctrl | 2050 | 1
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | K | 8 | ctrl | 2015 | 441299.678
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | K | 8 | ctrl | 2020 | 175456.4985
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | K | 8 | ctrl | 2030 | 106337.2718
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | K | 8 | ctrl | 2050 | 42534.9087
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | K | 8 | lower | 2020 | 143555.3169
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | K | 8 | lower | 2050 | 21267.4544
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | K | 8 | upper | 2020 | 308378.0882
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | K | 8 | upper | 2050 | 69119.2267
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [G, H, I, J] | [8, 13] | ctrl | 2015 | 8.826
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [G, H, I, J] | [8, 13] | ctrl | 2020 | 3.5091
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [G, H, I, J] | [8, 13] | ctrl | 2030 | 2.1267
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [G, H, I, J] | [8, 13] | ctrl | 2050 | 0.8507
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [G, H, I, J] | [8, 13] | lower | 2020 | 2.8711
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [G, H, I, J] | [8, 13] | lower | 2050 | 0.42535
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [G, H, I, J] | [8, 13] | upper | 2020 | 6.1676
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [G, H, I, J] | [8, 13] | upper | 2050 | 1.3824
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2015 | 7.0608
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2020 | 2.4564
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2030 | 1.276
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2050 | 0.48915
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2020 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2050 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2020 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2050 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2015 | 1.7652
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2020 | 1.0527
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2030 | 0.8507
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | ctrl | 2050 | 0.36155
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2020 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | lower | 2050 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2020 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | G |  | upper | 2050 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | ctrl | 2015 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | ctrl | 2020 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | ctrl | 2030 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | ctrl | 2050 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | lower | 2020 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | lower | 2050 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | upper | 2020 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | upper | 2050 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2015 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2020 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2030 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2050 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | lower | 2020 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | lower | 2050 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | upper | 2020 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | upper | 2050 | 0
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [*, *, *, *] | ctrl | 2015 | 25
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [*, *, *, *] | ctrl | 2020 | 25
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [*, *, *, *] | ctrl | 2030 | 25
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Cold start-up time [hours] | hours |  | E | [*, *, *, *] | ctrl | 2050 | 25
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.7
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.7
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.7
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.7
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | E |  | ctrl | 2015 | 0.03
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | E |  | ctrl | 2020 | 0.03
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | E |  | ctrl | 2030 | 0.03
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Regulation ability | Warm start-up time [hours] | hours |  | E |  | ctrl | 2050 | 0.03
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | D |  | ctrl | 2020 | 1.25
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | D |  | ctrl | 2030 | 1.25
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Cb coefficient (50°C/100°C) |  |  | D |  | ctrl | 2050 | 1.25
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2015 | 1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 5] | ctrl | 2015 | 0.45
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 5] | ctrl | 2020 | 0.5
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 5] | ctrl | 2030 | 0.5
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 5] | ctrl | 2050 | 0.5
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 5] | lower | 2020 | 0.45
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 5] | lower | 2050 | 0.46
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 5] | upper | 2020 | 0.52
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | [3, 5] | upper | 2050 | 0.53
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2015 | 0.45
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2020 | 0.5
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2030 | 0.5
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | 5 | ctrl | 2050 | 0.5
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.001
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.001
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.001
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.001
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  | 5 | ctrl | 2015 | 0.05
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  | 5 | ctrl | 2020 | 0.1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  | 5 | ctrl | 2030 | 1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  | 5 | ctrl | 2050 | 2
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 0.1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 0.1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 0.1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2015 | 10
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2020 | 10
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2030 | 10
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2050 | 10
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2015 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2015 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2015 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2015 | 1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2020 | 1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2030 | 1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Environment | SO2 (degree of desulphuring) [] |  |  |  |  | ctrl | 2050 | 1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | C |  | ctrl | 2015 | 101020.4082
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | C |  | ctrl | 2020 | 69119.2267
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | C |  | ctrl | 2030 | 58485.4995
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | C |  | ctrl | 2050 | 42534.9087
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | C |  | lower | 2020 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | C |  | lower | 2050 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | C |  | upper | 2020 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | C |  | upper | 2050 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | B | [3, 4] | ctrl | 2015 | 2.0204
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | B | [3, 4] | ctrl | 2020 | 1.3824
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | B | [3, 4] | ctrl | 2030 | 1.1697
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | B | [3, 4] | ctrl | 2050 | 0.8507
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | B | [3, 4] | lower | 2020 | 1.1697
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | B | [3, 4] | lower | 2050 | 0.53169
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | B | [3, 4] | upper | 2020 | 1.7014
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | B | [3, 4] | upper | 2050 | 0.95704
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | ctrl | 2015 | 1.7014
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | ctrl | 2020 | 1.0634
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | ctrl | 2030 | 0.8507
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | ctrl | 2050 | 0.63802
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | lower | 2020 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | lower | 2050 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | upper | 2020 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | upper | 2050 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | ctrl | 2015 | 0.31901
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | ctrl | 2020 | 0.31901
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | ctrl | 2030 | 0.31901
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | ctrl | 2050 | 0.21267
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | lower | 2020 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | lower | 2050 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | upper | 2020 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 4 | upper | 2050 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2015 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2020 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2030 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2050 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | lower | 2020 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | lower | 2050 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | upper | 2020 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | upper | 2050 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 0.5
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 0.25
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.025
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.0125
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2015 | 0.01
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0.01
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0.01
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0.01
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Technology-specific data | Minimum load efficiency [] |  |  |  | 5 | ctrl | 2015 | 0.3
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Technology-specific data | Minimum load efficiency [] |  |  |  | 5 | ctrl | 2020 | 0.35
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Technology-specific data | Minimum load efficiency [] |  |  |  | 5 | ctrl | 2030 | 0.35
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Technology-specific data | Minimum load efficiency [] |  |  |  | 5 | ctrl | 2050 | 0.35
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | E | 4 | ctrl | 2015 | 1.5
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | E | 4 | ctrl | 2020 | 1.5
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | E | 4 | ctrl | 2030 | 1.5
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | E | 4 | ctrl | 2040 | 1.5
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | E | 4 | ctrl | 2050 | 1.5
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | E | 4 | lower | 2020 | 1
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | E | 4 | lower | 2050 | 1
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | E | 4 | upper | 2020 | 3
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | E | 4 | upper | 2050 | 3
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B | 4 | ctrl | 2015 | 0.03
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B | 4 | ctrl | 2020 | 0.025
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B | 4 | ctrl | 2030 | 0.02
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B | 4 | ctrl | 2040 | 0.018
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B | 4 | ctrl | 2050 | 0.015
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B | 4 | lower | 2020 | 0.01
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B | 4 | lower | 2050 | 0.01
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B | 4 | upper | 2020 | 0.05
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B | 4 | upper | 2050 | 0.05
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A1 | 3 | ctrl | 2015 | 3.1
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A1 | 3 | ctrl | 2020 | 4.2
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A1 | 3 | ctrl | 2030 | 5
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A1 | 3 | ctrl | 2040 | 5.5
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A1 | 3 | ctrl | 2050 | 6
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A1 | 3 | lower | 2020 | 2
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A1 | 3 | lower | 2050 | 1.5
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A1 | 3 | upper | 2020 | 6
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A1 | 3 | upper | 2050 | 8
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 4 | ctrl | 2015 | 0.16
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 4 | ctrl | 2020 | 0.16
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 4 | ctrl | 2030 | 0.16
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 4 | ctrl | 2040 | 0.16
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 4 | ctrl | 2050 | 0.16
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 4 | lower | 2020 | 0.05
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 4 | lower | 2050 | 0.05
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 4 | upper | 2020 | 0.26
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 4 | upper | 2050 | 0.26
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | D | 14 | ctrl | 2015 | 25
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | D | 14 | ctrl | 2020 | 27
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | D | 14 | ctrl | 2030 | 30
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | D | 14 | ctrl | 2040 | 30
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | D | 14 | ctrl | 2050 | 30
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | D | 14 | lower | 2020 | 25
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | D | 14 | lower | 2050 | 25
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | D | 14 | upper | 2020 | 35
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | D | 14 | upper | 2050 | 40
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | I | [25, 26] | ctrl | 2015 | 27222.3416
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | I | [25, 26] | ctrl | 2020 | 14887.2181
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | I | [25, 26] | ctrl | 2030 | 13398.4962
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | I | [25, 26] | ctrl | 2040 | 12326.6165
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | I | [25, 26] | ctrl | 2050 | 12058.6466
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | I | [25, 26] | lower | 2020 | 11909.7744
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | I | [25, 26] | lower | 2050 | 9646.9173
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | I | [25, 26] | upper | 2020 | 17864.6617
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | I | [25, 26] | upper | 2050 | 14470.3759
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | [16, 2, 4] | ctrl | 2015 | 1.4143
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | [16, 2, 4] | ctrl | 2020 | 1.191
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | [16, 2, 4] | ctrl | 2030 | 1.1059
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | [16, 2, 4] | ctrl | 2040 | 1.0421
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | [16, 2, 4] | ctrl | 2050 | 1.0208
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | [16, 2, 4] | lower | 2020 | 0.8188
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | [16, 2, 4] | lower | 2050 | 0.8507
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | [16, 2, 4] | upper | 2020 | 1.2335
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | [16, 2, 4] | upper | 2050 | 1.2654
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2015 | 0.042535
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2020 | 0.042535
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2030 | 0.042535
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2040 | 0.042535
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2050 | 0.042535
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | lower | 2020 | 0.031901
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | lower | 2050 | 0.031901
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | upper | 2020 | 0.042535
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | upper | 2050 | 0.042535
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2015 | 0.9464
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2020 | 0.75499
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2030 | 0.68056
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2040 | 0.62739
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2050 | 0.61676
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | lower | 2020 | 0.60612
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | lower | 2050 | 0.48915
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | upper | 2020 | 0.9145
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | upper | 2050 | 0.73373
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2015 | 0.063802
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2020 | 0.053169
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2030 | 0.053169
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2040 | 0.053169
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2050 | 0.053169
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | lower | 2020 | 0.042535
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | lower | 2050 | 0.042535
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | upper | 2020 | 0.063802
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | upper | 2050 | 0.063802
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 25 | ctrl | 2015 | 0.1276
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 25 | ctrl | 2020 | 0.095704
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 25 | ctrl | 2030 | 0.08507
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 25 | ctrl | 2040 | 0.08507
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 25 | ctrl | 2050 | 0.074436
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 25 | lower | 2020 | 0.074436
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 25 | lower | 2050 | 0.063802
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 25 | upper | 2020 | 0.11697
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | M | 25 | upper | 2050 | 0.095704
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (land rent) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2015 | 0.095704
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (land rent) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2020 | 0.095704
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (land rent) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2030 | 0.095704
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (land rent) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2040 | 0.095704
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (land rent) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | ctrl | 2050 | 0.095704
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (land rent) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | lower | 2020 | 0.074436
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (land rent) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | lower | 2050 | 0.074436
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (land rent) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | upper | 2020 | 0.10634
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (land rent) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 25 | upper | 2050 | 0.10634
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (other, i.e. compensation of neighbours) [MEUR/MW_e] | MEUR/MW_e | 2020 | I | [25, 26] | ctrl | 2015 | 0.13824
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (other, i.e. compensation of neighbours) [MEUR/MW_e] | MEUR/MW_e | 2020 | I | [25, 26] | ctrl | 2020 | 0.14887
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (other, i.e. compensation of neighbours) [MEUR/MW_e] | MEUR/MW_e | 2020 | I | [25, 26] | ctrl | 2030 | 0.14887
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (other, i.e. compensation of neighbours) [MEUR/MW_e] | MEUR/MW_e | 2020 | I | [25, 26] | ctrl | 2040 | 0.14887
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (other, i.e. compensation of neighbours) [MEUR/MW_e] | MEUR/MW_e | 2020 | I | [25, 26] | ctrl | 2050 | 0.14887
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (other, i.e. compensation of neighbours) [MEUR/MW_e] | MEUR/MW_e | 2020 | I | [25, 26] | lower | 2020 | 0.11697
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (other, i.e. compensation of neighbours) [MEUR/MW_e] | MEUR/MW_e | 2020 | I | [25, 26] | lower | 2050 | 0.11697
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (other, i.e. compensation of neighbours) [MEUR/MW_e] | MEUR/MW_e | 2020 | I | [25, 26] | upper | 2020 | 0.18077
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Nominal investment (other, i.e. compensation of neighbours) [MEUR/MW_e] | MEUR/MW_e | 2020 | I | [25, 26] | upper | 2050 | 0.18077
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 |  |  | ctrl | 2015 | 2.9774
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 |  |  | ctrl | 2020 | 1.5951
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 |  |  | ctrl | 2030 | 1.4356
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 |  |  | ctrl | 2040 | 1.3186
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 |  |  | ctrl | 2050 | 1.2973
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 |  |  | lower | 2020 | 1.276
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 |  |  | lower | 2050 | 1.0315
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 |  |  | upper | 2020 | 1.9141
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 |  |  | upper | 2050 | 1.5525
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Availability [] |  |  |  |  | ctrl | 2015 | 0.967
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Availability [] |  |  |  |  | ctrl | 2020 | 0.972
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Availability [] |  |  |  |  | ctrl | 2030 | 0.977
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Availability [] |  |  |  |  | ctrl | 2040 | 0.977
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Availability [] |  |  |  |  | ctrl | 2050 | 0.982
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Availability [] |  |  |  |  | lower | 2020 | 0.989
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Availability [] |  |  |  |  | lower | 2050 | 0.989
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Availability [] |  |  |  |  | upper | 2020 | 0.945
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Availability [] |  |  |  |  | upper | 2050 | 0.945
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, L] | 3 | ctrl | 2015 | 3100
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, L] | 3 | ctrl | 2020 | 3400
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, L] | 3 | ctrl | 2030 | 3600
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, L] | 3 | ctrl | 2040 | 3700
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, L] | 3 | ctrl | 2050 | 3800
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, L] | 3 | lower | 2020 | 2000
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, L] | 3 | lower | 2050 | 2000
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, L] | 3 | upper | 2020 | 4000
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, L] | 3 | upper | 2050 | 4500
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average capacity factor [] |  |  |  | [4, 26] | ctrl | 2015 | 0.35388
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average capacity factor [] |  |  |  | [4, 26] | ctrl | 2020 | 0.38813
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average capacity factor [] |  |  |  | [4, 26] | ctrl | 2030 | 0.41096
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average capacity factor [] |  |  |  | [4, 26] | ctrl | 2040 | 0.42237
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average capacity factor [] |  |  |  | [4, 26] | ctrl | 2050 | 0.43379
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average capacity factor [] |  |  |  | [4, 26] | lower | 2020 | 0.22831
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average capacity factor [] |  |  |  | [4, 26] | lower | 2050 | 0.22831
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average capacity factor [] |  |  |  | [4, 26] | upper | 2020 | 0.45662
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Average capacity factor [] |  |  |  | [4, 26] | upper | 2050 | 0.5137
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | [4, 26] | ctrl | 2015 | 85
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | [4, 26] | ctrl | 2020 | 85
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | [4, 26] | ctrl | 2030 | 100
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | [4, 26] | ctrl | 2040 | 105
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | [4, 26] | ctrl | 2050 | 110
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | [4, 26] | lower | 2020 | 85
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | [4, 26] | lower | 2050 | 85
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | [4, 26] | upper | 2020 | 120
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | [4, 26] | upper | 2050 | 150
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  | K | [4, 26] | ctrl | 2015 | 106
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  | K | [4, 26] | ctrl | 2020 | 130
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  | K | [4, 26] | ctrl | 2030 | 145
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  | K | [4, 26] | ctrl | 2040 | 155
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  | K | [4, 26] | ctrl | 2050 | 165
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  | K | [4, 26] | lower | 2020 | 90
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  | K | [4, 26] | lower | 2050 | 100
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  | K | [4, 26] | upper | 2020 | 130
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  | K | [4, 26] | upper | 2050 | 150
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  |  |  | ctrl | 2015 | 351.29
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  |  |  | ctrl | 2020 | 316.43
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  |  |  | ctrl | 2030 | 302.79
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  |  |  | ctrl | 2040 | 291.48
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  |  |  | ctrl | 2050 | 280.6
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  |  |  | lower | 2020 | 314.38
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  |  |  | lower | 2050 | 190.99
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  |  |  | upper | 2020 | 452.04
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  |  |  | upper | 2050 | 452.71
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2015 | 1
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 1
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 1
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 1
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Construction time [years] | years |  |  |  | lower | 2020 | 0.5
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Construction time [years] | years |  |  |  | lower | 2050 | 0.5
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Construction time [years] | years |  |  |  | upper | 2020 | 1.5
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Construction time [years] | years |  |  |  | upper | 2050 | 1.5
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.03
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.03
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.03
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.03
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.02
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.02
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.1
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.1
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2015 | 0.01
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2020 | 0.01
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2030 | 0.01
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2050 | 0.01
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2020 | 0
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2050 | 0
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2020 | 0.03
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2050 | 0.03
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2015 | 0.16
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2020 | 0.16
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2030 | 0.16
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2050 | 0.16
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | lower | 2020 | 0.05
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | lower | 2050 | 0.05
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | upper | 2020 | 0.26
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | upper | 2050 | 0.26
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | C |  | ctrl | 2015 | 0.8
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | C |  | ctrl | 2020 | 0.8
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | C |  | ctrl | 2030 | 0.8
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | C |  | ctrl | 2050 | 0.8
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2015 | 20
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2020 | 20
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2030 | 20
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2050 | 20
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | G |  | ctrl | 2015 | 106337.2718
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | G |  | ctrl | 2020 | 101020.4082
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | G |  | ctrl | 2030 | 95703.5446
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | G |  | ctrl | 2050 | 90386.681
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | G |  | lower | 2020 | 0
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | G |  | lower | 2050 | 0
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | G |  | upper | 2020 | 0
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | G |  | upper | 2050 | 0
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2015 | 4.2535
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2020 | 4.0408
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2030 | 3.8388
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2050 | 3.6474
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | lower | 2020 | 3.1901
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | lower | 2050 | 3.1901
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | upper | 2020 | 6.3802
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | upper | 2050 | 6.3802
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2015 | 0.95704
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2020 | 0.95704
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2030 | 0.95704
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2050 | 0.95704
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | lower | 2020 | 0.90387
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | lower | 2050 | 0.90387
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | upper | 2020 | 1.0102
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | upper | 2050 | 1.0102
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2015 | 0.10634
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2020 | 0.10634
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2030 | 0.10634
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | ctrl | 2050 | 0.10634
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | lower | 2020 | 0.15951
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | lower | 2050 | 0.15951
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | upper | 2020 | 0.053169
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | [E, F] |  | upper | 2050 | 0.053169
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2015 | 0
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2020 | 0
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2030 | 0
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2050 | 0
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | lower | 2020 | 0
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | lower | 2050 | 0
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | upper | 2020 | 0
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | upper | 2050 | 0
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, J] |  | ctrl | 2015 | 1600
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, J] |  | ctrl | 2020 | 1800
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, J] |  | ctrl | 2030 | 2000
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, J] |  | ctrl | 2050 | 2200
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, J] |  | lower | 2020 | 1000
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, J] |  | lower | 2050 | 1000
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, J] |  | upper | 2020 | 2300
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | [A, J] |  | upper | 2050 | 2300
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Fixed O&M (*total) [EUR/unit/y] | EUR/unit/y | 2020 | [E, F] |  | ctrl | 2015 | 540
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Fixed O&M (*total) [EUR/unit/y] | EUR/unit/y | 2020 | [E, F] |  | ctrl | 2020 | 540
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Fixed O&M (*total) [EUR/unit/y] | EUR/unit/y | 2020 | [E, F] |  | ctrl | 2030 | 540
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Fixed O&M (*total) [EUR/unit/y] | EUR/unit/y | 2020 | [E, F] |  | ctrl | 2050 | 540
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Fixed O&M (*total) [EUR/unit/y] | EUR/unit/y | 2020 | [E, F] |  | lower | 2020 | 350
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Fixed O&M (*total) [EUR/unit/y] | EUR/unit/y | 2020 | [E, F] |  | lower | 2050 | 350
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Fixed O&M (*total) [EUR/unit/y] | EUR/unit/y | 2020 | [E, F] |  | upper | 2020 | 700
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Fixed O&M (*total) [EUR/unit/y] | EUR/unit/y | 2020 | [E, F] |  | upper | 2050 | 700
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Hub height [m] | m |  | H |  | ctrl | 2015 | 18
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Hub height [m] | m |  | H |  | ctrl | 2020 | 18
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Hub height [m] | m |  | H |  | ctrl | 2030 | 18
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Hub height [m] | m |  | H |  | ctrl | 2050 | 18
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Hub height [m] | m |  | H |  | lower | 2020 | 14
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Hub height [m] | m |  | H |  | lower | 2050 | 14
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Hub height [m] | m |  | H |  | upper | 2020 | 18
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Hub height [m] | m |  | H |  | upper | 2050 | 18
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Rotor diameter [m] | m |  | H |  | ctrl | 2015 | 8
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Rotor diameter [m] | m |  | H |  | ctrl | 2020 | 11
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Rotor diameter [m] | m |  | H |  | ctrl | 2030 | 12
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Rotor diameter [m] | m |  | H |  | ctrl | 2050 | 14
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Rotor diameter [m] | m |  | H |  | lower | 2020 | 4
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Rotor diameter [m] | m |  | H |  | lower | 2050 | 4
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Rotor diameter [m] | m |  | H |  | upper | 2020 | 14
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Technology-specific data | Rotor diameter [m] | m |  | H |  | upper | 2050 | 14
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | D |  | ctrl | 2020 | 2.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | D |  | ctrl | 2025 | 2.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | D |  | ctrl | 2030 | 2.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | D |  | ctrl | 2040 | 2.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | D |  | ctrl | 2050 | 2
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | D |  | lower | 2025 | 2
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | D |  | lower | 2050 | 1.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | D |  | upper | 2025 | 3
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | D |  | upper | 2050 | 2.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2020 | 0.019087
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2025 | 0.017588
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2030 | 0.017496
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2040 | 0.017316
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2050 | 0.017139
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B |  | lower | 2025 | 0.017588
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B |  | lower | 2050 | 0.017139
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B |  | upper | 2025 | 0.017588
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B |  | upper | 2050 | 0.017139
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1, 2 | ctrl | 2020 | 8.4
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1, 2 | ctrl | 2025 | 15
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1, 2 | ctrl | 2030 | 20
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1, 2 | ctrl | 2040 | 25
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1, 2 | ctrl | 2050 | 30
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1, 2 | lower | 2025 | 12.75
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1, 2 | lower | 2050 | 22.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1, 2 | upper | 2025 | 17.25
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1, 2 | upper | 2050 | 37.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2020 | 0.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2025 | 0.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2030 | 0.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2040 | 0.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2050 | 0.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | lower | 2025 | 0.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | lower | 2050 | 0.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | upper | 2025 | 0.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | upper | 2050 | 0.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E | 3 | ctrl | 2020 | 165.36
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E | 3 | ctrl | 2025 | 177.36
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E | 3 | ctrl | 2030 | 171.96
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E | 3 | ctrl | 2040 | 169.84
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E | 3 | ctrl | 2050 | 171.26
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E | 3 | lower | 2025 | 150.76
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E | 3 | lower | 2050 | 128.44
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E | 3 | upper | 2025 | 203.96
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E | 3 | upper | 2050 | 214.07
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2020 | 27
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2025 | 30
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2030 | 30
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2040 | 30
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2050 | 30
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | C |  | lower | 2025 | 25
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | C |  | lower | 2050 | 25
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | C |  | upper | 2025 | 35
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | C |  | upper | 2050 | 35
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2020 | 50000
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2025 | 42000
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2030 | 39000
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2040 | 34000
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2050 | 33000
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | H | 3 | lower | 2025 | 35700
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | H | 3 | lower | 2050 | 24750
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | H | 3 | upper | 2025 | 48300
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | H | 3 | upper | 2050 | 49500
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 3 | ctrl | 2020 | 2.12
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 3 | ctrl | 2025 | 1.88
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 3 | ctrl | 2030 | 1.8
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 3 | ctrl | 2040 | 1.68
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 3 | ctrl | 2050 | 1.64
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 3 | lower | 2025 | 1.88
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 3 | lower | 2050 | 1.64
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 3 | upper | 2025 | 1.88
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 3 | upper | 2050 | 1.64
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2020 | 0.03
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2025 | 0.02
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2030 | 0.02
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2040 | 0.01
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2050 | 0.01
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | lower | 2025 | 0.02
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | lower | 2050 | 0.01
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | upper | 2025 | 0.02
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | upper | 2050 | 0.02
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2020 | 0.21
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2025 | 0.21
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2030 | 0.22
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2040 | 0.22
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2050 | 0.21
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 4 | lower | 2025 | 0.18
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 4 | lower | 2050 | 0.16
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 4 | upper | 2025 | 0.25
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 4 | upper | 2050 | 0.32
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2020 | 0.25
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2025 | 0.24
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2030 | 0.24
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2040 | 0.25
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2050 | 0.26
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 5 | lower | 2025 | 0.2
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 5 | lower | 2050 | 0.2
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 5 | upper | 2025 | 0.28
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 5 | upper | 2050 | 0.4
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2020 | 0.54
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2025 | 0.4
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2030 | 0.37
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2040 | 0.33
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2050 | 0.32
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | lower | 2025 | 0.4
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | lower | 2050 | 0.32
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | upper | 2025 | 0.4
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | upper | 2050 | 0.32
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2020 | 0.38
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2025 | 0.31
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2030 | 0.28
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2040 | 0.25
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2050 | 0.23
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 6 | lower | 2025 | 0.26
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 6 | lower | 2050 | 0.17
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 6 | upper | 2025 | 0.36
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 6 | upper | 2050 | 0.34
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2020 | 0.72
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2025 | 0.69
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2030 | 0.67
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2040 | 0.61
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2050 | 0.61
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | lower | 2025 | 0.59
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | lower | 2050 | 0.46
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | upper | 2025 | 0.8
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | upper | 2050 | 0.91
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | H | 3 | ctrl | 2020 | 5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | H | 3 | ctrl | 2025 | 4.17
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | H | 3 | ctrl | 2030 | 3.89
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | H | 3 | ctrl | 2040 | 3.42
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | H | 3 | ctrl | 2050 | 3.25
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | H | 3 | lower | 2025 | 3.55
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | H | 3 | lower | 2050 | 2.44
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | H | 3 | upper | 2025 | 4.8
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | H | 3 | upper | 2050 | 4.88
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | J | 3 | ctrl | 2020 | 4400
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | J | 3 | ctrl | 2025 | 4775
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | J | 3 | ctrl | 2030 | 4800
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | J | 3 | ctrl | 2040 | 4850
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | J | 3 | ctrl | 2050 | 4900
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | J | 3 | lower | 2025 | 4300
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | J | 3 | lower | 2050 | 4050
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | J | 3 | upper | 2025 | 5250
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | J | 3 | upper | 2050 | 5500
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | 1 | ctrl | 2020 | 103.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | 1 | ctrl | 2025 | 138
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | 1 | ctrl | 2030 | 155
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | 1 | ctrl | 2040 | 170
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | 1 | ctrl | 2050 | 185
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | 1 | lower | 2025 | 124.2
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | 1 | lower | 2050 | 157.25
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | 1 | upper | 2025 | 151.8
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | 1 | upper | 2050 | 212.75
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  |  | 1 | ctrl | 2020 | 167
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  |  | 1 | ctrl | 2025 | 236
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  |  | 1 | ctrl | 2030 | 270
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  |  | 1 | ctrl | 2040 | 300
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  |  | 1 | ctrl | 2050 | 330
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  |  | 1 | lower | 2025 | 212.4
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  |  | 1 | lower | 2050 | 280.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  |  | 1 | upper | 2025 | 259.6
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  |  | 1 | upper | 2050 | 379.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | E | 3 | ctrl | 2020 | 6.05
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | E | 3 | ctrl | 2025 | 5.64
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | E | 3 | ctrl | 2030 | 5.82
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | E | 3 | ctrl | 2040 | 5.89
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | E | 3 | ctrl | 2050 | 5.84
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | E | 3 | lower | 2025 | 6.63
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | E | 3 | lower | 2050 | 7.79
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | E | 3 | upper | 2025 | 4.9
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | E | 3 | upper | 2050 | 4.67
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | I | 1 | ctrl | 2020 | 383.49
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | I | 1 | ctrl | 2025 | 342.91
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | I | 1 | ctrl | 2030 | 349.31
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | I | 1 | ctrl | 2040 | 353.68
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | I | 1 | ctrl | 2050 | 350.75
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | I | 1 | lower | 2025 | 359.84
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | I | 1 | lower | 2050 | 364.11
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | I | 1 | upper | 2025 | 325.9
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | I | 1 | upper | 2050 | 331.53
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | D |  | ctrl | 2020 | 2.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | D |  | ctrl | 2025 | 2.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | D |  | ctrl | 2030 | 2.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | D |  | ctrl | 2040 | 2.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | D |  | ctrl | 2050 | 2
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | D |  | lower | 2025 | 2
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | D |  | lower | 2050 | 1.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | D |  | upper | 2025 | 3
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Construction time [years] | years |  | D |  | upper | 2050 | 2.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2020 | 0.020483
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2025 | 0.019417
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2030 | 0.018872
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2040 | 0.018872
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B |  | ctrl | 2050 | 0.018872
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B |  | lower | 2025 | 0.019417
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B |  | lower | 2050 | 0.018872
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B |  | upper | 2025 | 0.019417
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Forced outage [] |  |  | B |  | upper | 2050 | 0.018872
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1, 2 | ctrl | 2020 | 8.4
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1, 2 | ctrl | 2025 | 10
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1, 2 | ctrl | 2030 | 15
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1, 2 | ctrl | 2040 | 15
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1, 2 | ctrl | 2050 | 15
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1, 2 | lower | 2025 | 8.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1, 2 | lower | 2050 | 11.25
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1, 2 | upper | 2025 | 11.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A | 1, 2 | upper | 2050 | 18.75
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2020 | 0.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2025 | 0.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2030 | 0.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2040 | 0.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | ctrl | 2050 | 0.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | lower | 2025 | 0.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | lower | 2050 | 0.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | upper | 2025 | 0.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | B |  | upper | 2050 | 0.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E | 3 | ctrl | 2020 | 32.02
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E | 3 | ctrl | 2025 | 35.18
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E | 3 | ctrl | 2030 | 35.81
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E | 3 | ctrl | 2040 | 35.81
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E | 3 | ctrl | 2050 | 35.81
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E | 3 | lower | 2025 | 29.91
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E | 3 | lower | 2050 | 26.86
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E | 3 | upper | 2025 | 40.46
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | E | 3 | upper | 2050 | 44.76
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2020 | 27
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2025 | 30
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2030 | 30
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2040 | 30
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | C |  | ctrl | 2050 | 30
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | C |  | lower | 2025 | 25
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | C |  | lower | 2050 | 25
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | C |  | upper | 2025 | 35
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Energy/technical data | Technical lifetime [years] | years |  | C |  | upper | 2050 | 35
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2020 | 50000
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2025 | 42000
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2030 | 39000
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2040 | 34000
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2050 | 33000
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | H | 3 | lower | 2025 | 35700
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | H | 3 | lower | 2050 | 24750
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | H | 3 | upper | 2025 | 48300
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | H | 3 | upper | 2050 | 49500
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 3 | ctrl | 2020 | 1.7
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 3 | ctrl | 2025 | 1.49
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 3 | ctrl | 2030 | 1.38
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 3 | ctrl | 2040 | 1.24
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 3 | ctrl | 2050 | 1.19
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 3 | lower | 2025 | 1.49
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 3 | lower | 2050 | 1.19
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 3 | upper | 2025 | 1.49
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 3 | upper | 2050 | 1.19
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2020 | 0.01
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2025 | 0.01
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2030 | 0.01
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2040 | 0.01
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2050 | 0.01
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | lower | 2025 | 0.01
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | lower | 2050 | 0.01
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | upper | 2025 | 0.05
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (array cables) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | upper | 2050 | 0.04
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2020 | 0.13
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2025 | 0.13
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2030 | 0.12
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2040 | 0.11
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2050 | 0.11
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 4 | lower | 2025 | 0.11
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 4 | lower | 2050 | 0.08
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 4 | upper | 2025 | 0.51
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (foundation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 4 | upper | 2050 | 0.42
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2020 | 0.05
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2025 | 0.05
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2030 | 0.05
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2040 | 0.05
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2050 | 0.05
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 5 | lower | 2025 | 0.04
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 5 | lower | 2050 | 0.04
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 5 | upper | 2025 | 0.2
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 5 | upper | 2050 | 0.19
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2020 | 0.39
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2025 | 0.31
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2030 | 0.25
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2040 | 0.23
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2050 | 0.22
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | lower | 2025 | 0.31
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | lower | 2050 | 0.22
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | upper | 2025 | 0.31
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | upper | 2050 | 0.22
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2020 | 0.39
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2025 | 0.33
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2030 | 0.29
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2040 | 0.26
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2050 | 0.25
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 6 | lower | 2025 | 0.28
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 6 | lower | 2050 | 0.18
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 6 | upper | 2025 | 1.31
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (project development etc.) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3, 6 | upper | 2050 | 0.98
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2020 | 0.72
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2025 | 0.66
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2030 | 0.65
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2040 | 0.58
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | ctrl | 2050 | 0.56
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | lower | 2025 | 0.56
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | lower | 2050 | 0.42
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | upper | 2025 | 2.63
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Nominal investment (turbines) [MEUR/MW_e] | MEUR/MW_e | 2020 |  | 3 | upper | 2050 | 2.24
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | H | 3 | ctrl | 2020 | 5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | H | 3 | ctrl | 2025 | 4.17
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | H | 3 | ctrl | 2030 | 3.89
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | H | 3 | ctrl | 2040 | 3.42
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | H | 3 | ctrl | 2050 | 3.25
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | H | 3 | lower | 2025 | 3.55
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | H | 3 | lower | 2050 | 2.44
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | H | 3 | upper | 2025 | 16.69
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | H | 3 | upper | 2050 | 13.01
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | J | 3 | ctrl | 2020 | 4100
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | J | 3 | ctrl | 2025 | 4325
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | J | 3 | ctrl | 2030 | 4450
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | J | 3 | ctrl | 2040 | 4450
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | J | 3 | ctrl | 2050 | 4450
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | J | 3 | lower | 2025 | 3675
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | J | 3 | lower | 2050 | 3250
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | J | 3 | upper | 2025 | 4975
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | J | 3 | upper | 2050 | 6500
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | 1 | ctrl | 2020 | 103.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | 1 | ctrl | 2025 | 115.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | 1 | ctrl | 2030 | 138
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | 1 | ctrl | 2040 | 138
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | 1 | ctrl | 2050 | 138
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | 1 | lower | 2025 | 98.17
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | 1 | lower | 2050 | 103.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | 1 | upper | 2025 | 132.82
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Hub height [m] | m |  |  | 1 | upper | 2050 | 207
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  |  | 1 | ctrl | 2020 | 167
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  |  | 1 | ctrl | 2025 | 191
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  |  | 1 | ctrl | 2030 | 236
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  |  | 1 | ctrl | 2040 | 236
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  |  | 1 | ctrl | 2050 | 236
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  |  | 1 | lower | 2025 | 162.35
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  |  | 1 | lower | 2050 | 177
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  |  | 1 | upper | 2025 | 219.65
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Rotor diameter [m] | m |  |  | 1 | upper | 2050 | 354
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | E | 3 | ctrl | 2020 | 31.23
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | E | 3 | ctrl | 2025 | 28.42
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | E | 3 | ctrl | 2030 | 27.92
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | E | 3 | ctrl | 2040 | 27.92
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | E | 3 | ctrl | 2050 | 27.92
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | E | 3 | lower | 2025 | 33.44
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | E | 3 | lower | 2050 | 37.23
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | E | 3 | upper | 2025 | 24.71
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Specific area coverage [MW_e/km2] | MW_e/km2 |  | E | 3 | upper | 2050 | 22.34
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | I | 1 | ctrl | 2020 | 383.49
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | I | 1 | ctrl | 2025 | 349.01
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | I | 1 | ctrl | 2030 | 342.91
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | I | 1 | ctrl | 2040 | 342.91
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | I | 1 | ctrl | 2050 | 342.91
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | I | 1 | lower | 2025 | 410.61
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | I | 1 | lower | 2050 | 457.21
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | I | 1 | upper | 2025 | 303.49
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Technology-specific data | Specific power [W_e/m2] | W_e/m2 |  | I | 1 | upper | 2050 | 190.5
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2015 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2040 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2040 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | B3,C |  | ctrl | 2015 | 0.006
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | B3,C |  | ctrl | 2020 | 0.006
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | B3,C |  | ctrl | 2030 | 0.006
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | B3,C |  | ctrl | 2040 | 0.006
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | B3,C |  | ctrl | 2050 | 0.006
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2040 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 6 | ctrl | 2015 | 6.36
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 6 | ctrl | 2020 | 5.12
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 6 | ctrl | 2030 | 4.57
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 6 | ctrl | 2040 | 4.29
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 6 | ctrl | 2050 | 4.04
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2015 | 30
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2020 | 35
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2030 | 40
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2040 | 40
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2050 | 40
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2015 | 16700
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2020 | 13400
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2030 | 10700
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2040 | 9600
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2050 | 8900
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | lower | 2020 | 12100
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | lower | 2050 | 8100
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | upper | 2020 | 14800
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | upper | 2050 | 9900
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2015 | 1.67
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2020 | 1.24
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2030 | 0.84
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2040 | 0.7
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2050 | 0.64
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O | 2, 4 | lower | 2020 | 1.19
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O | 2, 4 | lower | 2050 | 0.54
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O | 2, 4 | upper | 2020 | 1.3
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O | 2, 4 | upper | 2050 | 0.85
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2015 | 1.59
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2020 | 1.18
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2030 | 0.8
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2040 | 0.67
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2050 | 0.61
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N | 2, 4 | lower | 2020 | 1.13
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N | 2, 4 | lower | 2050 | 0.52
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N | 2, 4 | upper | 2020 | 1.24
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N | 2, 4 | upper | 2050 | 0.81
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.03
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.03
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.02
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.02
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.03
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.02
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.03
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.02
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.13
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.11
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.09
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.09
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.13
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.08
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.14
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.1
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.22
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.14
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.12
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.1
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.21
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.09
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.23
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.12
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.86
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.21
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.17
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.15
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.14
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.2
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.13
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.22
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.16
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2015 | 0.81
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2020 | 0.49
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2030 | 0.27
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2040 | 0.2
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2050 | 0.17
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | lower | 2020 | 0.47
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | lower | 2050 | 0.14
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | upper | 2020 | 0.51
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | upper | 2050 | 0.33
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Average annual degradation of full-load hours [] |  |  |  |  | ctrl | 2015 | 0.005
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Average annual degradation of full-load hours [] |  |  |  |  | ctrl | 2020 | 0.004
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Average annual degradation of full-load hours [] |  |  |  |  | ctrl | 2030 | 0.003
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Average annual degradation of full-load hours [] |  |  |  |  | ctrl | 2040 | 0.003
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Average annual degradation of full-load hours [] |  |  |  |  | ctrl | 2050 | 0.003
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | MWh_e/MW_e |  | A1,I |  | ctrl | 2015 | 934.72
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | MWh_e/MW_e |  | A1,I |  | ctrl | 2020 | 1010.33
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | MWh_e/MW_e |  | A1,I |  | ctrl | 2030 | 1116.06
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | MWh_e/MW_e |  | A1,I |  | ctrl | 2040 | 1127.81
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | MWh_e/MW_e |  | A1,I |  | ctrl | 2050 | 1139.56
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1 |  | ctrl | 2015 | 981.46
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1 |  | ctrl | 2020 | 1060.84
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1 |  | ctrl | 2030 | 1171.86
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1 |  | ctrl | 2040 | 1184.2
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1 |  | ctrl | 2050 | 1196.53
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2015 | 15900
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2020 | 12800
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2030 | 10200
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2040 | 9100
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2050 | 8500
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | lower | 2020 | 11500
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | lower | 2050 | 7700
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | upper | 2020 | 14100
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | upper | 2050 | 9400
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2020 | 12800
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2030 | 10200
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2040 | 9100
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2050 | 8500
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | MW_e |  | B3,C |  | ctrl | 2015 | 0.0063
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | MW_e |  | B3,C |  | ctrl | 2020 | 0.0063
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | MW_e |  | B3,C |  | ctrl | 2030 | 0.0063
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | MW_e |  | B3,C |  | ctrl | 2040 | 0.0063
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | MW_e |  | B3,C |  | ctrl | 2050 | 0.0063
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | MWh/m2/y |  | A | 1 | ctrl | 2015 | 1068
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | MWh/m2/y |  | A | 1 | ctrl | 2020 | 1068
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | MWh/m2/y |  | A | 1 | ctrl | 2030 | 1068
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | MWh/m2/y |  | A | 1 | ctrl | 2040 | 1068
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | MWh/m2/y |  | A | 1 | ctrl | 2050 | 1068
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2015 | 10
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2020 | 12.5
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2030 | 15
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2040 | 15
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2050 | 15
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.27
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.22
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.19
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.18
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.26
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.16
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.28
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.2
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.21
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.14
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.11
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.1
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.2
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.08
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.22
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.12
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.82
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.2
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.16
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.15
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.14
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.19
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.12
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.21
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.15
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2015 | 0.78
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2020 | 0.47
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2030 | 0.26
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2040 | 0.19
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2050 | 0.17
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | lower | 2020 | 0.45
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | lower | 2050 | 0.13
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | upper | 2020 | 0.49
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | upper | 2050 | 0.31
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.03
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.02
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.02
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.02
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.03
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.02
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.03
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.02
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | ctrl | 2015 | 0.165
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | ctrl | 2020 | 0.205
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | ctrl | 2030 | 0.23
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | ctrl | 2040 | 0.245
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | ctrl | 2050 | 0.26
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] |  |  | F |  | ctrl | 2015 | 0.79
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] |  |  | F |  | ctrl | 2020 | 0.86
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] |  |  | F |  | ctrl | 2030 | 0.95
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] |  |  | F |  | ctrl | 2040 | 0.96
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] |  |  | F |  | ctrl | 2050 | 0.97
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | W_e/W_e |  | D | 6 | ctrl | 2015 | 1.05
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | W_e/W_e |  | D | 6 | ctrl | 2020 | 1.05
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | W_e/W_e |  | D | 6 | ctrl | 2030 | 1.05
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | W_e/W_e |  | D | 6 | ctrl | 2040 | 1.05
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | W_e/W_e |  | D | 6 | ctrl | 2050 | 1.05
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | 1000m2/MW_e |  |  | 6 | ctrl | 2015 | 6.06
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | 1000m2/MW_e |  |  | 6 | ctrl | 2020 | 4.88
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | 1000m2/MW_e |  |  | 6 | ctrl | 2030 | 4.35
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | 1000m2/MW_e |  |  | 6 | ctrl | 2040 | 4.08
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | 1000m2/MW_e |  |  | 6 | ctrl | 2050 | 3.85
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Transposition factor |  |  | E |  | ctrl | 2015 | 1.1
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Transposition factor |  |  | E |  | ctrl | 2020 | 1.1
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Transposition factor |  |  | E |  | ctrl | 2030 | 1.1
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Transposition factor |  |  | E |  | ctrl | 2040 | 1.1
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | Technology-specific data | Transposition factor |  |  | E |  | ctrl | 2050 | 1.1
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2015 | 0
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 0
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 0
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2040 | 0
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 0
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2040 | 0
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | B2,C |  | ctrl | 2015 | 0.1
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | B2,C |  | ctrl | 2020 | 0.1
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | B2,C |  | ctrl | 2030 | 0.1
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | B2,C |  | ctrl | 2040 | 0.1
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | B2,C |  | ctrl | 2050 | 0.1
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 0
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 0
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 0
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2040 | 0
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 0
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 6 | ctrl | 2015 | 6.67
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 6 | ctrl | 2020 | 5.37
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 6 | ctrl | 2030 | 4.78
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 6 | ctrl | 2040 | 4.49
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 6 | ctrl | 2050 | 4.23
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2015 | 30
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2020 | 35
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2030 | 40
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2040 | 40
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2050 | 40
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2015 | 14300
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2020 | 10600
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2030 | 8900
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2040 | 8000
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2050 | 7500
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | lower | 2020 | 9500
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | lower | 2050 | 6700
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | upper | 2020 | 11700
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | upper | 2050 | 8300
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2015 | 1.43
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2020 | 0.87
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2030 | 0.57
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2040 | 0.46
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2050 | 0.41
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O | 2, 4 | lower | 2020 | 0.86
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O | 2, 4 | lower | 2050 | 0.36
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O | 2, 4 | upper | 2020 | 0.92
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O | 2, 4 | upper | 2050 | 0.59
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2015 | 1.3
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2020 | 0.79
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2030 | 0.51
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2040 | 0.42
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2050 | 0.38
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N | 2, 4 | lower | 2020 | 0.78
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N | 2, 4 | lower | 2050 | 0.33
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N | 2, 4 | upper | 2020 | 0.84
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N | 2, 4 | upper | 2050 | 0.53
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.04
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.04
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.03
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.03
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.04
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.03
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.05
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.03
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.13
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.11
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.09
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.09
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.13
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.08
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.14
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.1
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.17
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.11
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.09
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.08
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.17
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.07
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.18
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.1
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.61
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.09
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.07
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.06
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.06
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.09
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.05
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.09
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.07
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2015 | 0.81
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2020 | 0.44
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2030 | 0.24
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2040 | 0.18
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2050 | 0.15
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | lower | 2020 | 0.43
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | lower | 2050 | 0.12
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | upper | 2020 | 0.46
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | upper | 2050 | 0.29
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Average annual degradation of full-load hours [] |  |  |  |  | ctrl | 2015 | 0.005
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Average annual degradation of full-load hours [] |  |  |  |  | ctrl | 2020 | 0.004
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Average annual degradation of full-load hours [] |  |  |  |  | ctrl | 2030 | 0.003
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Average annual degradation of full-load hours [] |  |  |  |  | ctrl | 2040 | 0.003
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Average annual degradation of full-load hours [] |  |  |  |  | ctrl | 2050 | 0.003
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | MWh_e/MW_e |  | A1,I |  | ctrl | 2015 | 950.59
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | MWh_e/MW_e |  | A1,I |  | ctrl | 2020 | 1010.33
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | MWh_e/MW_e |  | A1,I |  | ctrl | 2030 | 1116.06
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | MWh_e/MW_e |  | A1,I |  | ctrl | 2040 | 1127.81
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | MWh_e/MW_e |  | A1,I |  | ctrl | 2050 | 1139.56
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1 |  | ctrl | 2015 | 1045.65
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1 |  | ctrl | 2020 | 1111.36
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1 |  | ctrl | 2030 | 1227.67
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1 |  | ctrl | 2040 | 1240.59
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1 |  | ctrl | 2050 | 1253.51
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2015 | 13000
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2020 | 9600
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2030 | 8100
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2040 | 7300
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | ctrl | 2050 | 6800
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | lower | 2020 | 8600
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | lower | 2050 | 6100
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | upper | 2020 | 10600
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P |  | upper | 2050 | 7500
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Fixed O&M (other, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2015 | 13000
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Fixed O&M (other, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2020 | 9600
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Fixed O&M (other, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2030 | 8100
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Fixed O&M (other, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2040 | 7300
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Fixed O&M (other, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2050 | 6800
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | MW_e |  | B2,C |  | ctrl | 2015 | 0.11
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | MW_e |  | B2,C |  | ctrl | 2020 | 0.11
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | MW_e |  | B2,C |  | ctrl | 2030 | 0.11
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | MW_e |  | B2,C |  | ctrl | 2040 | 0.11
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | MW_e |  | B2,C |  | ctrl | 2050 | 0.11
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | MWh/m2/y |  | A | 1 | ctrl | 2015 | 1068
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | MWh/m2/y |  | A | 1 | ctrl | 2020 | 1068
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | MWh/m2/y |  | A | 1 | ctrl | 2030 | 1068
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | MWh/m2/y |  | A | 1 | ctrl | 2040 | 1068
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | MWh/m2/y |  | A | 1 | ctrl | 2050 | 1068
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2015 | 10
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2020 | 12.5
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2030 | 15
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2040 | 15
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2050 | 15
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.12
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.1
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.09
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.08
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.12
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.07
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.13
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.09
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.16
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.1
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.08
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.07
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.16
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.06
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.17
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.09
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.56
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.08
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.06
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.06
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.05
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.08
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.05
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.08
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.06
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2015 | 0.74
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2020 | 0.4
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2030 | 0.22
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2040 | 0.16
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | ctrl | 2050 | 0.14
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | lower | 2020 | 0.39
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | lower | 2050 | 0.11
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | upper | 2020 | 0.42
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,O |  | upper | 2050 | 0.26
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.04
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.03
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.03
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.03
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.04
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.02
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.04
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.03
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | ctrl | 2015 | 0.165
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | ctrl | 2020 | 0.205
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | ctrl | 2030 | 0.23
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | ctrl | 2040 | 0.245
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | ctrl | 2050 | 0.26
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] |  |  |  | 3 | ctrl | 2015 | 0
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] |  |  |  | 3 | ctrl | 2020 | 0
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] |  |  |  | 3 | ctrl | 2030 | 0
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] |  |  |  | 3 | ctrl | 2040 | 0.01
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] |  |  |  | 3 | ctrl | 2050 | 0.02
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] |  |  | F |  | ctrl | 2015 | 0.81
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] |  |  | F |  | ctrl | 2020 | 0.86
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] |  |  | F |  | ctrl | 2030 | 0.95
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] |  |  | F |  | ctrl | 2040 | 0.96
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] |  |  | F |  | ctrl | 2050 | 0.97
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | W_e/W_e |  | D | 6 | ctrl | 2015 | 1.1
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | W_e/W_e |  | D | 6 | ctrl | 2020 | 1.1
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | W_e/W_e |  | D | 6 | ctrl | 2030 | 1.1
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | W_e/W_e |  | D | 6 | ctrl | 2040 | 1.1
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | W_e/W_e |  | D | 6 | ctrl | 2050 | 1.1
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | 1000m2/MW_e |  | W | 6 | ctrl | 2015 | 6.06
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | 1000m2/MW_e |  | W | 6 | ctrl | 2020 | 4.88
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | 1000m2/MW_e |  | W | 6 | ctrl | 2030 | 4.35
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | 1000m2/MW_e |  | W | 6 | ctrl | 2040 | 4.08
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | 1000m2/MW_e |  | W | 6 | ctrl | 2050 | 3.85
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Transposition factor |  |  | E |  | ctrl | 2015 | 1.1
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Transposition factor |  |  | E |  | ctrl | 2020 | 1.1
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Transposition factor |  |  | E |  | ctrl | 2030 | 1.1
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Transposition factor |  |  | E |  | ctrl | 2040 | 1.1
22 Rooftop PV comm.&industrial | PV - renewable power - solar - commercial/industrial rooftop | Technology-specific data | Transposition factor |  |  | E |  | ctrl | 2050 | 1.1
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2015 | 0.5
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 0.5
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 0.5
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2040 | 0.5
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 0.5
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2040 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2015 | 4
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2020 | 40
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2030 | 40
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2040 | 40
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2050 | 40
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2040 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2015 | 20.25
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2020 | 13.75
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2030 | 12.26
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2040 | 11.51
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2050 | 10.84
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2015 | 30
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2020 | 35
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2030 | 40
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2040 | 40
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2050 | 40
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2015 | 13600
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2020 | 11300
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2030 | 9500
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2040 | 8100
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2050 | 7400
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | lower | 2020 | 10100
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | lower | 2050 | 6600
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | upper | 2020 | 12400
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | upper | 2050 | 8100
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Fixed O&M (land rent) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | S |  | ctrl | 2020 | 4400
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Fixed O&M (land rent) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | S |  | ctrl | 2030 | 3900
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Fixed O&M (land rent) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | S |  | ctrl | 2040 | 3100
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Fixed O&M (land rent) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | S |  | ctrl | 2050 | 2500
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2015 | 1.55
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2020 | 0.56
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2030 | 0.38
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2040 | 0.32
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2050 | 0.29
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | lower | 2020 | 0.54
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | lower | 2050 | 0.25
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | upper | 2020 | 0.6
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | upper | 2050 | 0.4
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2015 | 1.15
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2020 | 0.45
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2030 | 0.31
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2040 | 0.26
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2050 | 0.23
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | lower | 2020 | 0.44
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | lower | 2050 | 0.2
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | upper | 2020 | 0.48
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | upper | 2050 | 0.32
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.09
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.06
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.05
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.04
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.04
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.06
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.04
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.07
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.05
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.14
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.13
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.1
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.09
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.09
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.12
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.08
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.14
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.1
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.11
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.03
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.02
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.02
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.01
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.03
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.01
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.03
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.02
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.23
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.05
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.04
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.04
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.03
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.05
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.03
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.05
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.04
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.89
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.26
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.14
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.11
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.09
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.25
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.07
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.27
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.17
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (soft costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2015 | 0.09
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (soft costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2020 | 0.04
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (soft costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2030 | 0.03
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (soft costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2040 | 0.03
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (soft costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2050 | 0.03
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (soft costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | lower | 2020 | 0.04
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (soft costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | lower | 2050 | 0.02
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (soft costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | upper | 2020 | 0.04
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Financial data | Nominal investment (soft costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | upper | 2050 | 0.03
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Average annual degradation of full-load hours [] |  |  | A2 |  | ctrl | 2015 | 0.005
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Average annual degradation of full-load hours [] |  |  | A2 |  | ctrl | 2020 | 0.004
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Average annual degradation of full-load hours [] |  |  | A2 |  | ctrl | 2030 | 0.003
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Average annual degradation of full-load hours [] |  |  | A2 |  | ctrl | 2040 | 0.003
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Average annual degradation of full-load hours [] |  |  | A2 |  | ctrl | 2050 | 0.003
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Average annual degradation of full-load hours [] |  |  | A2 |  | lower | 2020 | 0.003
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Average annual degradation of full-load hours [] |  |  | A2 |  | upper | 2020 | 0.005
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | MWh_e/MW_e |  | A1, K |  | ctrl | 2015 | 981.33
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | MWh_e/MW_e |  | A1, K |  | ctrl | 2020 | 1074.62
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | MWh_e/MW_e |  | A1, K |  | ctrl | 2030 | 1187.08
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | MWh_e/MW_e |  | A1, K |  | ctrl | 2040 | 1199.58
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | MWh_e/MW_e |  | A1, K |  | ctrl | 2050 | 1212.07
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1 |  | ctrl | 2015 | 1324.8
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1 |  | ctrl | 2020 | 1343.28
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1 |  | ctrl | 2030 | 1483.85
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1 |  | ctrl | 2040 | 1499.47
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1 |  | ctrl | 2050 | 1515.09
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2015 | 10100
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2020 | 9000
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2030 | 7600
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2040 | 6500
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2050 | 5900
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | lower | 2020 | 8100
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | lower | 2050 | 5300
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | upper | 2020 | 9900
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | upper | 2050 | 6500
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Fixed O&M (land rent, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | S | 6 | ctrl | 2020 | 3500
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Fixed O&M (land rent, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | S | 6 | ctrl | 2030 | 3100
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Fixed O&M (land rent, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | S | 6 | ctrl | 2040 | 2500
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Fixed O&M (land rent, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | S | 6 | ctrl | 2050 | 2000
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Fixed O&M (other, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2020 | 5500
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Fixed O&M (other, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2030 | 4500
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Fixed O&M (other, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2040 | 4000
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Fixed O&M (other, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2050 | 3900
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | MW_e |  | C |  | ctrl | 2015 | 5.4
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | MW_e |  | C |  | ctrl | 2020 | 50
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | MW_e |  | C |  | ctrl | 2030 | 50
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | MW_e |  | C |  | ctrl | 2040 | 50
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | MW_e |  | C |  | ctrl | 2050 | 50
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | MWh/m2/y |  | A | 1 | ctrl | 2015 | 1068
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | MWh/m2/y |  | A | 1 | ctrl | 2020 | 1068
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | MWh/m2/y |  | A | 1 | ctrl | 2030 | 1068
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | MWh/m2/y |  | A | 1 | ctrl | 2040 | 1068
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | MWh/m2/y |  | A | 1 | ctrl | 2050 | 1068
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2015 | 10
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2020 | 12.5
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2030 | 15
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2040 | 15
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2050 | 15
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2015 | 0.11
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2020 | 0.1
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2030 | 0.08
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2040 | 0.07
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2050 | 0.07
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | lower | 2020 | 0.1
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | lower | 2050 | 0.06
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | upper | 2020 | 0.11
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | upper | 2050 | 0.08
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.08
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.02
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.02
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.01
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.01
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.02
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.01
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.03
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.01
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.17
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.04
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.03
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.03
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.03
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.04
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.02
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.04
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.03
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.66
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.21
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.11
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.08
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.07
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.2
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.06
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.22
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.14
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (soft costs, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2015 | 0.06
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (soft costs, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2020 | 0.03
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (soft costs, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2030 | 0.02
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (soft costs, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2040 | 0.02
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (soft costs, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2050 | 0.02
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (soft costs, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | lower | 2020 | 0.03
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (soft costs, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | lower | 2050 | 0.02
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (soft costs, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | upper | 2020 | 0.03
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (soft costs, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | upper | 2050 | 0.02
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | R |  | ctrl | 2015 | 0.06
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | R |  | ctrl | 2020 | 0.05
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | R |  | ctrl | 2030 | 0.04
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | R |  | ctrl | 2040 | 0.04
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | R |  | ctrl | 2050 | 0.03
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | R |  | lower | 2020 | 0.05
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | R |  | lower | 2050 | 0.03
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | R |  | upper | 2020 | 0.05
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | R |  | upper | 2050 | 0.04
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | ctrl | 2015 | 0.165
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | ctrl | 2020 | 0.205
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | ctrl | 2030 | 0.23
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | ctrl | 2040 | 0.245
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | ctrl | 2050 | 0.26
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | lower | 2020 | 0.2
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | upper | 2020 | 0.21
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Performance ratio (contribution from bifaciality) [] |  |  | H | 3 | ctrl | 2015 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Performance ratio (contribution from bifaciality) [] |  |  | H | 3 | ctrl | 2020 | 0.01
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Performance ratio (contribution from bifaciality) [] |  |  | H | 3 | ctrl | 2030 | 0.05
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Performance ratio (contribution from bifaciality) [] |  |  | H | 3 | ctrl | 2040 | 0.05
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Performance ratio (contribution from bifaciality) [] |  |  | H | 3 | ctrl | 2050 | 0.05
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Performance ratio (measure of combined losses) [] |  |  | F |  | ctrl | 2015 | 0.81
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Performance ratio (measure of combined losses) [] |  |  | F |  | ctrl | 2020 | 0.86
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Performance ratio (measure of combined losses) [] |  |  | F |  | ctrl | 2030 | 0.95
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Performance ratio (measure of combined losses) [] |  |  | F |  | ctrl | 2040 | 0.96
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Performance ratio (measure of combined losses) [] |  |  | F |  | ctrl | 2050 | 0.97
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | W_e/W_e |  | D | 6 | ctrl | 2015 | 1.35
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | W_e/W_e |  | D | 6 | ctrl | 2020 | 1.25
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | W_e/W_e |  | D | 6 | ctrl | 2030 | 1.25
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | W_e/W_e |  | D | 6 | ctrl | 2040 | 1.25
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | W_e/W_e |  | D | 6 | ctrl | 2050 | 1.25
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2015 | 15
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2020 | 11
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2030 | 9.8
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2040 | 9.2
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2050 | 8.67
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Transposition factor |  |  | E |  | ctrl | 2015 | 1.15
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Transposition factor |  |  | E |  | ctrl | 2020 | 1.17
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Transposition factor |  |  | E |  | ctrl | 2030 | 1.17
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Transposition factor |  |  | E |  | ctrl | 2040 | 1.17
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | Technology-specific data | Transposition factor |  |  | E |  | ctrl | 2050 | 1.17
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 0.5
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 0.5
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2040 | 0.5
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 0.5
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2040 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2020 | 40
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2030 | 40
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2040 | 40
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | ctrl | 2050 | 40
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2040 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2020 | 17.88
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2030 | 15.93
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2040 | 14.96
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2050 | 14.09
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2020 | 35
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2030 | 40
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2040 | 40
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2050 | 40
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2015 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2020 | 12100
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2030 | 10400
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2040 | 9400
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2050 | 9000
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P2 |  | lower | 2020 | 10900
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P2 |  | lower | 2050 | 8100
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P2 |  | upper | 2020 | 13400
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P2 |  | upper | 2050 | 9900
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (land rent) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | S |  | ctrl | 2015 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (land rent) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | S |  | ctrl | 2020 | 5300
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (land rent) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | S |  | ctrl | 2030 | 4800
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (land rent) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | S |  | ctrl | 2040 | 4400
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (land rent) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | S |  | ctrl | 2050 | 4100
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2015 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2020 | 0.65
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2030 | 0.45
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2040 | 0.38
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2050 | 0.35
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | lower | 2020 | 0.6
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | lower | 2050 | 0.29
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | upper | 2020 | 0.7
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | upper | 2050 | 0.47
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2015 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2020 | 0.52
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2030 | 0.36
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2040 | 0.31
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2050 | 0.28
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | lower | 2020 | 0.48
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | lower | 2050 | 0.23
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | upper | 2020 | 0.56
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | upper | 2050 | 0.38
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.06
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.05
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.04
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.04
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.06
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.04
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.07
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.05
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.13
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.1
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.09
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.09
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.12
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.07
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.14
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.1
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.02
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.02
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.01
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.01
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (inverter) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.02
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.04
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.02
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.04
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.26
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.14
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.11
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.09
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.24
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.07
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.28
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (pv modules) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.17
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (soft costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2015 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (soft costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2020 | 0.05
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (soft costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2030 | 0.04
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (soft costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2040 | 0.04
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (soft costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2050 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (soft costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | lower | 2020 | 0.04
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (soft costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | lower | 2050 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (soft costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | upper | 2020 | 0.05
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (soft costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | upper | 2050 | 0.04
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (tracker related costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | T |  | ctrl | 2015 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (tracker related costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | T |  | ctrl | 2020 | 0.09
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (tracker related costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | T |  | ctrl | 2030 | 0.07
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (tracker related costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | T |  | ctrl | 2040 | 0.06
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (tracker related costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | T |  | ctrl | 2050 | 0.06
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (tracker related costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | T |  | lower | 2020 | 0.08
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (tracker related costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | T |  | lower | 2050 | 0.05
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (tracker related costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | T |  | upper | 2020 | 0.09
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (tracker related costs) [MEUR/MW_e] | MEUR/MW_e | 2020 | T |  | upper | 2050 | 0.07
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual degradation of full-load hours [] |  |  | A2 |  | ctrl | 2020 | 0.004
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual degradation of full-load hours [] |  |  | A2 |  | ctrl | 2030 | 0.003
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual degradation of full-load hours [] |  |  | A2 |  | ctrl | 2040 | 0.003
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual degradation of full-load hours [] |  |  | A2 |  | ctrl | 2050 | 0.003
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual degradation of full-load hours [] |  |  | A2 |  | lower | 2020 | 0.003
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual degradation of full-load hours [] |  |  | A2 |  | upper | 2020 | 0.005
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | MWh_e/MW_e |  | A1, K |  | ctrl | 2020 | 1235.81
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | MWh_e/MW_e |  | A1, K |  | ctrl | 2030 | 1369.71
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | MWh_e/MW_e |  | A1, K |  | ctrl | 2040 | 1379.51
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | MWh_e/MW_e |  | A1, K |  | ctrl | 2050 | 1393.88
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1 |  | ctrl | 2020 | 1544.77
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1 |  | ctrl | 2030 | 1712.14
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1 |  | ctrl | 2040 | 1724.39
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  | A1 |  | ctrl | 2050 | 1742.36
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2020 | 9700
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2030 | 8300
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2040 | 7500
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | ctrl | 2050 | 7200
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | lower | 2020 | 8700
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | lower | 2050 | 6500
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | upper | 2020 | 10700
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (*total, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 |  |  | upper | 2050 | 7900
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (land rent, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | S | 6 | ctrl | 2020 | 4200
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (land rent, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | S | 6 | ctrl | 2030 | 3800
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (land rent, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | S | 6 | ctrl | 2040 | 3500
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (land rent, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | S | 6 | ctrl | 2050 | 3300
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (other, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2020 | 5500
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (other, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2030 | 4500
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (other, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2040 | 4000
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (other, per DC) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2050 | 3900
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | MW_e |  | C |  | ctrl | 2020 | 50
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | MW_e |  | C |  | ctrl | 2030 | 50
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | MW_e |  | C |  | ctrl | 2040 | 50
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | MW_e |  | C |  | ctrl | 2050 | 50
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | MWh/m2/y |  | A | 1 | ctrl | 2020 | 1068
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | MWh/m2/y |  | A | 1 | ctrl | 2030 | 1068
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | MWh/m2/y |  | A | 1 | ctrl | 2040 | 1068
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | MWh/m2/y |  | A | 1 | ctrl | 2050 | 1068
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2020 | 12.5
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2030 | 15
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2040 | 15
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Inverter lifetime [years] | years |  |  | 6 | ctrl | 2050 | 15
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2020 | 0.1
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2030 | 0.08
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2040 | 0.07
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2050 | 0.07
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | lower | 2020 | 0.09
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | lower | 2050 | 0.06
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | upper | 2020 | 0.11
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (installation, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | upper | 2050 | 0.08
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.02
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.02
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.01
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.01
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.02
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.01
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (inverter, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.01
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.02
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.02
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.02
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.02
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.02
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.21
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.11
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.08
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.07
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.19
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.05
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.22
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (pv module, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.14
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (soft costs, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2020 | 0.04
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (soft costs, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2030 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (soft costs, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2040 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (soft costs, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | ctrl | 2050 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (soft costs, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | lower | 2020 | 0.04
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (soft costs, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | lower | 2050 | 0.02
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (soft costs, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | upper | 2020 | 0.04
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (soft costs, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | V |  | upper | 2050 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (tracker related cost, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | T |  | ctrl | 2020 | 0.07
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (tracker related cost, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | T |  | ctrl | 2030 | 0.06
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (tracker related cost, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | T |  | ctrl | 2040 | 0.05
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (tracker related cost, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | T |  | ctrl | 2050 | 0.05
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (tracker related cost, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | T |  | lower | 2020 | 0.06
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (tracker related cost, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | T |  | lower | 2050 | 0.04
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (tracker related cost, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | T |  | upper | 2020 | 0.08
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (tracker related cost, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | T |  | upper | 2050 | 0.05
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | R |  | ctrl | 2020 | 0.05
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | R |  | ctrl | 2030 | 0.04
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | R |  | ctrl | 2040 | 0.04
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | R |  | ctrl | 2050 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | R |  | lower | 2020 | 0.04
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | R |  | lower | 2050 | 0.03
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | R |  | upper | 2020 | 0.05
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | MEUR/MW_e | 2020 | R |  | upper | 2050 | 0.04
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | ctrl | 2020 | 0.205
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | ctrl | 2030 | 0.23
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | ctrl | 2040 | 0.245
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | ctrl | 2050 | 0.26
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | lower | 2020 | 0.2
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | PV module conversion efficiency [] |  |  | U | 3 | upper | 2020 | 0.21
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (contribution from bifaciality) [] |  |  | H | 3 | ctrl | 2020 | 0.01
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (contribution from bifaciality) [] |  |  | H | 3 | ctrl | 2030 | 0.05
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (contribution from bifaciality) [] |  |  | H | 3 | ctrl | 2040 | 0.05
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (contribution from bifaciality) [] |  |  | H | 3 | ctrl | 2050 | 0.05
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (measure of combined losses) [] |  |  | F |  | ctrl | 2020 | 0.86
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (measure of combined losses) [] |  |  | F |  | ctrl | 2030 | 0.95
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (measure of combined losses) [] |  |  | F |  | ctrl | 2040 | 0.96
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (measure of combined losses) [] |  |  | F |  | ctrl | 2050 | 0.97
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | W_e/W_e |  | D | 5, 6 | ctrl | 2020 | 1.25
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | W_e/W_e |  | D | 5, 6 | ctrl | 2030 | 1.25
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | W_e/W_e |  | D | 5, 6 | ctrl | 2040 | 1.25
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | W_e/W_e |  | D | 5, 6 | ctrl | 2050 | 1.25
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2020 | 14.3
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2030 | 12.75
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2040 | 11.97
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2050 | 11.28
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Transposition factor |  |  | E |  | ctrl | 2020 | 1.35
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Transposition factor |  |  | E |  | ctrl | 2030 | 1.35
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Transposition factor |  |  | E |  | ctrl | 2040 | 1.35
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | Technology-specific data | Transposition factor |  |  | E |  | ctrl | 2050 | 1.35
23 Wave Energy | Wave power - renewable power - wave - medium | Energy/technical data | Construction time [years] | years |  | C | 4 | ctrl | 2020 | 3.5
23 Wave Energy | Wave power - renewable power - wave - medium | Energy/technical data | Construction time [years] | years |  | C | 4 | ctrl | 2030 | 3.5
23 Wave Energy | Wave power - renewable power - wave - medium | Energy/technical data | Construction time [years] | years |  | C | 4 | ctrl | 2050 | 3.5
23 Wave Energy | Wave power - renewable power - wave - medium | Energy/technical data | Construction time [years] | years |  |  |  | lower | 2020 | 3
23 Wave Energy | Wave power - renewable power - wave - medium | Energy/technical data | Construction time [years] | years |  |  |  | lower | 2050 | 3
23 Wave Energy | Wave power - renewable power - wave - medium | Energy/technical data | Construction time [years] | years |  |  |  | upper | 2020 | 4
23 Wave Energy | Wave power - renewable power - wave - medium | Energy/technical data | Construction time [years] | years |  |  |  | upper | 2050 | 4
23 Wave Energy | Wave power - renewable power - wave - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2020 | 2
23 Wave Energy | Wave power - renewable power - wave - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | lower | 2050 | 50
23 Wave Energy | Wave power - renewable power - wave - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2020 | 50
23 Wave Energy | Wave power - renewable power - wave - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  |  |  | upper | 2050 | 500
23 Wave Energy | Wave power - renewable power - wave - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 4 | ctrl | 2015 | 10
23 Wave Energy | Wave power - renewable power - wave - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 4 | ctrl | 2020 | 20
23 Wave Energy | Wave power - renewable power - wave - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 4 | ctrl | 2030 | 25
23 Wave Energy | Wave power - renewable power - wave - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 4 | ctrl | 2050 | 30
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2015 | 0
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2020 | 0
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2030 | 0
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | ctrl | 2050 | 0
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2020 | 4.0408
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | lower | 2050 | 0
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2020 | 9.5704
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 |  | upper | 2050 | 0
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [A, B] | [2, 2, 2, 3] | ctrl | 2015 | 0
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [A, B] | [2, 2, 2, 3] | ctrl | 2020 | 0
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [A, B] | [2, 2, 2, 3] | ctrl | 2030 | 0
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [A, B] | [2, 2, 2, 3] | ctrl | 2050 | 1.7014
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [A, B] | [2, 2, 2, 3] | lower | 2020 | 0
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [A, B] | [2, 2, 2, 3] | lower | 2050 | 0
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [A, B] | [2, 2, 2, 3] | upper | 2020 | 0
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [A, B] | [2, 2, 2, 3] | upper | 2050 | 0
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Variable O&M (*total) [2011-EUR/MWh_e] | 2011-EUR/MWh_e | 2020 | 0 | 4 | ctrl | 2015 | 21.2675
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Variable O&M (*total) [2011-EUR/MWh_e] | 2011-EUR/MWh_e | 2020 | 0 | 4 | ctrl | 2020 | 15.9506
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Variable O&M (*total) [2011-EUR/MWh_e] | 2011-EUR/MWh_e | 2020 | 0 | 4 | ctrl | 2030 | 10.6337
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Variable O&M (*total) [2011-EUR/MWh_e] | 2011-EUR/MWh_e | 2020 | 0 | 4 | ctrl | 2050 | 7.4436
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Variable O&M (*total) [2011-EUR/MWh_e] | 2011-EUR/MWh_e | 2020 | 0 | 4 | lower | 2020 | 0
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Variable O&M (*total) [2011-EUR/MWh_e] | 2011-EUR/MWh_e | 2020 | 0 | 4 | lower | 2050 | 0
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Variable O&M (*total) [2011-EUR/MWh_e] | 2011-EUR/MWh_e | 2020 | 0 | 4 | upper | 2020 | 0
23 Wave Energy | Wave power - renewable power - wave - medium | Financial data | Variable O&M (*total) [2011-EUR/MWh_e] | 2011-EUR/MWh_e | 2020 | 0 | 4 | upper | 2050 | 0
23 Wave Energy | Wave power - renewable power - wave - medium | Technology-specific data | Availability [] |  |  |  | 4 | ctrl | 2015 | 0.9
23 Wave Energy | Wave power - renewable power - wave - medium | Technology-specific data | Availability [] |  |  |  | 4 | ctrl | 2020 | 0.95
23 Wave Energy | Wave power - renewable power - wave - medium | Technology-specific data | Availability [] |  |  |  | 4 | ctrl | 2030 | 0.97
23 Wave Energy | Wave power - renewable power - wave - medium | Technology-specific data | Availability [] |  |  |  | 4 | ctrl | 2050 | 0.98
23 Wave Energy | Wave power - renewable power - wave - medium | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  |  | 4 | ctrl | 2015 | 1500
23 Wave Energy | Wave power - renewable power - wave - medium | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  |  | 4 | ctrl | 2020 | 2500
23 Wave Energy | Wave power - renewable power - wave - medium | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  |  | 4 | ctrl | 2030 | 3500
23 Wave Energy | Wave power - renewable power - wave - medium | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | MWh_e/MW_e |  |  | 4 | ctrl | 2050 | 4500
23 Wave Energy | Wave power - renewable power - wave - medium | Technology-specific data | Length of installation of one power plant [km] | km |  |  |  | lower | 2020 | 0.2
23 Wave Energy | Wave power - renewable power - wave - medium | Technology-specific data | Length of installation of one power plant [km] | km |  |  |  | lower | 2050 | 5
23 Wave Energy | Wave power - renewable power - wave - medium | Technology-specific data | Length of installation of one power plant [km] | km |  |  |  | upper | 2020 | 5
23 Wave Energy | Wave power - renewable power - wave - medium | Technology-specific data | Length of installation of one power plant [km] | km |  |  |  | upper | 2050 | 100
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | ctrl | 2020 | 0.01
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | ctrl | 2025 | 0.01
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | ctrl | 2030 | 0.01
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | ctrl | 2040 | 0.01
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | ctrl | 2050 | 0.01
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | lower | 2025 | 0.01
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | lower | 2050 | 0.01
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | upper | 2025 | 0.01
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | upper | 2050 | 0.01
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | ctrl | 2020 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | ctrl | 2025 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | ctrl | 2030 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | ctrl | 2040 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | ctrl | 2050 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | lower | 2025 | 0.3
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | lower | 2050 | 0.3
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | upper | 2025 | 0.05
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | upper | 2050 | 0.05
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2020 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2025 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2030 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2040 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2050 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2025 | 0.3
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2050 | 0.2
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2025 | 1.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2050 | 1.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2020 | 2.9
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2025 | 2.95
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2030 | 3
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2040 | 3.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2050 | 3.15
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | lower | 2025 | 2.75
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | lower | 2050 | 2.85
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | upper | 2025 | 3.35
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | upper | 2050 | 3.55
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2020 | 2.55
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2025 | 2.6
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2030 | 2.65
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2040 | 2.75
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2050 | 2.8
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | lower | 2025 | 2.4
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | lower | 2050 | 2.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | upper | 2025 | 3
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | upper | 2050 | 3.2
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | lower | 2025 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | lower | 2050 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | upper | 2025 | 2
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | upper | 2050 | 2
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | ctrl | 2020 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | ctrl | 2025 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | ctrl | 2030 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | ctrl | 2040 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | ctrl | 2050 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | lower | 2025 | 0.7
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | lower | 2050 | 0.7
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | upper | 2025 | 2
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | upper | 2050 | 2
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2020 | 25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2025 | 25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2030 | 25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2040 | 25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2050 | 25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | lower | 2025 | 15
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | lower | 2050 | 15
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | upper | 2025 | 40
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | upper | 2050 | 40
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | ctrl | 2020 | 2126.7454
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | ctrl | 2025 | 2126.7454
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | ctrl | 2030 | 2126.7454
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | ctrl | 2040 | 2126.7454
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | ctrl | 2050 | 2126.7454
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | lower | 2025 | 1063.3727
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | lower | 2050 | 1063.3727
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | upper | 2025 | 3190.1182
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | upper | 2050 | 5316.8636
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2020 | 1.5206
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2025 | 1.5206
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2030 | 1.4143
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2040 | 1.4143
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2050 | 1.4143
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | lower | 2025 | 1.0102
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | lower | 2050 | 1.0102
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | upper | 2025 | 2.0204
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | upper | 2050 | 2.0204
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2020 | 1.1378
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2025 | 1.1378
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2030 | 1.0634
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2040 | 1.0634
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2050 | 1.0634
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2025 | 0.75499
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2050 | 0.75499
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2025 | 1.5206
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2050 | 1.5206
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | ctrl | 2020 | 0.031901
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | ctrl | 2025 | 0.031901
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | ctrl | 2030 | 0.031901
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | ctrl | 2040 | 0.031901
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | ctrl | 2050 | 0.031901
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | lower | 2025 | 0.021267
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | lower | 2050 | 0.021267
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | upper | 2025 | 0.20204
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | upper | 2050 | 0.20204
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2020 | 0.27648
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2025 | 0.27648
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2030 | 0.25521
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2040 | 0.25521
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2050 | 0.25521
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2025 | 0.18077
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2050 | 0.18077
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2025 | 0.20204
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2050 | 0.20204
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | ctrl | 2020 | 10.6337
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | ctrl | 2025 | 10.6337
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | ctrl | 2030 | 10.6337
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | ctrl | 2040 | 10.6337
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | ctrl | 2050 | 10.6337
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | lower | 2025 | 5.3169
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | lower | 2050 | 2.1267
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | upper | 2025 | 21.2675
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | upper | 2050 | 21.2675
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2020 | 2.8605
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2025 | 2.8605
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2030 | 2.8605
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2040 | 2.8605
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2050 | 2.8605
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | lower | 2025 | 2.3075
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | lower | 2050 | 2.3075
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | upper | 2025 | 3.3709
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | upper | 2050 | 3.3709
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | upper | 2025 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | upper | 2050 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2020 | 2.8605
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2025 | 2.8605
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2030 | 2.8605
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2040 | 2.8605
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2050 | 2.8605
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | lower | 2025 | 2.3075
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | lower | 2050 | 2.3075
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | upper | 2025 | 3.3709
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | upper | 2050 | 3.3709
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | lower | 2025 | 0.2
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | lower | 2050 | 0.2
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | ctrl | 2020 | 0.25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | ctrl | 2025 | 0.25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | ctrl | 2030 | 0.25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | ctrl | 2040 | 0.25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | ctrl | 2050 | 0.25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2020 | 0.05
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2025 | 0.05
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2030 | 0.05
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2040 | 0.05
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2050 | 0.05
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | lower | 2025 | 0.05
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | lower | 2050 | 0.05
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | upper | 2025 | 0.2
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | upper | 2050 | 0.2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | ctrl | 2020 | 0.01
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | ctrl | 2025 | 0.01
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | ctrl | 2030 | 0.01
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | ctrl | 2040 | 0.01
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | ctrl | 2050 | 0.01
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | lower | 2025 | 0.01
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | lower | 2050 | 0.01
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | upper | 2025 | 0.01
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | upper | 2050 | 0.01
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | ctrl | 2020 | 0.7
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | ctrl | 2025 | 0.7
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | ctrl | 2030 | 0.6
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | ctrl | 2040 | 0.6
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | ctrl | 2050 | 0.6
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | lower | 2025 | 0.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | lower | 2050 | 0.4
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | upper | 2025 | 0.05
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | upper | 2050 | 0.05
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2020 | 3
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2025 | 3
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2030 | 3
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2040 | 3
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2050 | 3
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2025 | 1.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2050 | 1.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2025 | 5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2050 | 5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2020 | 3.4
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2025 | 3.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2030 | 3.6
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2040 | 3.65
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2050 | 3.7
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | lower | 2025 | 3.2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | lower | 2050 | 3.3
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | upper | 2025 | 3.7
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | upper | 2050 | 3.8
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2020 | 3.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2025 | 3.15
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2030 | 3.2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2040 | 3.3
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2050 | 3.4
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | lower | 2025 | 2.9
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | lower | 2050 | 3
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | upper | 2025 | 3.3
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | upper | 2050 | 3.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | lower | 2025 | 0.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | lower | 2050 | 0.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | upper | 2025 | 2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | upper | 2050 | 2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | ctrl | 2020 | 0.8
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | ctrl | 2025 | 0.8
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | ctrl | 2030 | 0.8
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | ctrl | 2040 | 0.8
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | ctrl | 2050 | 0.8
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | lower | 2025 | 0.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | lower | 2050 | 0.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | upper | 2025 | 1.2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | upper | 2050 | 1.2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2020 | 25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2025 | 25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2030 | 25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2040 | 25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2050 | 25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | lower | 2025 | 15
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | lower | 2050 | 15
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | upper | 2025 | 40
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | upper | 2050 | 40
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | ctrl | 2020 | 2126.7454
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | ctrl | 2025 | 2126.7454
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | ctrl | 2030 | 2126.7454
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | ctrl | 2040 | 2126.7454
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | ctrl | 2050 | 2126.7454
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | lower | 2025 | 1063.3727
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | lower | 2050 | 1063.3727
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | upper | 2025 | 3190.1182
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | upper | 2050 | 5316.8636
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2020 | 1.0102
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2025 | 1.0102
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2030 | 0.9145
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2040 | 0.9145
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2050 | 0.9145
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | lower | 2025 | 0.80816
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | lower | 2050 | 0.71246
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | upper | 2025 | 1.5206
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | upper | 2050 | 1.5206
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2020 | 0.80816
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2025 | 0.80816
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2030 | 0.72309
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2040 | 0.72309
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2050 | 0.72309
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2025 | 0.64866
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2050 | 0.56359
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2025 | 1.2122
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2050 | 1.2122
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | ctrl | 2020 | 0.021267
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | ctrl | 2025 | 0.021267
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | ctrl | 2030 | 0.021267
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | ctrl | 2040 | 0.021267
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | ctrl | 2050 | 0.021267
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | lower | 2025 | 0.021267
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | lower | 2050 | 0.010634
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | upper | 2025 | 0.14887
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | upper | 2050 | 0.14887
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2020 | 0.18077
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2025 | 0.18077
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2030 | 0.15951
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2040 | 0.15951
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2050 | 0.15951
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2025 | 0.14887
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2050 | 0.1276
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2025 | 0.14887
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2050 | 0.14887
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | ctrl | 2020 | 10.6337
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | ctrl | 2025 | 10.6337
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | ctrl | 2030 | 10.6337
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | ctrl | 2040 | 10.6337
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | ctrl | 2050 | 10.6337
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | lower | 2025 | 5.3169
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | lower | 2050 | 2.1267
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | upper | 2025 | 21.2675
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | upper | 2050 | 21.2675
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2020 | 2.3288
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2025 | 2.3288
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2030 | 2.6691
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2040 | 2.3288
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2050 | 2.8392
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | lower | 2025 | 2.3288
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | lower | 2050 | 2.3288
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | upper | 2025 | 3.9238
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | upper | 2050 | 2.3288
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | upper | 2025 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | upper | 2050 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2020 | 2.3288
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2025 | 2.3288
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2030 | 2.6691
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2040 | 2.3288
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2050 | 2.8392
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | lower | 2025 | 2.3288
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | lower | 2050 | 2.3288
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | upper | 2025 | 3.9238
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | upper | 2050 | 2.3288
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | lower | 2025 | 0.2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | lower | 2050 | 0.2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | ctrl | 2020 | 0.25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | ctrl | 2025 | 0.25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | ctrl | 2030 | 0.25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | ctrl | 2040 | 0.25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | ctrl | 2050 | 0.25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2020 | 0.05
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2025 | 0.05
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2030 | 0.05
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2040 | 0.05
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2050 | 0.05
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | lower | 2025 | 0.05
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | lower | 2050 | 0.05
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | upper | 2025 | 0.2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | upper | 2050 | 0.2
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | ctrl | 2020 | 0.01
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | ctrl | 2025 | 0.01
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | ctrl | 2030 | 0.01
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | ctrl | 2040 | 0.01
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | ctrl | 2050 | 0.01
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | lower | 2025 | 0.01
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | lower | 2050 | 0.01
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | upper | 2025 | 0.01
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | [1, 14, 15] | upper | 2050 | 0.01
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | ctrl | 2020 | 0.7
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | ctrl | 2025 | 0.7
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | ctrl | 2030 | 0.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | ctrl | 2040 | 0.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | ctrl | 2050 | 0.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | lower | 2025 | 0.5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | lower | 2050 | 0.4
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | [F, G] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | upper | 2025 | 0.05
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | upper | 2050 | 0.05
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2020 | 10
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2025 | 10
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2030 | 10
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2040 | 10
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2050 | 10
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2025 | 5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2050 | 5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2025 | 20
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2050 | 20
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2020 | 3.8
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2025 | 3.8
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2030 | 3.85
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2040 | 3.9
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2050 | 3.9
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | lower | 2025 | 3.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | lower | 2050 | 3.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | upper | 2025 | 4
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, B, D] | [1, 14, 15] | upper | 2050 | 4.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2020 | 3.5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2025 | 3.5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2030 | 3.55
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2040 | 3.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2050 | 3.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | lower | 2025 | 3.3
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | lower | 2050 | 3.3
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | upper | 2025 | 3.7
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, C] | [1, 14, 15] | upper | 2050 | 3.8
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | lower | 2025 | 0.5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | lower | 2050 | 0.5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | upper | 2025 | 2
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | upper | 2050 | 2
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | ctrl | 2020 | 0.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | ctrl | 2025 | 0.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | ctrl | 2030 | 0.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | ctrl | 2040 | 0.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | ctrl | 2050 | 0.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | lower | 2025 | 0.4
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | lower | 2050 | 0.4
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | upper | 2025 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | Q | [15, 18] | upper | 2050 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2020 | 25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2025 | 25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2030 | 25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2040 | 25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2050 | 25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | lower | 2025 | 15
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | lower | 2050 | 15
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | upper | 2025 | 40
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | upper | 2050 | 40
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | ctrl | 2020 | 2126.7454
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | ctrl | 2025 | 2126.7454
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | ctrl | 2030 | 2126.7454
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | ctrl | 2040 | 2126.7454
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | ctrl | 2050 | 2126.7454
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | lower | 2025 | 1063.3727
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | lower | 2050 | 1063.3727
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | upper | 2025 | 3190.1182
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M | [1, 14, 15] | upper | 2050 | 5316.8636
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2020 | 0.9145
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2025 | 0.9145
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2030 | 0.80816
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2040 | 0.80816
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2050 | 0.80816
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | lower | 2025 | 0.71246
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | lower | 2050 | 0.71246
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | upper | 2025 | 1.2122
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, K, L, P, Q] | [1, 14, 15] | upper | 2050 | 1.2122
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2020 | 0.72309
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2025 | 0.72309
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2030 | 0.64866
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2040 | 0.64866
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2050 | 0.64866
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2025 | 0.56359
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2050 | 0.56359
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2025 | 0.96767
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2050 | 0.96767
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | ctrl | 2020 | 0.021267
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | ctrl | 2025 | 0.021267
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | ctrl | 2030 | 0.021267
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | ctrl | 2040 | 0.021267
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | ctrl | 2050 | 0.021267
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | lower | 2025 | 0.010634
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | lower | 2050 | 0.010634
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | upper | 2025 | 0.11697
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | K | [1, 14, 15] | upper | 2050 | 0.11697
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2020 | 0.15951
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2025 | 0.15951
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2030 | 0.14887
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2040 | 0.14887
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2050 | 0.14887
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2025 | 0.1276
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2050 | 0.1276
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2025 | 0.11697
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2050 | 0.11697
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | ctrl | 2020 | 10.6337
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | ctrl | 2025 | 10.6337
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | ctrl | 2030 | 10.6337
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | ctrl | 2040 | 10.6337
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | ctrl | 2050 | 10.6337
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | lower | 2025 | 5.3169
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | lower | 2050 | 2.1267
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | upper | 2025 | 21.2675
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | O | 15 | upper | 2050 | 21.2675
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2020 | 1.7971
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2025 | 1.7971
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2030 | 1.7971
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2040 | 1.7971
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2050 | 1.7971
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | lower | 2025 | 1.0634
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | lower | 2050 | 1.0634
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | upper | 2025 | 2.8605
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | upper | 2050 | 2.8605
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | upper | 2025 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [E, N] | [1, 14, 15] | upper | 2050 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2020 | 1.7971
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2025 | 1.7971
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2030 | 1.7971
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2040 | 1.7971
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2050 | 1.7971
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | lower | 2025 | 1.5951
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | lower | 2050 | 1.5951
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | upper | 2025 | 2.8605
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | upper | 2050 | 2.8605
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | lower | 2025 | 0.2
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | lower | 2050 | 0.2
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | [H, I] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | ctrl | 2020 | 0.25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | ctrl | 2025 | 0.25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | ctrl | 2030 | 0.25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | ctrl | 2040 | 0.25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | ctrl | 2050 | 0.25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | [H, J] | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2020 | 0.05
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2025 | 0.05
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2030 | 0.05
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2040 | 0.05
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2050 | 0.05
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | lower | 2025 | 0.05
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | lower | 2050 | 0.05
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | H | [1, 9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [1, 9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | upper | 2025 | 0.2
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | H | [9, 14, 15] | upper | 2050 | 0.2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2020 | 0.01
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2025 | 0.01
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2030 | 0.01
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2040 | 0.01
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2050 | 0.01
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | lower | 2025 | 0.01
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | lower | 2050 | 0.01
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | upper | 2025 | 0.01
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | upper | 2050 | 0.01
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2020 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2025 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2030 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2040 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2050 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | lower | 2025 | 0.3
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | lower | 2050 | 0.3
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | upper | 2025 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | upper | 2050 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2020 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2025 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2030 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2040 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2050 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2025 | 0.3
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2050 | 0.2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2025 | 1.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2050 | 1.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2020 | 4.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2025 | 4.2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2030 | 4.3
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2040 | 4.4
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2050 | 4.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | lower | 2025 | 4.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | lower | 2050 | 4.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | upper | 2025 | 4.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | upper | 2050 | 4.8
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2020 | 4
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2025 | 4.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2030 | 4.2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2040 | 4.3
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2050 | 4.4
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | lower | 2025 | 4
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | lower | 2050 | 4
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | upper | 2025 | 4.3
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | upper | 2050 | 4.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | lower | 2025 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | lower | 2050 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | upper | 2025 | 2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | upper | 2050 | 2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | ctrl | 2020 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | ctrl | 2025 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | ctrl | 2030 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | ctrl | 2040 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | ctrl | 2050 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | lower | 2025 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | lower | 2050 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | upper | 2025 | 0.2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | upper | 2050 | 0.2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2020 | 25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2025 | 25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2030 | 25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2040 | 25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2050 | 25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | lower | 2025 | 15
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | lower | 2050 | 15
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | upper | 2025 | 40
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | upper | 2050 | 40
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2020 | 2126.7454
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2025 | 2126.7454
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2030 | 2126.7454
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2040 | 2126.7454
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2050 | 2126.7454
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | lower | 2025 | 1063.3727
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | lower | 2050 | 1063.3727
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | upper | 2025 | 3190.1182
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | upper | 2050 | 5316.8636
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2020 | 1.3186
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2025 | 1.3186
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2030 | 1.2122
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2040 | 1.2122
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2050 | 1.2122
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | lower | 2025 | 1.0102
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | lower | 2050 | 1.0102
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | upper | 2025 | 2.0204
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | upper | 2050 | 2.0204
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2020 | 0.98894
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2025 | 0.98894
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2030 | 0.9145
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2040 | 0.9145
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2050 | 0.9145
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2025 | 0.75499
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2050 | 0.75499
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2025 | 1.5206
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2050 | 1.5206
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2020 | 0.021267
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2025 | 0.021267
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2030 | 0.021267
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2040 | 0.021267
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2050 | 0.021267
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | lower | 2025 | 0.021267
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | lower | 2050 | 0.021267
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | upper | 2025 | 0.20204
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | upper | 2050 | 0.20204
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2020 | 0.23394
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2025 | 0.23394
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2030 | 0.22331
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2040 | 0.22331
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2050 | 0.22331
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2025 | 0.18077
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2050 | 0.18077
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2025 | 0.20204
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2050 | 0.20204
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2020 | 10.6337
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2025 | 10.6337
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2030 | 10.6337
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2040 | 10.6337
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2050 | 10.6337
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | lower | 2025 | 5.3169
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | lower | 2050 | 2.1267
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | upper | 2025 | 21.2675
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | upper | 2050 | 21.2675
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2020 | 2.8605
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2025 | 2.8605
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2030 | 2.8605
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2040 | 3.2858
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2050 | 3.3709
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | lower | 2025 | 1.7971
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | lower | 2050 | 2.8605
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | upper | 2025 | 2.8605
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | upper | 2050 | 3.3709
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | upper | 2025 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | upper | 2050 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2020 | 2.8605
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2025 | 2.8605
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2030 | 2.8605
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2040 | 3.2858
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2050 | 3.3709
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | lower | 2025 | 1.7971
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | lower | 2050 | 2.8605
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | upper | 2025 | 2.8605
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | upper | 2050 | 3.3709
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | lower | 2025 | 0.2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | lower | 2050 | 0.2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2020 | 0.25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2025 | 0.25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2030 | 0.25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2040 | 0.25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2050 | 0.25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2020 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2025 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2030 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2040 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2050 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | lower | 2025 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | lower | 2050 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | upper | 2025 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | upper | 2050 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | upper | 2025 | 0.2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | upper | 2050 | 0.2
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2020 | 0.01
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2025 | 0.01
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2030 | 0.01
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2040 | 0.01
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2050 | 0.01
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | lower | 2025 | 0.01
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | lower | 2050 | 0.01
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | upper | 2025 | 0.01
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | upper | 2050 | 0.01
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2020 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2025 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2030 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2040 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2050 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | lower | 2025 | 0.3
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | lower | 2050 | 0.3
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | upper | 2025 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | upper | 2050 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2020 | 3
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2025 | 3
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2030 | 3
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2040 | 3
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2050 | 3
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2025 | 1.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2050 | 1.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2025 | 5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2050 | 5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2020 | 4.6
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2025 | 4.7
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2030 | 4.8
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2040 | 4.9
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2050 | 5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | lower | 2025 | 4.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | lower | 2050 | 4.6
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | upper | 2025 | 4.9
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | upper | 2050 | 5.2
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2020 | 4.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2025 | 4.6
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2030 | 4.7
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2040 | 4.8
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2050 | 4.9
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | lower | 2025 | 4.4
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | lower | 2050 | 4.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | upper | 2025 | 4.8
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | upper | 2050 | 5.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | lower | 2025 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | lower | 2050 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | upper | 2025 | 2
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | upper | 2050 | 2
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | ctrl | 2020 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | ctrl | 2025 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | ctrl | 2030 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | ctrl | 2040 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | ctrl | 2050 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | lower | 2025 | 0.03
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | lower | 2050 | 0.03
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | upper | 2025 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | upper | 2050 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2020 | 25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2025 | 25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2030 | 25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2040 | 25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2050 | 25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | lower | 2025 | 15
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | lower | 2050 | 15
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | upper | 2025 | 40
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | upper | 2050 | 40
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2020 | 2126.7454
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2025 | 2126.7454
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2030 | 2126.7454
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2040 | 2126.7454
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2050 | 2126.7454
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | lower | 2025 | 1063.3727
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | lower | 2050 | 1063.3727
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | upper | 2025 | 3190.1182
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | upper | 2050 | 5316.8636
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2020 | 0.9145
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2025 | 0.9145
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2030 | 0.80816
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2040 | 0.80816
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2050 | 0.80816
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | lower | 2025 | 0.71246
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | lower | 2050 | 0.71246
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | upper | 2025 | 1.2122
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | upper | 2050 | 1.2122
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2020 | 0.72309
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2025 | 0.72309
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2030 | 0.64866
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2040 | 0.64866
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2050 | 0.64866
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2025 | 0.56359
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2050 | 0.56359
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2025 | 0.96767
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2050 | 0.96767
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2020 | 0.021267
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2025 | 0.021267
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2030 | 0.021267
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2040 | 0.021267
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2050 | 0.021267
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | lower | 2025 | 0.010634
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | lower | 2050 | 0.010634
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | upper | 2025 | 0.11697
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | upper | 2050 | 0.11697
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2020 | 0.15951
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2025 | 0.15951
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2030 | 0.14887
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2040 | 0.14887
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2050 | 0.14887
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2025 | 0.1276
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2050 | 0.1276
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2025 | 0.11697
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2050 | 0.11697
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2020 | 10.6337
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2025 | 10.6337
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2030 | 10.6337
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2040 | 10.6337
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2050 | 10.6337
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | lower | 2025 | 5.3169
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | lower | 2050 | 2.1267
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | upper | 2025 | 21.2675
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | upper | 2050 | 21.2675
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2020 | 2.3288
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2025 | 2.3288
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2030 | 2.6691
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2040 | 2.3288
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2050 | 2.8392
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | lower | 2025 | 2.3288
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | lower | 2050 | 2.3075
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | upper | 2025 | 2.3288
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | upper | 2050 | 2.3288
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | upper | 2025 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | upper | 2050 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2020 | 2.3288
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2025 | 2.3288
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2030 | 2.6691
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2040 | 2.3288
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2050 | 2.8392
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | lower | 2025 | 2.3288
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | lower | 2050 | 2.3075
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | upper | 2025 | 2.3288
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | upper | 2050 | 2.3288
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | lower | 2025 | 0.2
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | lower | 2050 | 0.2
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2020 | 0.25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2025 | 0.25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2030 | 0.25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2040 | 0.25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2050 | 0.25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2020 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2025 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2030 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2040 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2050 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | lower | 2025 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | lower | 2050 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | upper | 2025 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | upper | 2050 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | upper | 2025 | 0.2
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | upper | 2050 | 0.2
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2020 | 0.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2025 | 0.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2030 | 0.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2040 | 0.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2050 | 0.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | lower | 2025 | 0.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | lower | 2050 | 0.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | upper | 2025 | 0.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | upper | 2050 | 0.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2020 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2025 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2030 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2040 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2050 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | lower | 2025 | 0.3
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | lower | 2050 | 0.3
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | upper | 2025 | 0.05
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | upper | 2050 | 0.05
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2020 | 10
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2025 | 10
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2030 | 10
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2040 | 10
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2050 | 10
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2025 | 5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2050 | 5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2025 | 20
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2050 | 20
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2020 | 5.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2025 | 5.2
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2030 | 5.3
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2040 | 5.4
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2050 | 5.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | lower | 2025 | 5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | lower | 2050 | 5.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | upper | 2025 | 5.3
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, A1, C, D] | [1, 14, 15] | upper | 2050 | 5.7
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2020 | 5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2025 | 5.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2030 | 5.2
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2040 | 5.3
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2050 | 5.4
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | lower | 2025 | 4.9
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | lower | 2050 | 5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | upper | 2025 | 5.2
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, A1, B, D] | [1, 14, 15] | upper | 2050 | 5.6
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | lower | 2025 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | lower | 2050 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | upper | 2025 | 2
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | upper | 2050 | 2
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | ctrl | 2020 | 0.03
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | ctrl | 2025 | 0.03
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | ctrl | 2030 | 0.03
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | ctrl | 2040 | 0.03
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | ctrl | 2050 | 0.03
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | lower | 2025 | 0.02
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | lower | 2050 | 0.02
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | upper | 2025 | 0.06
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  | [15, 18] | upper | 2050 | 0.06
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2020 | 25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2025 | 25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2030 | 25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2040 | 25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2050 | 25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | lower | 2025 | 15
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | lower | 2050 | 15
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | upper | 2025 | 40
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | upper | 2050 | 40
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2020 | 2126.7454
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2025 | 2126.7454
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2030 | 2126.7454
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2040 | 2126.7454
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2050 | 2126.7454
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | lower | 2025 | 1063.3727
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | lower | 2050 | 1063.3727
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | upper | 2025 | 3190.1182
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | upper | 2050 | 5316.8636
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2020 | 0.71246
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2025 | 0.71246
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2030 | 0.60612
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2040 | 0.60612
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2050 | 0.60612
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | lower | 2025 | 0.51042
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | lower | 2050 | 0.51042
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | upper | 2025 | 1.0102
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | upper | 2050 | 1.0102
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2020 | 0.56359
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2025 | 0.56359
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2030 | 0.48915
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2040 | 0.48915
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2050 | 0.48915
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2025 | 0.40408
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2050 | 0.40408
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2025 | 0.80816
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2050 | 0.80816
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2020 | 0.010634
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2025 | 0.010634
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2030 | 0.010634
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2040 | 0.010634
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2050 | 0.010634
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | lower | 2025 | 0.010634
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | lower | 2050 | 0.010634
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | upper | 2025 | 0.10634
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | upper | 2050 | 0.10634
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2020 | 0.1276
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2025 | 0.1276
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2030 | 0.10634
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2040 | 0.10634
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2050 | 0.10634
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2025 | 0.095704
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2050 | 0.095704
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2025 | 0.10634
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2050 | 0.10634
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2020 | 10.6337
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2025 | 10.6337
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2030 | 10.6337
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2040 | 10.6337
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2050 | 10.6337
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | lower | 2025 | 5.3169
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | lower | 2050 | 2.1267
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | upper | 2025 | 21.2675
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | upper | 2050 | 21.2675
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2020 | 1.7971
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2025 | 1.7971
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2030 | 2.1374
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2040 | 2.2224
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2050 | 1.7971
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | lower | 2025 | 1.2654
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | lower | 2050 | 1.7971
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | upper | 2025 | 2.3288
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | upper | 2050 | 2.8392
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | upper | 2025 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | [D, M] | [1, 14, 15] | upper | 2050 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2020 | 1.7971
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2025 | 1.7971
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2030 | 2.1374
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2040 | 2.2224
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2050 | 1.7971
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | lower | 2025 | 1.2654
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | lower | 2050 | 1.7971
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | upper | 2025 | 2.3288
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | upper | 2050 | 2.8392
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | lower | 2025 | 0.2
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | lower | 2050 | 0.2
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2020 | 0.25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2025 | 0.25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2030 | 0.25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2040 | 0.25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2050 | 0.25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2020 | 0.05
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2025 | 0.05
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2030 | 0.05
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2040 | 0.05
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2050 | 0.05
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | lower | 2025 | 0.05
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | lower | 2050 | 0.05
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | upper | 2025 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | upper | 2050 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | upper | 2025 | 0.2
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | upper | 2050 | 0.2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2020 | 0.01
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2025 | 0.01
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2030 | 0.01
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2040 | 0.01
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | ctrl | 2050 | 0.01
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | lower | 2025 | 0.01
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | lower | 2050 | 0.01
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | upper | 2025 | 0.01
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | D | [1, 14, 15] | upper | 2050 | 0.01
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | lower | 2025 | 0.7
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | lower | 2050 | 0.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | upper | 2025 | 1.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Construction time [years] | years |  | [E, F] | [9, 14, 15] | upper | 2050 | 1.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | upper | 2025 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Forced outage [] |  |  |  | [1, 14, 15] | upper | 2050 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2020 | 20
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2025 | 20
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2030 | 20
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2040 | 20
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2050 | 20
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2025 | 10
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2050 | 10
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2025 | 50
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2050 | 100
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, C, D] | [1, 14, 15] | ctrl | 2020 | 3.7
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, C, D] | [1, 14, 15] | ctrl | 2025 | 3.7
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, C, D] | [1, 14, 15] | ctrl | 2030 | 3.7
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, C, D] | [1, 14, 15] | ctrl | 2040 | 3.8
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, C, D] | [1, 14, 15] | ctrl | 2050 | 3.8
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, C, D] | [1, 14, 15] | lower | 2025 | 3.6
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, C, D] | [1, 14, 15] | lower | 2050 | 3.7
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, C, D] | [1, 14, 15] | upper | 2025 | 3.8
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | [A, C, D] | [1, 14, 15] | upper | 2050 | 3.9
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, D] | [1, 14, 15] | ctrl | 2020 | 3.4
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, D] | [1, 14, 15] | ctrl | 2025 | 3.4
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, D] | [1, 14, 15] | ctrl | 2030 | 3.4
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, D] | [1, 14, 15] | ctrl | 2040 | 3.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, D] | [1, 14, 15] | ctrl | 2050 | 3.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, D] | [1, 14, 15] | lower | 2025 | 3.3
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, D] | [1, 14, 15] | lower | 2050 | 3.4
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, D] | [1, 14, 15] | upper | 2025 | 3.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | [A, B, D] | [1, 14, 15] | upper | 2050 | 3.6
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | lower | 2025 | 0.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | lower | 2050 | 0.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | upper | 2025 | 2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 14, 15] | upper | 2050 | 2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | O | [15, 18] | ctrl | 2020 | 0.03
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | O | [15, 18] | ctrl | 2025 | 0.03
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | O | [15, 18] | ctrl | 2030 | 0.03
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | O | [15, 18] | ctrl | 2040 | 0.03
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | O | [15, 18] | ctrl | 2050 | 0.03
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | O | [15, 18] | lower | 2025 | 0.02
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | O | [15, 18] | lower | 2050 | 0.02
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | O | [15, 18] | upper | 2025 | 0.06
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | O | [15, 18] | upper | 2050 | 0.06
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2020 | 25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2025 | 25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2030 | 25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2040 | 25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2050 | 25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | lower | 2025 | 15
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | lower | 2050 | 15
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | upper | 2025 | 40
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 9, 10, 14, 15] | upper | 2050 | 40
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2020 | 4253.4909
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2025 | 4253.4909
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2030 | 4253.4909
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2040 | 4253.4909
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | ctrl | 2050 | 4253.4909
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | lower | 2025 | 2126.7454
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | lower | 2050 | 2126.7454
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | upper | 2025 | 5316.8636
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | L | [1, 14, 15] | upper | 2050 | 5316.8636
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2020 | 0.51042
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2025 | 0.51042
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2030 | 0.40408
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2040 | 0.40408
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | ctrl | 2050 | 0.40408
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | lower | 2025 | 0.30838
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | lower | 2050 | 0.30838
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | upper | 2025 | 1.0634
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, J, K, O] | [1, 14, 15] | upper | 2050 | 1.0634
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2020 | 0.42535
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2025 | 0.42535
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2030 | 0.34028
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2040 | 0.34028
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2050 | 0.34028
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2025 | 0.25521
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2050 | 0.25521
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2025 | 0.90387
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2050 | 0.90387
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | upper | 2025 | 0.10634
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (grid connection) [MEUR/MW_e] | MEUR/MW_e | 2020 | J | [1, 14, 15] | upper | 2050 | 0.10634
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2020 | 0.074436
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2025 | 0.074436
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2030 | 0.063802
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2040 | 0.063802
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | ctrl | 2050 | 0.063802
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2025 | 0.042535
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | lower | 2050 | 0.042535
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2025 | 0.053169
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | A | [1, 14, 15] | upper | 2050 | 0.053169
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2020 | 10.6337
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2025 | 10.6337
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2030 | 10.6337
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2040 | 10.6337
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | ctrl | 2050 | 10.6337
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | lower | 2025 | 5.3169
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | lower | 2050 | 2.1267
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | upper | 2025 | 21.2675
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | N | 15 | upper | 2050 | 21.2675
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2020 | 1.2654
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2025 | 1.2654
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2030 | 1.6057
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2040 | 1.6908
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | ctrl | 2050 | 1.7758
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | lower | 2025 | 1.2654
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | lower | 2050 | 1.5632
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | upper | 2025 | 1.7971
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  | [1, 14, 15] | upper | 2050 | 1.2654
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | upper | 2025 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M | [1, 14, 15] | upper | 2050 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2020 | 1.2654
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2025 | 1.2654
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2030 | 1.6057
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2040 | 1.6908
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | ctrl | 2050 | 1.7758
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | lower | 2025 | 1.2654
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | lower | 2050 | 1.5632
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | upper | 2025 | 1.7971
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | L | [1, 14, 15] | upper | 2050 | 1.2654
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2020 | 2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2025 | 2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2030 | 2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2040 | 2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | ctrl | 2050 | 2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | lower | 2025 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | lower | 2050 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | upper | 2025 | 3
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Cold start-up time [hours] | hours |  | [G, H] | [9, 14, 15] | upper | 2050 | 2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2020 | 0.25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2025 | 0.25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2030 | 0.25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2040 | 0.25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | ctrl | 2050 | 0.25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Minimum load (of full load) [] |  |  | [G, I] | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2020 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2025 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2030 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2040 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2050 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | lower | 2025 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | lower | 2050 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | upper | 2025 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | [1, 9, 14, 15] | upper | 2050 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2020 | 0.2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2025 | 0.2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2030 | 0.2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2040 | 0.2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | ctrl | 2050 | 0.2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | upper | 2025 | 0.3
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Regulation ability | Warm start-up time [hours] | hours |  | G | [9, 14, 15] | upper | 2050 | 0.3
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | 3 | ctrl | 2015 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | 3 | ctrl | 2020 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | 3 | ctrl | 2030 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | 3 | ctrl | 2050 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | 3 | lower | 2020 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | 3 | lower | 2050 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | 3 | upper | 2020 | 0.03
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E | 3 | upper | 2050 | 0.03
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2015 | 0.5
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 0.5
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 0.5
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 0.5
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Construction time [years] | years |  |  |  | lower | 2020 | 0.3
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Construction time [years] | years |  |  |  | lower | 2050 | 0.3
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Construction time [years] | years |  |  |  | upper | 2020 | 0.7
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Construction time [years] | years |  |  |  | upper | 2050 | 0.7
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Forced outage [] |  |  | C |  | ctrl | 2015 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Forced outage [] |  |  | C |  | ctrl | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Forced outage [] |  |  | C |  | ctrl | 2030 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Forced outage [] |  |  | C |  | ctrl | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Forced outage [] |  |  | C |  | lower | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Forced outage [] |  |  | C |  | lower | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Forced outage [] |  |  | C |  | upper | 2020 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Forced outage [] |  |  | C |  | upper | 2050 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, A1] | 13 | ctrl | 2015 | 12
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, A1] | 13 | ctrl | 2020 | 12
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, A1] | 13 | ctrl | 2030 | 12
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, A1] | 13 | ctrl | 2050 | 12
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, A1] | 13 | lower | 2020 | 12
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, A1] | 13 | lower | 2050 | 12
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, A1] | 13 | upper | 2020 | 20
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [A, A1] | 13 | upper | 2050 | 30
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | B | 4 | ctrl | 2015 | 1.7
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | B | 4 | ctrl | 2020 | 1.71
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | B | 4 | ctrl | 2030 | 1.73
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | B | 4 | ctrl | 2050 | 1.75
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | B | 4 | lower | 2020 | 1.7
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | B | 4 | lower | 2050 | 1.7
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | B | 4 | upper | 2020 | 1.8
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | B | 4 | upper | 2050 | 1.8
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | D |  | ctrl | 2015 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | D |  | ctrl | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | D |  | ctrl | 2030 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | D |  | ctrl | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | D |  | lower | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | D |  | lower | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | D |  | upper | 2020 | 1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | D |  | upper | 2050 | 1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2015 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2020 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2030 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | ctrl | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | lower | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | lower | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | upper | 2020 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  |  |  | upper | 2050 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 3 | ctrl | 2015 | 25
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 3 | ctrl | 2020 | 25
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 3 | ctrl | 2030 | 25
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 3 | ctrl | 2050 | 25
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 3 | lower | 2020 | 15
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 3 | lower | 2050 | 15
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 3 | upper | 2020 | 30
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 3 | upper | 2050 | 30
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2015 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | lower | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | lower | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | upper | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | upper | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2015 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | lower | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | lower | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | upper | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | upper | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2015 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | lower | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | lower | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | upper | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | upper | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2015 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  |  | lower | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  |  | lower | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  |  | upper | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  |  | upper | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 | 3 | ctrl | 2015 | 2126.7454
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 | 3 | ctrl | 2020 | 2126.7454
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 | 3 | ctrl | 2030 | 2126.7454
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 | 3 | ctrl | 2050 | 2126.7454
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 | 3 | lower | 2020 | 1063.3727
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 | 3 | lower | 2050 | 1063.3727
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 | 3 | upper | 2020 | 3190.1182
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | 0 | 3 | upper | 2050 | 3190.1182
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, A1] | 3 | ctrl | 2015 | 0.63802
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, A1] | 3 | ctrl | 2020 | 0.59549
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, A1] | 3 | ctrl | 2030 | 0.54232
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, A1] | 3 | ctrl | 2050 | 0.48915
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, A1] | 3 | lower | 2020 | 0.42535
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, A1] | 3 | lower | 2050 | 0.42535
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, A1] | 3 | upper | 2020 | 0.8507
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [A, A1] | 3 | upper | 2050 | 0.8507
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | 3 | ctrl | 2015 | 53.1686
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | 3 | ctrl | 2020 | 53.1686
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | 3 | ctrl | 2030 | 53.1686
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | 3 | ctrl | 2050 | 53.1686
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | 3 | lower | 2020 | 31.9012
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | 3 | lower | 2050 | 31.9012
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | 3 | upper | 2020 | 74.4361
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | 3 | upper | 2050 | 74.4361
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | 3 | ctrl | 2015 | 53.1686
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | 3 | ctrl | 2020 | 53.1686
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | 3 | ctrl | 2030 | 53.1686
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | 3 | ctrl | 2050 | 53.1686
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | 3 | lower | 2020 | 31.9012
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | 3 | lower | 2050 | 31.9012
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | 3 | upper | 2020 | 74.4361
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | 3 | upper | 2050 | 74.4361
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | ctrl | 2015 | 0.95704
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | ctrl | 2020 | 1.0421
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | ctrl | 2030 | 1.3292
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | ctrl | 2050 | 1.5206
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | lower | 2020 | 1.0634
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | lower | 2050 | 1.4887
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | upper | 2020 | 2.6584
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | upper | 2050 | 0.31901
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | E |  | ctrl | 2015 | 0.63802
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | E |  | ctrl | 2020 | 0.74436
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | E |  | ctrl | 2030 | 1.0634
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | E |  | ctrl | 2050 | 1.276
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | E |  | lower | 2020 | 0.74436
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | E |  | lower | 2050 | 1.276
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | E |  | upper | 2020 | 2.2331
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | E |  | upper | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 | 3 | ctrl | 2015 | 0.31901
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 | 3 | ctrl | 2020 | 0.29774
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 | 3 | ctrl | 2030 | 0.26584
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 | 3 | ctrl | 2050 | 0.24458
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 | 3 | lower | 2020 | 0.31901
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 | 3 | lower | 2050 | 0.21267
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 | 3 | upper | 2020 | 0.42535
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 | 3 | upper | 2050 | 0.31901
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2015 | 0.5
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0.5
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0.5
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0.5
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2020 | 0.25
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0.25
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2020 | 2
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 2
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2020 | 0.1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2050 | 0.1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2020 | 0.1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2050 | 0.1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2015 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2020 | 1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E, F, M | 1 | ctrl | 2020 | 0.029
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E, F, M | 1 | ctrl | 2025 | 0.029
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E, F, M | 1 | ctrl | 2030 | 0.029
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E, F, M | 1 | ctrl | 2040 | 0.029
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E, F, M | 1 | ctrl | 2050 | 0.029
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E, F, M | 1 | lower | 2025 | 0.029
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E, F, M | 1 | lower | 2050 | 0.029
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E, F, M | 1 | upper | 2025 | 0.029
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | E, F, M | 1 | upper | 2050 | 0.029
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | H, I, M | 1 | ctrl | 2020 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | H, I, M | 1 | ctrl | 2025 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | H, I, M | 1 | ctrl | 2030 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | H, I, M | 1 | ctrl | 2040 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | H, I, M | 1 | ctrl | 2050 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | H, I, M | 1 | lower | 2025 | 1.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | H, I, M | 1 | lower | 2050 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | H, I, M | 1 | upper | 2025 | 3
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Construction time [years] | years |  | H, I, M | 1 | upper | 2050 | 3
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  | M | 1 | ctrl | 2020 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  | M | 1 | ctrl | 2025 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  | M | 1 | ctrl | 2030 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  | M | 1 | ctrl | 2040 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  | M | 1 | ctrl | 2050 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  | M | 1 | lower | 2025 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  | M | 1 | lower | 2050 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  | M | 1 | upper | 2025 | 0.05
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Forced outage [] |  |  | M | 1 | upper | 2050 | 0.05
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A,B, M | 1 | ctrl | 2020 | 65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A,B, M | 1 | ctrl | 2025 | 65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A,B, M | 1 | ctrl | 2030 | 65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A,B, M | 1 | ctrl | 2040 | 65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A,B, M | 1 | ctrl | 2050 | 65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A,B, M | 1 | lower | 2025 | 30
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A,B, M | 1 | lower | 2050 | 30
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A,B, M | 1 | upper | 2025 | 150
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | A,B, M | 1 | upper | 2050 | 300
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | C, D, F, M, V | 1 | ctrl | 2020 | 3.01
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | C, D, F, M, V | 1 | ctrl | 2025 | 3.01
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | C, D, F, M, V | 1 | ctrl | 2030 | 3.01
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | C, D, F, M, V | 1 | ctrl | 2040 | 3.11
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | C, D, F, M, V | 1 | ctrl | 2050 | 3.11
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | C, D, F, M, V | 1 | lower | 2025 | 2.9
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | C, D, F, M, V | 1 | lower | 2050 | 3
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | C, D, F, M, V | 1 | upper | 2025 | 3.1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | C, D, F, M, V | 1 | upper | 2050 | 3.2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | C, D, F, M | 1 | ctrl | 2020 | 3.2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | C, D, F, M | 1 | ctrl | 2025 | 3.2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | C, D, F, M | 1 | ctrl | 2030 | 3.2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | C, D, F, M | 1 | ctrl | 2040 | 3.3
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | C, D, F, M | 1 | ctrl | 2050 | 3.3
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | C, D, F, M | 1 | lower | 2025 | 3.1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | C, D, F, M | 1 | lower | 2050 | 3.2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | C, D, F, M | 1 | upper | 2025 | 3.3
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | C, D, F, M | 1 | upper | 2050 | 3.4
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | M | 1 | ctrl | 2020 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | M | 1 | ctrl | 2025 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | M | 1 | ctrl | 2030 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | M | 1 | ctrl | 2040 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | M | 1 | ctrl | 2050 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | M | 1 | lower | 2025 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | M | 1 | lower | 2050 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | M | 1 | upper | 2025 | 4
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | M | 1 | upper | 2050 | 4
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | M | 1 | ctrl | 2020 | 0.03
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | M | 1 | ctrl | 2025 | 0.03
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | M | 1 | ctrl | 2030 | 0.03
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | M | 1 | ctrl | 2040 | 0.03
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | M | 1 | ctrl | 2050 | 0.03
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | M | 1 | lower | 2025 | 0.02
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | M | 1 | lower | 2050 | 0.02
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | M | 1 | upper | 2025 | 0.06
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | M | 1 | upper | 2050 | 0.06
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  | G,M | 1 | ctrl | 2020 | 25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  | G,M | 1 | ctrl | 2025 | 25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  | G,M | 1 | ctrl | 2030 | 25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  | G,M | 1 | ctrl | 2040 | 25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  | G,M | 1 | ctrl | 2050 | 25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  | G,M | 1 | lower | 2025 | 15
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  | G,M | 1 | lower | 2050 | 15
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  | G,M | 1 | upper | 2025 | 40
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Energy/technical data | Technical lifetime [years] | years |  | G,M | 1 | upper | 2050 | 40
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M, R | 1 | ctrl | 2020 | 2047.35
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M, R | 1 | ctrl | 2025 | 2047.35
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M, R | 1 | ctrl | 2030 | 2047.35
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M, R | 1 | ctrl | 2040 | 2047.35
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M, R | 1 | ctrl | 2050 | 2047.35
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M, R | 1 | lower | 2025 | 1485.15
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M, R | 1 | lower | 2050 | 1485.15
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M, R | 1 | upper | 2025 | 2970.3
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | M, R | 1 | upper | 2050 | 2970.3
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | A, M, R | 1 | ctrl | 2020 | 0.94
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | A, M, R | 1 | ctrl | 2025 | 0.94
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | A, M, R | 1 | ctrl | 2030 | 0.89
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | A, M, R | 1 | ctrl | 2040 | 0.84
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | A, M, R | 1 | ctrl | 2050 | 0.8
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | A, M, R | 1 | lower | 2025 | 0.79
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | A, M, R | 1 | lower | 2050 | 0.65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | A, M, R | 1 | upper | 2025 | 1.4
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | A, M, R | 1 | upper | 2050 | 1.4
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2020 | 0.57
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2025 | 0.57
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2030 | 0.54
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2040 | 0.52
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2050 | 0.49
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | lower | 2025 | 0.45
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | lower | 2050 | 0.4
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | upper | 2025 | 0.86
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | upper | 2050 | 0.86
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2020 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2025 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2030 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2040 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2050 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | lower | 2025 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | lower | 2050 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | upper | 2025 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | upper | 2050 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (other) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2020 | 0.16
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (other) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2025 | 0.16
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (other) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2030 | 0.15
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (other) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2040 | 0.14
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (other) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2050 | 0.14
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (other) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | lower | 2025 | 0.13
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (other) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | lower | 2050 | 0.11
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (other) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | upper | 2025 | 0.24
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (other) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | upper | 2050 | 0.24
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (seawater system) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2020 | 0.2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (seawater system) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2025 | 0.2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (seawater system) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2030 | 0.19
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (seawater system) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2040 | 0.18
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (seawater system) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2050 | 0.17
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (seawater system) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | lower | 2025 | 0.15
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (seawater system) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | lower | 2050 | 0.14
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (seawater system) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | upper | 2025 | 0.3
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Nominal investment (seawater system) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, R | 1 | upper | 2050 | 0.3
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | M, Q | 1 | ctrl | 2020 | 4.95
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | M, Q | 1 | ctrl | 2025 | 4.95
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | M, Q | 1 | ctrl | 2030 | 4.95
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | M, Q | 1 | ctrl | 2040 | 4.95
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | M, Q | 1 | ctrl | 2050 | 4.95
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | M, Q | 1 | lower | 2025 | 2.97
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | M, Q | 1 | lower | 2050 | 2.97
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | M, Q | 1 | upper | 2025 | 14.85
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 | M, Q | 1 | upper | 2050 | 14.85
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2020 | 0.99
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2025 | 0.99
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2030 | 0.99
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2040 | 0.99
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2050 | 0.99
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, R, S | 1 | lower | 2025 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, R, S | 1 | lower | 2050 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, R, S | 1 | upper | 2025 | 1.98
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, R, S | 1 | upper | 2050 | 1.98
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, P | 1 | ctrl | 2020 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, P | 1 | ctrl | 2025 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, P | 1 | ctrl | 2030 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, P | 1 | ctrl | 2040 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, P | 1 | ctrl | 2050 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, P | 1 | lower | 2025 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, P | 1 | lower | 2050 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, P | 1 | upper | 2025 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, P | 1 | upper | 2050 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2020 | 0.99
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2025 | 0.99
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2030 | 0.99
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2040 | 0.99
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2050 | 0.99
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, R, S | 1 | lower | 2025 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, R, S | 1 | lower | 2050 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, R, S | 1 | upper | 2025 | 1.98
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | M, R, S | 1 | upper | 2050 | 1.98
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | K, O, M | 1 | ctrl | 2020 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | K, O, M | 1 | ctrl | 2025 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | K, O, M | 1 | ctrl | 2030 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | K, O, M | 1 | ctrl | 2040 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | K, O, M | 1 | ctrl | 2050 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | K, O, M | 1 | lower | 2025 | 0.25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | K, O, M | 1 | lower | 2050 | 0.25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | K, O, M | 1 | upper | 2025 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  | K, O, M | 1 | upper | 2050 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | K, L, M | 1 | ctrl | 2020 | 0.25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | K, L, M | 1 | ctrl | 2025 | 0.25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | K, L, M | 1 | ctrl | 2030 | 0.25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | K, L, M | 1 | ctrl | 2040 | 0.25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | K, L, M | 1 | ctrl | 2050 | 0.25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | K, L, M | 1 | lower | 2025 | 0.1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | K, L, M | 1 | lower | 2050 | 0.1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | K, L, M | 1 | upper | 2025 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  | K, L, M | 1 | upper | 2050 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J, K, M | 1 | ctrl | 2020 | 0.65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J, K, M | 1 | ctrl | 2025 | 0.65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J, K, M | 1 | ctrl | 2030 | 0.65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J, K, M | 1 | ctrl | 2040 | 0.65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J, K, M | 1 | ctrl | 2050 | 0.65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J, K, M | 1 | lower | 2025 | 0.65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J, K, M | 1 | lower | 2050 | 0.65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J, K, M | 1 | upper | 2025 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | J, K, M | 1 | upper | 2050 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | J, K, M | 1 | ctrl | 2020 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | J, K, M | 1 | ctrl | 2025 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | J, K, M | 1 | ctrl | 2030 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | J, K, M | 1 | ctrl | 2040 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | J, K, M | 1 | ctrl | 2050 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | J, K, M | 1 | lower | 2025 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | J, K, M | 1 | lower | 2050 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | J, K, M | 1 | upper | 2025 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | J, K, M | 1 | upper | 2050 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | K, N, M | 1 | ctrl | 2020 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | K, N, M | 1 | ctrl | 2025 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | K, N, M | 1 | ctrl | 2030 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | K, N, M | 1 | ctrl | 2040 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | K, N, M | 1 | ctrl | 2050 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | K, N, M | 1 | lower | 2025 | 0.25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | K, N, M | 1 | lower | 2050 | 0.25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | K, N, M | 1 | upper | 2025 | 0.75
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  | K, N, M | 1 | upper | 2050 | 0.75
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (grid connection fee) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2020 | 0.05
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (grid connection fee) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2025 | 0.05
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (grid connection fee) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2030 | 0.05
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (grid connection fee) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2040 | 0.05
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (grid connection fee) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2050 | 0.04
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (grid connection fee) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | lower | 2025 | 0.01
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (grid connection fee) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | lower | 2050 | 0.03
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (grid connection fee) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | upper | 2025 | 0.08
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (grid connection fee) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | upper | 2050 | 0.08
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (heatpump building) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2020 | 0.11
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (heatpump building) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2025 | 0.11
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (heatpump building) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2030 | 0.1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (heatpump building) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2040 | 0.1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (heatpump building) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2050 | 0.09
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (heatpump building) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | lower | 2025 | 0.09
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (heatpump building) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | lower | 2050 | 0.05
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (heatpump building) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | upper | 2025 | 0.16
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (heatpump building) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | upper | 2050 | 0.16
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater connection) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2020 | 0.08
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater connection) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2025 | 0.08
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater connection) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2030 | 0.08
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater connection) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2040 | 0.08
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater connection) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2050 | 0.07
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater connection) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | lower | 2025 | 0.07
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater connection) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | lower | 2050 | 0.04
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater connection) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | upper | 2025 | 0.13
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater connection) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | upper | 2050 | 0.13
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater intake) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2020 | 0.05
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater intake) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2025 | 0.05
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater intake) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2030 | 0.05
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater intake) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2040 | 0.05
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater intake) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2050 | 0.05
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater intake) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | lower | 2025 | 0.05
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater intake) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | lower | 2050 | 0.03
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater intake) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | upper | 2025 | 0.08
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater intake) [MEUR/MW_h] | MEUR/MW_h | 2020 | M, T | 1 | upper | 2050 | 0.08
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater piping) [EUR/m] | EUR/m | 2020 | M, T | 1 | ctrl | 2020 | 1663.47
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater piping) [EUR/m] | EUR/m | 2020 | M, T | 1 | ctrl | 2025 | 1663.47
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater piping) [EUR/m] | EUR/m | 2020 | M, T | 1 | ctrl | 2030 | 1580.3
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater piping) [EUR/m] | EUR/m | 2020 | M, T | 1 | ctrl | 2040 | 1497.13
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater piping) [EUR/m] | EUR/m | 2020 | M, T | 1 | ctrl | 2050 | 1413.95
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater piping) [EUR/m] | EUR/m | 2020 | M, T | 1 | lower | 2025 | 1413.95
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater piping) [EUR/m] | EUR/m | 2020 | M, T | 1 | lower | 2050 | 831.74
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater piping) [EUR/m] | EUR/m | 2020 | M, T | 1 | upper | 2025 | 2495.21
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Technology-specific data | Nominal investment (seawater piping) [EUR/m] | EUR/m | 2020 | M, T | 1 | upper | 2050 | 2495.21
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | ctrl | 2015 | 0.005
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | ctrl | 2020 | 0.005
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | ctrl | 2030 | 0.005
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | ctrl | 2050 | 0.005
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | lower | 2020 | 0.001
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | lower | 2050 | 0.001
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | upper | 2020 | 0.005
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | upper | 2050 | 0.005
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2015 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Construction time [years] | years |  |  |  | lower | 2020 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Construction time [years] | years |  |  |  | lower | 2050 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Construction time [years] | years |  |  |  | upper | 2020 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Construction time [years] | years |  |  |  | upper | 2050 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.005
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.005
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2015 | 5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2020 | 5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2030 | 5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2050 | 5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2020 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2050 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2020 | 25
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2050 | 25
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  |  |  | ctrl | 2015 | 0.98
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  |  |  | ctrl | 2020 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  |  |  | ctrl | 2030 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  |  |  | ctrl | 2050 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  |  |  | lower | 2020 | 0.98
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  |  |  | lower | 2050 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  |  |  | upper | 2020 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Heat efficiency (net, annual average) [] |  |  |  |  | upper | 2050 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  |  |  | ctrl | 2015 | 0.98
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  |  |  | ctrl | 2020 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  |  |  | ctrl | 2030 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  |  |  | ctrl | 2050 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  |  |  | lower | 2020 | 0.98
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  |  |  | lower | 2050 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  |  |  | upper | 2020 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Heat efficiency (net, name plate) [] |  |  |  |  | upper | 2050 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 0.2
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 0.2
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 0.2
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 0.2
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 0.2
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 0.2
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 0.2
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 0.2
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2015 | 20
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2020 | 20
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2030 | 20
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2050 | 20
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  |  | lower | 2020 | 20
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  |  | lower | 2050 | 20
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  |  | upper | 2020 | 20
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Energy/technical data | Technical lifetime [years] | years |  |  |  | upper | 2050 | 20
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | ctrl | 2015 | 1169.71
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | ctrl | 2020 | 1137.8088
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | ctrl | 2030 | 1084.6402
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | ctrl | 2050 | 978.3029
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | lower | 2020 | 1063.3727
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | lower | 2030 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | lower | 2050 | 957.0354
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | upper | 2020 | 1169.71
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | upper | 2030 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | upper | 2050 | 1000
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2015 | 0.15951
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2020 | 0.15951
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2030 | 0.14887
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2050 | 0.13824
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | lower | 2020 | 0.10634
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | lower | 2030 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | lower | 2050 | 0.10634
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | upper | 2020 | 0.26584
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | upper | 2030 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | upper | 2050 | 0.25
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2015 | 0.1276
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2020 | 0.1276
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2030 | 0.11697
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2050 | 0.10634
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | lower | 2020 | 0.08507
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | lower | 2030 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | lower | 2050 | 0.08507
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | upper | 2020 | 0.21267
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | upper | 2030 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | upper | 2050 | 0.2
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2015 | 0.031901
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2020 | 0.031901
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2030 | 0.031901
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2050 | 0.031901
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | lower | 2020 | 0.021267
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | lower | 2030 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | lower | 2050 | 0.021267
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | upper | 2020 | 0.053169
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | upper | 2030 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | upper | 2050 | 0.05
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2015 | 0.8507
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2020 | 0.95704
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2030 | 1.0634
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2050 | 1.0634
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | lower | 2020 | 0.53169
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | lower | 2030 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | lower | 2050 | 0.53169
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | upper | 2020 | 0.95704
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | upper | 2030 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | upper | 2050 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2015 | 0.31901
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2020 | 0.31901
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2030 | 0.53169
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2050 | 0.63802
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | lower | 2020 | 0.10634
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | lower | 2030 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | lower | 2050 | 0.10634
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | upper | 2020 | 0.31901
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | upper | 2030 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | upper | 2050 | 0.6
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2015 | 0.53169
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2020 | 0.53169
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2030 | 0.53169
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2050 | 0.42535
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | lower | 2020 | 0.42535
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | lower | 2030 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | lower | 2050 | 0.31901
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | upper | 2020 | 0.53169
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | upper | 2030 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | upper | 2050 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2015 | 0.08
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0.08
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0.08
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0.08
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2020 | 0.08
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0.08
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2020 | 0.08
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0.08
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.05
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.05
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.05
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.05
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2020 | 0.05
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2050 | 0.05
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2020 | 0.05
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2050 | 0.05
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2015 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2020 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2030 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2050 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | lower | 2020 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | lower | 2050 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | upper | 2020 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | upper | 2050 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2015 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2020 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2020 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Technology-specific data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 |  |  | ctrl | 2015 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Technology-specific data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 |  |  | ctrl | 2020 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Technology-specific data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 |  |  | ctrl | 2030 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Technology-specific data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 |  |  | ctrl | 2050 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Technology-specific data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 |  |  | lower | 2020 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Technology-specific data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 |  |  | lower | 2050 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Technology-specific data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 |  |  | upper | 2020 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Technology-specific data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 |  |  | upper | 2050 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | ctrl | 2015 | 0.005
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | ctrl | 2020 | 0.005
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | ctrl | 2030 | 0.005
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | ctrl | 2050 | 0.005
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | lower | 2020 | 0.001
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | lower | 2050 | 0.001
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | upper | 2020 | 0.005
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | upper | 2050 | 0.005
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2015 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Construction time [years] | years |  |  |  | lower | 2020 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Construction time [years] | years |  |  |  | lower | 2050 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Construction time [years] | years |  |  |  | upper | 2020 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Construction time [years] | years |  |  |  | upper | 2050 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2015 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2020 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2030 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Forced outage [] |  |  |  |  | ctrl | 2050 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2020 | 0.005
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Forced outage [] |  |  |  |  | lower | 2050 | 0.005
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2020 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Forced outage [] |  |  |  |  | upper | 2050 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2015 | 5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2020 | 5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2030 | 5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | ctrl | 2050 | 5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2020 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2050 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2020 | 25
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2050 | 25
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  |  |  | ctrl | 2015 | 0.98
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  |  |  | ctrl | 2020 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  |  |  | ctrl | 2030 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  |  |  | ctrl | 2050 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  |  |  | lower | 2020 | 0.98
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  |  |  | lower | 2050 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  |  |  | upper | 2020 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  |  |  | upper | 2050 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  |  |  | ctrl | 2015 | 0.98
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  |  |  | ctrl | 2020 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  |  |  | ctrl | 2030 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  |  |  | ctrl | 2050 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  |  |  | lower | 2020 | 0.98
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  |  |  | lower | 2050 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  |  |  | upper | 2020 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Heat efficiency (net, name plate) [] |  |  |  |  | upper | 2050 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2015 | 0.2
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2020 | 0.2
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2030 | 0.2
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | ctrl | 2050 | 0.2
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2020 | 0.2
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | lower | 2050 | 0.2
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2020 | 0.2
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  |  | upper | 2050 | 0.2
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2015 | 20
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2020 | 20
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2030 | 20
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2050 | 20
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  |  | lower | 2020 | 20
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  |  | lower | 2050 | 20
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  |  | upper | 2020 | 20
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Energy/technical data | Technical lifetime [years] | years |  |  |  | upper | 2050 | 20
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | ctrl | 2015 | 1169.71
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | ctrl | 2020 | 1137.8088
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | ctrl | 2030 | 1084.6402
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | ctrl | 2050 | 978.3029
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | lower | 2020 | 1063.3727
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | lower | 2030 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | lower | 2050 | 957.0354
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | upper | 2020 | 1169.71
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | upper | 2030 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 |  |  | upper | 2050 | 1000
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2015 | 0.074436
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2020 | 0.074436
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2030 | 0.063802
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2050 | 0.063802
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | lower | 2020 | 0.021267
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | lower | 2030 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | lower | 2050 | 0.021267
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | upper | 2020 | 0.18077
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | upper | 2030 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | upper | 2050 | 0.17
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2015 | 0.063802
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2020 | 0.063802
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2030 | 0.053169
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2050 | 0.053169
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | lower | 2020 | 0.021267
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | lower | 2030 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | lower | 2050 | 0.021267
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | upper | 2020 | 0.14887
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | upper | 2030 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | upper | 2050 | 0.14
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2015 | 0.010634
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2020 | 0.010634
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2030 | 0.010634
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | ctrl | 2050 | 0.010634
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | lower | 2020 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | lower | 2030 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | lower | 2050 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | upper | 2020 | 0.031901
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | upper | 2030 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  |  | upper | 2050 | 0.03
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2015 | 0.8507
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2020 | 0.95704
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2030 | 1.0634
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2050 | 1.0634
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | lower | 2020 | 0.53169
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | lower | 2030 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | lower | 2050 | 0.53169
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | upper | 2020 | 0.95704
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | upper | 2030 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | upper | 2050 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2015 | 0.31901
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2020 | 0.31901
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2030 | 0.53169
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2050 | 0.63802
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | lower | 2020 | 0.10634
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | lower | 2030 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | lower | 2050 | 0.10634
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | upper | 2020 | 0.31901
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | upper | 2030 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | upper | 2050 | 0.6
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2015 | 0.53169
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2020 | 0.53169
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2030 | 0.53169
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | ctrl | 2050 | 0.42535
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | lower | 2020 | 0.42535
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | lower | 2030 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | lower | 2050 | 0.31901
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | upper | 2020 | 0.53169
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | upper | 2030 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 |  |  | upper | 2050 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2015 | 0.08
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0.08
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0.08
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0.08
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2020 | 0.08
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  |  |  | lower | 2050 | 0.08
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2020 | 0.08
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Cold start-up time [hours] | hours |  |  |  | upper | 2050 | 0.08
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2015 | 0.05
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2020 | 0.05
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2030 | 0.05
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | ctrl | 2050 | 0.05
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2020 | 0.05
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | lower | 2050 | 0.05
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2020 | 0.05
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Minimum load (of full load) [] |  |  |  |  | upper | 2050 | 0.05
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2015 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2020 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2020 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2020 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2015 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2020 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2030 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2050 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | lower | 2020 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | lower | 2050 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | upper | 2020 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | upper | 2050 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2015 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2020 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2020 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Technology-specific data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 |  |  | ctrl | 2015 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Technology-specific data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 |  |  | ctrl | 2020 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Technology-specific data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 |  |  | ctrl | 2030 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Technology-specific data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 |  |  | ctrl | 2050 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Technology-specific data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 |  |  | lower | 2020 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Technology-specific data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 |  |  | lower | 2050 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Technology-specific data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 |  |  | upper | 2020 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Technology-specific data | Startup cost [EUR/MW_h/startup] | EUR/MW_h/startup | 2020 |  |  | upper | 2050 | 0
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | L | 1 | ctrl | 2015 | 0.0015
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | L | 1 | ctrl | 2020 | 0.0014
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | L | 1 | ctrl | 2030 | 0.0012
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | L | 1 | ctrl | 2050 | 0.001
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | L | 1 | lower | 2020 | 0.0013
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | L | 1 | lower | 2050 | 0.0008
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | L | 1 | upper | 2020 | 0.002
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | L | 1 | upper | 2050 | 0.0015
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Construction time [years] | years |  | F | 9 | ctrl | 2015 | 0.5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Construction time [years] | years |  | F | 9 | ctrl | 2020 | 0.5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Construction time [years] | years |  | F | 9 | ctrl | 2030 | 0.5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Construction time [years] | years |  | F | 9 | ctrl | 2050 | 0.5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Construction time [years] | years |  | F | 9 | lower | 2020 | 0.2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Construction time [years] | years |  | F | 9 | lower | 2050 | 0.2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Construction time [years] | years |  | F | 9 | upper | 2020 | 0.7
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Construction time [years] | years |  | F | 9 | upper | 2050 | 0.7
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 3 | ctrl | 2015 | 0.01
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 3 | ctrl | 2020 | 0.01
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 3 | ctrl | 2030 | 0.01
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 3 | ctrl | 2050 | 0.01
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 3 | lower | 2020 | 0.0008
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 3 | lower | 2050 | 0.0008
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 3 | upper | 2020 | 0.02
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 3 | upper | 2050 | 0.02
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2020 | 0.5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | lower | 2050 | 0.5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2020 | 10
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  |  |  | upper | 2050 | 10
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | B | [1, 3] | ctrl | 2015 | 1.03
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | B | [1, 3] | ctrl | 2020 | 1.03
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | B | [1, 3] | ctrl | 2030 | 1.04
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | B | [1, 3] | ctrl | 2050 | 1.04
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | B | [1, 3] | lower | 2020 | 0.93
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | B | [1, 3] | lower | 2050 | 0.94
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | B | [1, 3] | upper | 2020 | 1.05
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | B | [1, 3] | upper | 2050 | 1.06
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | A | [1, 2, 3] | ctrl | 2015 | 1.05
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | A | [1, 2, 3] | ctrl | 2020 | 1.05
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | A | [1, 2, 3] | ctrl | 2030 | 1.06
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | A | [1, 2, 3] | ctrl | 2050 | 1.06
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | A | [1, 2, 3] | lower | 2020 | 0.95
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | A | [1, 2, 3] | lower | 2050 | 0.96
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | A | [1, 2, 3] | upper | 2020 | 1.07
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Heat efficiency (net, name plate) [] |  |  | A | [1, 2, 3] | upper | 2050 | 1.08
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | F | 3 | ctrl | 2015 | 0.4
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | F | 3 | ctrl | 2020 | 0.4
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | F | 3 | ctrl | 2030 | 0.4
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | F | 3 | ctrl | 2050 | 0.4
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | F | 3 | lower | 2020 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | F | 3 | lower | 2050 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | F | 3 | upper | 2020 | 0.6
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | F | 3 | upper | 2050 | 0.6
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | E | 2 | ctrl | 2015 | 0
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | E | 2 | ctrl | 2020 | 0
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | E | 2 | ctrl | 2030 | 0
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | E | 2 | ctrl | 2050 | 0
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | E | 2 | lower | 2020 | 0
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | E | 2 | lower | 2050 | 0
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | E | 2 | upper | 2020 | 0.01
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | E | 2 | upper | 2050 | 0.01
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | K | 3 | ctrl | 2015 | 25
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | K | 3 | ctrl | 2020 | 25
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | K | 3 | ctrl | 2030 | 25
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | K | 3 | ctrl | 2050 | 25
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | K | 3 | lower | 2020 | 25
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | K | 3 | lower | 2050 | 25
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 6
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 6
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 7 | ctrl | 2015 | 1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 7 | ctrl | 2020 | 1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 7 | ctrl | 2030 | 1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | I | 7 | ctrl | 2050 | 1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 10
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 9
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 7
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 6
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2020 | 8
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [1, 2] | lower | 2050 | 5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2020 | 60
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | [1, 2] | upper | 2050 | 30
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | H | 1 | ctrl | 2015 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | H | 1 | ctrl | 2020 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | H | 1 | ctrl | 2030 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | H | 1 | ctrl | 2050 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | H | 1 | lower | 2020 | 0
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | H | 1 | lower | 2050 | 0
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | H | 1 | upper | 2020 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | H | 1 | upper | 2050 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2015 | 2126.7454
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2020 | 2073.5768
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2030 | 2020.4082
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | ctrl | 2050 | 1807.7336
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | lower | 2020 | 1063.3727
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | lower | 2050 | 1063.3727
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | upper | 2020 | 2658.4318
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | F |  | upper | 2050 | 2658.4318
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | J | [2, 3] | ctrl | 2015 | 0.063802
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | J | [2, 3] | ctrl | 2020 | 0.063802
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | J | [2, 3] | ctrl | 2030 | 0.053169
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | J | [2, 3] | ctrl | 2050 | 0.053169
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | J | [2, 3] | lower | 2020 | 0.042535
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | J | [2, 3] | lower | 2050 | 0.042535
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | J | [2, 3] | upper | 2020 | 0.26584
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | J | [2, 3] | upper | 2050 | 0.26584
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | [2, 3] | ctrl | 2015 | 0.042535
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | [2, 3] | ctrl | 2020 | 0.042535
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | [2, 3] | ctrl | 2030 | 0.031901
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | [2, 3] | ctrl | 2050 | 0.031901
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | [2, 3] | lower | 2020 | 0.031901
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | [2, 3] | lower | 2050 | 0.031901
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | [2, 3] | upper | 2020 | 0.15951
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | [2, 3] | upper | 2050 | 0.15951
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | [2, 3] | ctrl | 2015 | 0.021267
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | [2, 3] | ctrl | 2020 | 0.021267
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | [2, 3] | ctrl | 2030 | 0.021267
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | [2, 3] | ctrl | 2050 | 0.021267
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | [2, 3] | lower | 2020 | 0.010634
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | [2, 3] | lower | 2050 | 0.010634
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | [2, 3] | upper | 2020 | 0.10634
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | 0 | [2, 3] | upper | 2050 | 0.10634
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | ctrl | 2015 | 1.1697
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | ctrl | 2020 | 1.1697
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | ctrl | 2030 | 1.0634
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | ctrl | 2050 | 1.0634
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | lower | 2020 | 0.63802
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | lower | 2050 | 0.63802
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | upper | 2020 | 2.2331
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | upper | 2050 | 2.3394
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | L |  | ctrl | 2015 | 0.10634
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | L |  | ctrl | 2020 | 0.10634
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | L |  | ctrl | 2030 | 0.10634
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | L |  | ctrl | 2050 | 0.10634
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | L |  | lower | 2020 | 0.10634
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | L |  | lower | 2050 | 0.10634
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | L |  | upper | 2020 | 0.10634
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | L |  | upper | 2050 | 0.21267
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 | [8, 9] | ctrl | 2015 | 1.0634
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 | [8, 9] | ctrl | 2020 | 1.0634
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 | [8, 9] | ctrl | 2030 | 0.95704
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 | [8, 9] | ctrl | 2050 | 0.95704
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 | [8, 9] | lower | 2020 | 0.53169
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 | [8, 9] | lower | 2050 | 0.53169
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 | [8, 9] | upper | 2020 | 2.1267
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 | [8, 9] | upper | 2050 | 2.1267
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  | D | 9 | ctrl | 2015 | 0.4
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  | D | 9 | ctrl | 2020 | 0.4
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  | D | 9 | ctrl | 2030 | 0.4
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  | D | 9 | ctrl | 2050 | 0.4
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  | D | 9 | lower | 2020 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  | D | 9 | lower | 2050 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  | D | 9 | upper | 2020 | 0.5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  | D | 9 | upper | 2050 | 0.5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 9 | ctrl | 2015 | 0.15
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 9 | ctrl | 2020 | 0.15
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 9 | ctrl | 2030 | 0.15
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 9 | ctrl | 2050 | 0.15
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 9 | lower | 2020 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 9 | lower | 2050 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 9 | upper | 2020 | 0.2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  |  | 9 | upper | 2050 | 0.2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | D | 9 | ctrl | 2015 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | D | 9 | ctrl | 2020 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | D | 9 | ctrl | 2030 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | D | 9 | ctrl | 2050 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | D | 9 | lower | 2020 | 0.08
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | D | 9 | lower | 2050 | 0.08
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | D | 9 | upper | 2020 | 0.15
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | D | 9 | upper | 2050 | 0.15
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2020 | 0.041206
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2025 | 0.041375
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2030 | 0.041538
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2040 | 0.041846
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2050 | 0.041992
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | lower | 2025 | 0.016473
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | lower | 2050 | 0.016473
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | upper | 2025 | 0.074229
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | upper | 2050 | 0.074229
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2020 | 4.5
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2025 | 4.5
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2030 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2040 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2050 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2025 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2050 | 3
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2025 | 5
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2050 | 5
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2020 | 0.02
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2025 | 0.02
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2030 | 0.02
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2040 | 0.02
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2050 | 0.02
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2025 | 0.01
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2050 | 0.01
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2025 | 0.03
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2050 | 0.03
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2020 | 11.42
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2025 | 11.37
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2030 | 11.33
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2040 | 11.24
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2050 | 11.2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | lower | 2025 | 19.28
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | lower | 2050 | 19.28
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | upper | 2025 | 4.28
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | upper | 2050 | 4.28
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2020 | 4.6027
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2025 | 4.6719
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2030 | 4.7404
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2040 | 4.8757
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2050 | 4.9424
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | lower | 2025 | 5.3085
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | lower | 2050 | 5.7553
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | upper | 2025 | 4.059
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | upper | 2050 | 4.3155
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2020 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2025 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2030 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2040 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2050 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2025 | 1
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2050 | 1
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2025 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2050 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2020 | 5
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2025 | 5
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2030 | 5
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2040 | 5
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2050 | 5
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | lower | 2025 | 3
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | lower | 2050 | 3
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | upper | 2025 | 7
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | upper | 2050 | 7
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2020 | 25
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2025 | 25
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2030 | 30
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2040 | 30
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2050 | 30
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | lower | 2025 | 25
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | lower | 2050 | 25
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | upper | 2025 | 30
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | upper | 2050 | 35
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2020 | 24032.2234
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2025 | 23287.8625
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2030 | 22649.8389
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2040 | 21905.478
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2050 | 21161.1171
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | lower | 2025 | 23287.8625
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | lower | 2050 | 21161.1171
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | upper | 2025 | 23287.8625
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | upper | 2050 | 21161.1171
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2020 | 2.8817
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2025 | 2.8179
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2030 | 2.6584
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2040 | 2.5946
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2050 | 2.5308
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | lower | 2025 | 1.7333
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | lower | 2050 | 1.6163
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | upper | 2025 | 4.3173
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | upper | 2050 | 3.9983
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2020 | 1.6376
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2025 | 1.5844
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2030 | 1.5419
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2040 | 1.4887
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2050 | 1.4462
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2025 | 0.9145
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2050 | 0.82943
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2025 | 2.4564
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2050 | 2.2331
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2020 | 0.71246
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2025 | 0.71246
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2030 | 0.60612
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2040 | 0.60612
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2050 | 0.60612
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | lower | 2025 | 0.49979
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | lower | 2050 | 0.49979
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | upper | 2025 | 1.0102
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | upper | 2050 | 0.98894
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2020 | 0.54232
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2025 | 0.53169
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2030 | 0.51042
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2040 | 0.49979
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2050 | 0.47852
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2025 | 0.31901
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2050 | 0.28711
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2025 | 0.84006
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2050 | 0.76563
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2020 | 6.0612
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2025 | 6.0719
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2030 | 6.5185
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2040 | 6.6461
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2050 | 6.2314
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | lower | 2025 | 5.4126
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | lower | 2050 | 6.1144
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | upper | 2025 | 6.4759
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | upper | 2050 | 7.0608
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 0
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2025 | 0
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 0
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2040 | 0
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 0
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2025 | 0
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 0
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2025 | 0
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 0
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2020 | 6.0612
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2025 | 6.0719
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2030 | 6.5185
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2040 | 6.6461
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2050 | 6.2314
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | lower | 2025 | 5.4126
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | lower | 2050 | 6.1144
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | upper | 2025 | 6.4759
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | upper | 2050 | 7.0608
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2020 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2025 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2030 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2040 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2050 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | lower | 2025 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | lower | 2050 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | upper | 2025 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | upper | 2050 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2020 | 0.2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2025 | 0.2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2030 | 0.2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2040 | 0.2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2050 | 0.2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | lower | 2025 | 0.2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | lower | 2050 | 0.2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | upper | 2025 | 0.2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | upper | 2050 | 0.2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2020 | 1200
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2025 | 1200
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2030 | 1200
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2040 | 1200
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2050 | 1200
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | lower | 2025 | 1200
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | lower | 2050 | 1200
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | upper | 2025 | 1200
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | upper | 2050 | 1200
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2020 | 9.41
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2025 | 9.41
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2030 | 9.41
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2040 | 9.41
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2050 | 9.41
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | lower | 2025 | 15.88
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | lower | 2050 | 15.88
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | upper | 2025 | 3.53
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | upper | 2050 | 3.53
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2020 | 2.01
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2025 | 1.96
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2030 | 1.92
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2040 | 1.84
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2050 | 1.8
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | lower | 2025 | 3.31
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | lower | 2050 | 3.03
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | upper | 2025 | 0.74
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | upper | 2050 | 0.67
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2020 | 5.68
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2025 | 5.7914
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2030 | 5.9027
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2040 | 6.1255
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2050 | 6.2369
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | lower | 2025 | 5.7914
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | lower | 2050 | 6.2369
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | upper | 2025 | 5.7914
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | upper | 2050 | 6.2369
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | L | 1 | ctrl | 2020 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | L | 1 | ctrl | 2025 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | L | 1 | ctrl | 2030 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | L | 1 | ctrl | 2040 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | L | 1 | ctrl | 2050 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | L | 1 | lower | 2025 | 3
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | L | 1 | lower | 2050 | 3
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | L | 1 | upper | 2025 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | L | 1 | upper | 2050 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2020 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2025 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2030 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2040 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2050 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | lower | 2025 | 3
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | lower | 2050 | 3
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | upper | 2025 | 1
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | upper | 2050 | 1
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2020 | 0.065014
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2025 | 0.065126
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2030 | 0.065233
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2040 | 0.065433
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2050 | 0.065528
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | lower | 2025 | 0.037115
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | lower | 2050 | 0.037115
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | upper | 2025 | 0.092698
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | upper | 2050 | 0.092698
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2020 | 4.5
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2025 | 4.5
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2030 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2040 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2050 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2025 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2050 | 3
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2025 | 5
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2050 | 5
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2020 | 0.02
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2025 | 0.02
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2030 | 0.02
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2040 | 0.02
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2050 | 0.02
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2025 | 0.01
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2050 | 0.01
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2025 | 0.03
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2050 | 0.03
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2020 | 13.14
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2025 | 13.11
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2030 | 13.09
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2040 | 13.05
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2050 | 13.03
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | lower | 2025 | 22.18
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | lower | 2050 | 22.18
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | upper | 2025 | 4.93
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | upper | 2050 | 4.93
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2020 | 8.4437
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2025 | 8.5533
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2030 | 8.6608
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2040 | 8.8699
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2050 | 8.9716
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | lower | 2025 | 11.2426
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | lower | 2050 | 12.0754
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | upper | 2025 | 6.504
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | upper | 2050 | 6.774
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2020 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2025 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2030 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2040 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2050 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2025 | 1
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2050 | 1
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2025 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2050 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2020 | 5
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2025 | 5
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2030 | 5
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2040 | 5
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2050 | 5
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | lower | 2025 | 3
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | lower | 2050 | 3
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | upper | 2025 | 7
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | upper | 2050 | 7
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2020 | 25
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2025 | 25
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2030 | 30
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2040 | 30
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2050 | 30
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | lower | 2025 | 25
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | lower | 2050 | 25
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | upper | 2025 | 30
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | upper | 2050 | 35
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2020 | 25414.608
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2025 | 24670.2471
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2030 | 23925.8862
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2040 | 23181.5253
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2050 | 22437.1643
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | lower | 2025 | 24670.2471
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | lower | 2050 | 22437.1643
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | upper | 2025 | 24670.2471
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | upper | 2050 | 22437.1643
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2020 | 3.0625
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2025 | 2.9774
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2030 | 2.8605
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2040 | 2.7754
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2050 | 2.6903
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | lower | 2025 | 1.8077
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | lower | 2050 | 1.6589
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | upper | 2025 | 4.4024
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | upper | 2050 | 4.0302
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2020 | 2.1055
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2025 | 2.0417
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2030 | 1.9779
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2040 | 1.9247
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2050 | 1.8609
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2025 | 1.2122
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2050 | 1.0953
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2025 | 3.0093
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2050 | 2.7329
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2020 | 0.25521
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2025 | 0.25521
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2030 | 0.22331
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2040 | 0.22331
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2050 | 0.21267
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | lower | 2025 | 0.18077
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | lower | 2050 | 0.18077
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | upper | 2025 | 0.36155
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | upper | 2050 | 0.36155
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2020 | 0.70183
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2025 | 0.68056
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2030 | 0.65929
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2040 | 0.63802
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2050 | 0.61676
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2025 | 0.41472
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2050 | 0.38281
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2025 | 1.0315
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2050 | 0.93577
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2020 | 4.8809
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2025 | 4.8064
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2030 | 4.8809
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2040 | 4.849
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2050 | 4.615
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | lower | 2025 | 4.5619
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | lower | 2050 | 4.5831
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | upper | 2025 | 4.9447
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | upper | 2050 | 4.9128
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 0
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2025 | 0
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 0
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2040 | 0
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 0
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2025 | 0
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 0
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2025 | 0
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 0
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2020 | 4.8809
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2025 | 4.8064
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2030 | 4.8809
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2040 | 4.849
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2050 | 4.615
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | lower | 2025 | 4.5619
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | lower | 2050 | 4.5831
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | upper | 2025 | 4.9447
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | upper | 2050 | 4.9128
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2020 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2025 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2030 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2040 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2050 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | lower | 2025 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | lower | 2050 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | upper | 2025 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | upper | 2050 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2020 | 0.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2025 | 0.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2030 | 0.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2040 | 0.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2050 | 0.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | lower | 2025 | 0.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | lower | 2050 | 0.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | upper | 2025 | 0.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | upper | 2050 | 0.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2020 | 2000
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2025 | 2000
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2030 | 2000
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2040 | 2000
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2050 | 2000
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | lower | 2025 | 2000
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | lower | 2050 | 2000
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | upper | 2025 | 2000
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | upper | 2050 | 2000
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2020 | 12.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2025 | 12.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2030 | 12.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2040 | 12.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2050 | 12.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | lower | 2025 | 20.58
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | lower | 2050 | 20.58
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | upper | 2025 | 4.57
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | upper | 2050 | 4.57
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2020 | 0.95
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2025 | 0.92
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2030 | 0.9
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2040 | 0.86
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2050 | 0.84
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | lower | 2025 | 1.56
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | lower | 2050 | 1.43
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | upper | 2025 | 0.35
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | upper | 2050 | 0.32
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2020 | 5.05
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2025 | 5.149
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2030 | 5.248
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2040 | 5.4461
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2050 | 5.5451
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | lower | 2025 | 5.149
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | lower | 2050 | 5.5451
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | upper | 2025 | 5.149
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | upper | 2050 | 5.5451
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | L | 1 | ctrl | 2020 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | L | 1 | ctrl | 2025 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | L | 1 | ctrl | 2030 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | L | 1 | ctrl | 2040 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | L | 1 | ctrl | 2050 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | L | 1 | lower | 2025 | 3
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | L | 1 | lower | 2050 | 3
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | L | 1 | upper | 2025 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | L | 1 | upper | 2050 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2020 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2025 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2030 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2040 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2050 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | lower | 2025 | 3
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | lower | 2050 | 3
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | upper | 2025 | 1
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | upper | 2050 | 1
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2020 | 0.020765
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2025 | 0.020935
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2030 | 0.021103
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2040 | 0.021269
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2050 | 0.021433
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | lower | 2025 | 0.008237
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | lower | 2050 | 0.008237
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | upper | 2025 | 0.037009
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | upper | 2050 | 0.037009
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2020 | 4.5
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2025 | 4.5
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2030 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2040 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2050 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2025 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2050 | 3
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2025 | 5
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2050 | 5
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2020 | 0.02
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2025 | 0.02
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2030 | 0.02
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2040 | 0.02
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2050 | 0.02
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2025 | 0.01
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2050 | 0.01
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2025 | 0.03
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2050 | 0.03
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2020 | 22.66
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2025 | 22.47
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2030 | 22.3
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2040 | 22.12
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2050 | 21.95
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | lower | 2025 | 38.56
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | lower | 2050 | 38.56
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | upper | 2025 | 8.56
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | upper | 2050 | 8.56
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2020 | 1.6514
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2025 | 1.6602
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2030 | 1.6691
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2040 | 1.6779
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2050 | 1.6867
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | lower | 2025 | 1.7235
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | lower | 2050 | 1.7942
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | upper | 2025 | 1.6444
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | upper | 2050 | 1.7085
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2020 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2025 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2030 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2040 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2050 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2025 | 1
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2050 | 1
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2025 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2050 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2020 | 5
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2025 | 5
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2030 | 5
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2040 | 5
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2050 | 5
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | lower | 2025 | 3
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | lower | 2050 | 3
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | upper | 2025 | 7
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | upper | 2050 | 7
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2020 | 25
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2025 | 25
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2030 | 30
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2040 | 30
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2050 | 30
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | lower | 2025 | 25
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | lower | 2050 | 25
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | upper | 2025 | 30
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | upper | 2050 | 35
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2020 | 11803.4372
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2025 | 11484.4254
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2030 | 11165.4135
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2040 | 10740.0645
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2050 | 10421.0526
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | lower | 2025 | 11484.4254
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | lower | 2050 | 10421.0526
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | upper | 2025 | 11484.4254
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | upper | 2050 | 10421.0526
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2020 | 1.3398
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2025 | 1.3079
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2030 | 1.2654
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2040 | 1.2229
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2050 | 1.191
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | lower | 2025 | 0.7869
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | lower | 2050 | 0.73373
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | upper | 2025 | 1.9991
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | upper | 2050 | 1.8503
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2020 | 0.8188
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2025 | 0.79753
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2030 | 0.77626
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2040 | 0.75499
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2050 | 0.72309
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2025 | 0.45725
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2050 | 0.41472
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2025 | 1.2335
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2050 | 1.1165
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2020 | 0.24458
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2025 | 0.23394
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2030 | 0.23394
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2040 | 0.22331
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2050 | 0.21267
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | lower | 2025 | 0.17014
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | lower | 2050 | 0.17014
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | upper | 2025 | 0.35091
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | upper | 2050 | 0.35091
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2020 | 0.27648
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2025 | 0.26584
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2030 | 0.25521
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2040 | 0.25521
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2050 | 0.24458
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2025 | 0.15951
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2050 | 0.13824
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2025 | 0.42535
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2050 | 0.38281
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2020 | 2.2118
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2025 | 2.2437
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2030 | 2.2756
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2040 | 2.265
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2050 | 2.2437
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | lower | 2025 | 2.2012
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | lower | 2050 | 2.1586
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | upper | 2025 | 2.2012
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | upper | 2050 | 2.1586
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 0
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2025 | 0
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 0
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2040 | 0
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 0
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2025 | 0
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 0
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2025 | 0
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 0
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2020 | 2.2118
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2025 | 2.2437
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2030 | 2.2756
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2040 | 2.265
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2050 | 2.2437
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | lower | 2025 | 2.2012
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | lower | 2050 | 2.1586
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | upper | 2025 | 2.2012
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | upper | 2050 | 2.1586
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2020 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2025 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2030 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2040 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2050 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | lower | 2025 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | lower | 2050 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | upper | 2025 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | upper | 2050 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2020 | 0.2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2025 | 0.2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2030 | 0.2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2040 | 0.2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2050 | 0.2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | lower | 2025 | 0.2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | lower | 2050 | 0.2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | upper | 2025 | 0.2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | upper | 2050 | 0.2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2020 | 1200
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2025 | 1200
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2030 | 1200
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2040 | 1200
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2050 | 1200
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | lower | 2025 | 1200
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | lower | 2050 | 1200
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | upper | 2025 | 1200
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | upper | 2050 | 1200
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2020 | 9.41
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2025 | 9.41
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2030 | 9.41
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2040 | 9.41
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2050 | 9.41
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | lower | 2025 | 15.88
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | lower | 2050 | 15.88
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | upper | 2025 | 3.52
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | upper | 2050 | 3.52
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2020 | 13.25
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2025 | 13.07
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2030 | 12.89
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2040 | 12.71
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2050 | 12.54
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | lower | 2025 | 22.06
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | lower | 2050 | 21.17
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | upper | 2025 | 4.89
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | upper | 2050 | 4.69
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2020 | 1.71
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2025 | 1.72
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2030 | 1.73
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2040 | 1.74
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2050 | 1.75
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | lower | 2025 | 1.72
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | lower | 2050 | 1.75
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | upper | 2025 | 1.72
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | upper | 2050 | 1.75
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2020 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2025 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2030 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2040 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2050 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | lower | 2025 | 3
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | lower | 2050 | 3
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | upper | 2025 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | upper | 2050 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2020 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2025 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2030 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2040 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2050 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | lower | 2025 | 3
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | lower | 2050 | 3
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | upper | 2025 | 1
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | upper | 2050 | 1
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2020 | 0.048566
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2025 | 0.048774
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2030 | 0.048978
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2040 | 0.049177
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2050 | 0.049374
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | lower | 2025 | 0.027614
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | lower | 2050 | 0.027614
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | upper | 2025 | 0.069033
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | upper | 2050 | 0.069033
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2020 | 4.5
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2025 | 4.5
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2030 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2040 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2050 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2025 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2050 | 3
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2025 | 5
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2050 | 5
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2020 | 0.02
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2025 | 0.02
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2030 | 0.02
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2040 | 0.02
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2050 | 0.02
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2025 | 0.01
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2050 | 0.01
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2025 | 0.03
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2050 | 0.03
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2020 | 17.58
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2025 | 17.51
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2030 | 17.44
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2040 | 17.37
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2050 | 17.3
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | lower | 2025 | 29.84
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | lower | 2050 | 29.84
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | upper | 2025 | 6.62
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | upper | 2050 | 6.62
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2020 | 2.9286
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2025 | 2.953
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2030 | 2.9773
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2040 | 3.0015
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2050 | 3.0257
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | lower | 2025 | 3.1686
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | lower | 2050 | 3.2946
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | upper | 2025 | 2.7479
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | upper | 2050 | 2.8422
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2020 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2025 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2030 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2040 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2050 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2025 | 1
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2050 | 1
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2025 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2050 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2020 | 5
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2025 | 5
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2030 | 5
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2040 | 5
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2050 | 5
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | lower | 2025 | 3
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | lower | 2050 | 3
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | upper | 2025 | 7
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | upper | 2050 | 7
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2020 | 25
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2025 | 25
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2030 | 30
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2040 | 30
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2050 | 30
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | lower | 2025 | 25
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | lower | 2050 | 25
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | upper | 2025 | 30
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | upper | 2050 | 35
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2020 | 18396.348
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2025 | 17864.6617
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2030 | 17332.9753
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2040 | 16801.2889
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2050 | 16269.6026
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | lower | 2025 | 17864.6617
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | lower | 2050 | 16269.6026
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | upper | 2025 | 17864.6617
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | upper | 2050 | 16269.6026
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2020 | 2.2224
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2025 | 2.1586
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2030 | 2.0948
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2040 | 2.031
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2050 | 1.9672
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | lower | 2025 | 1.3398
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | lower | 2050 | 1.2122
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | upper | 2025 | 3.0519
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | upper | 2050 | 2.7648
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2020 | 1.5738
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2025 | 1.5313
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2030 | 1.4781
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2040 | 1.4356
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2050 | 1.393
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2025 | 0.87197
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2050 | 0.7869
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2025 | 2.2437
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2050 | 2.031
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2020 | 0.1276
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2025 | 0.1276
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2030 | 0.11697
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2040 | 0.11697
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2050 | 0.11697
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | lower | 2025 | 0.17014
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | lower | 2050 | 0.14887
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | upper | 2025 | 0.042535
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | upper | 2050 | 0.031901
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2020 | 0.52105
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2025 | 0.51042
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2030 | 0.48915
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2040 | 0.47852
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2050 | 0.46788
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2025 | 0.29774
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2050 | 0.27648
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2025 | 0.76563
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2050 | 0.70183
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2020 | 3.1795
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2025 | 3.1476
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2030 | 3.105
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2040 | 3.0412
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2050 | 2.9774
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | lower | 2025 | 3.1157
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | lower | 2050 | 2.9136
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | upper | 2025 | 3.1157
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | upper | 2050 | 2.9136
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 0
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2025 | 0
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 0
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2040 | 0
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 0
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2025 | 0
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 0
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2025 | 0
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 0
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2020 | 3.1795
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2025 | 3.1476
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2030 | 3.105
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2040 | 3.0412
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2050 | 2.9774
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | lower | 2025 | 3.1157
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | lower | 2050 | 2.9136
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | upper | 2025 | 3.1157
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | upper | 2050 | 2.9136
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2020 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2025 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2030 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2040 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2050 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | lower | 2025 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | lower | 2050 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | upper | 2025 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | upper | 2050 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2020 | 0.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2025 | 0.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2030 | 0.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2040 | 0.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2050 | 0.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | lower | 2025 | 0.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | lower | 2050 | 0.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | upper | 2025 | 0.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | upper | 2050 | 0.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2020 | 2000
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2025 | 2000
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2030 | 2000
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2040 | 2000
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2050 | 2000
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | lower | 2025 | 2000
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | lower | 2050 | 2000
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | upper | 2025 | 2000
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | upper | 2050 | 2000
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2020 | 12.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2025 | 12.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2030 | 12.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2040 | 12.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2050 | 12.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | lower | 2025 | 20.6
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | lower | 2050 | 20.6
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | upper | 2025 | 4.57
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | upper | 2050 | 4.57
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2020 | 5.39
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2025 | 5.32
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2030 | 5.25
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2040 | 5.18
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2050 | 5.11
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | lower | 2025 | 9.01
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | lower | 2050 | 8.65
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | upper | 2025 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | upper | 2050 | 1.92
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2020 | 1.71
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2025 | 1.72
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2030 | 1.73
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2040 | 1.74
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2050 | 1.75
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | lower | 2025 | 1.72
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | lower | 2050 | 1.75
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | upper | 2025 | 1.72
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | upper | 2050 | 1.75
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2020 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2025 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2030 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2040 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2050 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | lower | 2025 | 3
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | lower | 2050 | 3
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | upper | 2025 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | upper | 2050 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2020 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2025 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2030 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2040 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2050 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | lower | 2025 | 3
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | lower | 2050 | 3
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | upper | 2025 | 1
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | upper | 2050 | 1
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2020 | 0.043039
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2025 | 0.043177
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2030 | 0.04331
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2040 | 0.04356
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2050 | 0.043679
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | lower | 2025 | 0.017214
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | lower | 2050 | 0.017214
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | upper | 2025 | 0.077488
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | upper | 2050 | 0.077488
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2020 | 4.5
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2025 | 4.5
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2030 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2040 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2050 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2025 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2050 | 3
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2025 | 5
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2050 | 5
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2020 | 0.02
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2025 | 0.02
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2030 | 0.02
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2040 | 0.02
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2050 | 0.02
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2025 | 0.01
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2050 | 0.01
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2025 | 0.03
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2050 | 0.03
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2020 | 10.93
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2025 | 10.9
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2030 | 10.86
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2040 | 10.8
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2050 | 10.77
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | lower | 2025 | 18.45
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | lower | 2050 | 18.45
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | upper | 2025 | 4.1
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | upper | 2050 | 4.1
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2020 | 5.4809
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2025 | 5.561
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2030 | 5.6401
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2040 | 5.7959
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2050 | 5.8725
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | lower | 2025 | 6.5168
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | lower | 2050 | 7.0429
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | upper | 2025 | 4.678
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | upper | 2050 | 4.9432
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2020 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2025 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2030 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2040 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2050 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2025 | 1
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2050 | 1
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2025 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2050 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2020 | 5
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2025 | 5
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2030 | 5
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2040 | 5
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2050 | 5
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | lower | 2025 | 3
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | lower | 2050 | 3
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | upper | 2025 | 7
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | upper | 2050 | 7
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2020 | 25
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2025 | 25
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2030 | 30
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2040 | 30
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2050 | 30
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | lower | 2025 | 25
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | lower | 2050 | 25
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | upper | 2025 | 30
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | upper | 2050 | 35
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2020 | 24670.2471
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2025 | 23925.8862
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2030 | 23181.5253
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2040 | 22437.1643
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2050 | 21799.1407
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | lower | 2025 | 23925.8862
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | lower | 2050 | 21799.1407
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | upper | 2025 | 23925.8862
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | upper | 2050 | 21799.1407
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2020 | 2.8711
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2025 | 2.8073
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2030 | 2.6478
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2040 | 2.584
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2050 | 2.5202
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | lower | 2025 | 1.7014
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | lower | 2050 | 1.5738
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | upper | 2025 | 4.296
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | upper | 2050 | 3.977
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2020 | 1.7014
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2025 | 1.6589
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2030 | 1.6057
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2040 | 1.5525
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2050 | 1.51
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2025 | 0.9464
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2050 | 0.86133
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2025 | 2.5627
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2050 | 2.3394
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2020 | 0.59549
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2025 | 0.59549
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2030 | 0.51042
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2040 | 0.51042
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2050 | 0.51042
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | lower | 2025 | 0.42535
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | lower | 2050 | 0.41472
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | upper | 2025 | 0.8507
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | upper | 2050 | 0.84006
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2020 | 0.56359
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2025 | 0.55295
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2030 | 0.53169
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2040 | 0.52105
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2050 | 0.49979
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2025 | 0.32965
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2050 | 0.29774
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2025 | 0.8826
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2050 | 0.79753
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2020 | 5.806
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2025 | 5.7954
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2030 | 6.1463
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2040 | 6.2314
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2050 | 5.8592
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | lower | 2025 | 5.2424
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | lower | 2050 | 5.7741
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | upper | 2025 | 6.1357
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | upper | 2050 | 6.5716
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 0
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2025 | 0
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 0
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2040 | 0
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 0
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2025 | 0
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 0
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2025 | 0
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 0
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2020 | 5.806
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2025 | 5.7954
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2030 | 6.1463
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2040 | 6.2314
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2050 | 5.8592
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | lower | 2025 | 5.2424
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | lower | 2050 | 5.7741
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | upper | 2025 | 6.1357
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | upper | 2050 | 6.5716
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2020 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2025 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2030 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2040 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2050 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | lower | 2025 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | lower | 2050 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | upper | 2025 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | upper | 2050 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2020 | 0.2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2025 | 0.2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2030 | 0.2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2040 | 0.2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2050 | 0.2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | lower | 2025 | 0.2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | lower | 2050 | 0.2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | upper | 2025 | 0.2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | upper | 2050 | 0.2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2020 | 1200
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2025 | 1200
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2030 | 1200
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2040 | 1200
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2050 | 1200
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | lower | 2025 | 1200
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | lower | 2050 | 1200
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | upper | 2025 | 1200
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | upper | 2050 | 1200
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2020 | 9.41
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2025 | 9.41
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2030 | 9.41
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2040 | 9.41
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2050 | 9.41
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | lower | 2025 | 15.88
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | lower | 2050 | 15.88
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | upper | 2025 | 3.53
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | upper | 2050 | 3.53
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2020 | 1.52
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2025 | 1.49
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2030 | 1.46
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2040 | 1.39
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2050 | 1.36
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | lower | 2025 | 2.51
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | lower | 2050 | 2.3
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | upper | 2025 | 0.56
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | upper | 2050 | 0.51
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2020 | 6.03
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2025 | 6.1482
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2030 | 6.2665
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2040 | 6.5029
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2050 | 6.6212
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | lower | 2025 | 6.1482
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | lower | 2050 | 6.6212
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | upper | 2025 | 6.1482
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | upper | 2050 | 6.6212
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2020 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2025 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2030 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2040 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2050 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | lower | 2025 | 3
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | lower | 2050 | 3
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | upper | 2025 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | upper | 2050 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2020 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2025 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2030 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2040 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2050 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | lower | 2025 | 3
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | lower | 2050 | 3
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | upper | 2025 | 1
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | upper | 2050 | 1
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2020 | 0.067497
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2025 | 0.067554
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2030 | 0.067609
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2040 | 0.067711
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | ctrl | 2050 | 0.067759
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | lower | 2025 | 0.038557
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | lower | 2050 | 0.038557
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | upper | 2025 | 0.096617
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | [2, 3, 4] | upper | 2050 | 0.096617
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2020 | 4.5
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2025 | 4.5
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2030 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2040 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2050 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2025 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2050 | 3
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2025 | 5
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2050 | 5
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2020 | 0.02
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2025 | 0.02
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2030 | 0.02
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2040 | 0.02
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2050 | 0.02
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2025 | 0.01
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2050 | 0.01
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2025 | 0.03
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2050 | 0.03
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2020 | 12.65
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2025 | 12.64
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2030 | 12.63
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2040 | 12.61
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | ctrl | 2050 | 12.6
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | lower | 2025 | 21.35
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | lower | 2050 | 21.35
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | upper | 2025 | 4.73
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | [I, A] | [1, 2] | upper | 2050 | 4.73
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2020 | 11.8542
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2025 | 11.9638
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2030 | 12.0706
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2040 | 12.2757
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | ctrl | 2050 | 12.3744
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | lower | 2025 | 18.297
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | lower | 2050 | 19.3674
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | upper | 2025 | 8.1691
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | AG |  | upper | 2050 | 8.3762
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2020 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2025 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2030 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2040 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2050 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2025 | 1
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2050 | 1
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2025 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2050 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2020 | 5
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2025 | 5
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2030 | 5
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2040 | 5
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2050 | 5
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | lower | 2025 | 3
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | lower | 2050 | 3
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | upper | 2025 | 7
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | upper | 2050 | 7
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2020 | 25
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2025 | 25
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2030 | 30
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2040 | 30
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2050 | 30
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | lower | 2025 | 25
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | lower | 2050 | 25
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | upper | 2025 | 30
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | upper | 2050 | 35
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2020 | 26052.6316
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2025 | 25308.2707
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2030 | 24563.9098
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2040 | 23713.2116
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | ctrl | 2050 | 22968.8507
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | lower | 2025 | 25308.2707
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | lower | 2050 | 22968.8507
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | upper | 2025 | 25308.2707
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | [E, J] | [1, 3, 2] | upper | 2050 | 22968.8507
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2020 | 3.0625
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2025 | 2.9668
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2030 | 2.8605
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2040 | 2.7754
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | ctrl | 2050 | 2.6903
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | lower | 2025 | 1.7333
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | lower | 2050 | 1.5844
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | upper | 2025 | 4.413
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, K] | [2, 4, 7] | upper | 2050 | 4.0302
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2020 | 2.1905
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2025 | 2.1267
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2030 | 2.0629
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2040 | 1.9885
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2050 | 1.9247
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2025 | 1.2122
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2050 | 1.1059
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2025 | 3.1369
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2050 | 2.8498
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2020 | 0.13824
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2025 | 0.13824
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2030 | 0.11697
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2040 | 0.11697
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | ctrl | 2050 | 0.11697
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | lower | 2025 | 0.10634
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | lower | 2050 | 0.095704
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | upper | 2025 | 0.20204
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | [J, K] |  | upper | 2050 | 0.20204
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2020 | 0.73373
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2025 | 0.71246
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2030 | 0.69119
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2040 | 0.65929
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | ctrl | 2050 | 0.63802
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2025 | 0.41472
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | lower | 2050 | 0.38281
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2025 | 1.074
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | [2, 4] | upper | 2050 | 0.9783
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2020 | 4.615
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2025 | 4.5193
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2030 | 4.5087
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2040 | 4.4236
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | ctrl | 2050 | 4.2429
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | lower | 2025 | 4.3811
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | lower | 2050 | 4.2322
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | upper | 2025 | 4.6044
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | FJ | 2 | upper | 2050 | 4.4236
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 0
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2025 | 0
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 0
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2040 | 0
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 0
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2025 | 0
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 0
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2025 | 0
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 0
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2020 | 4.615
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2025 | 4.5193
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2030 | 4.5087
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2040 | 4.4236
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | ctrl | 2050 | 4.2429
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | lower | 2025 | 4.3811
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | lower | 2050 | 4.2322
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | upper | 2025 | 4.6044
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F |  | upper | 2050 | 4.4236
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2020 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2025 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2030 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2040 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2050 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | lower | 2025 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | lower | 2050 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | upper | 2025 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | upper | 2050 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2020 | 0.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2025 | 0.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2030 | 0.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2040 | 0.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | ctrl | 2050 | 0.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | lower | 2025 | 0.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | lower | 2050 | 0.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | upper | 2025 | 0.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [2, 5] | upper | 2050 | 0.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2020 | 2000
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2025 | 2000
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2030 | 2000
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2040 | 2000
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | ctrl | 2050 | 2000
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | lower | 2025 | 2000
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | lower | 2050 | 2000
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | upper | 2025 | 2000
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1 | upper | 2050 | 2000
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2020 | 12.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2025 | 12.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2030 | 12.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2040 | 12.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | ctrl | 2050 | 12.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | lower | 2025 | 20.58
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | lower | 2050 | 20.58
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | upper | 2025 | 4.57
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | [I, A, L, N] | 1 | upper | 2050 | 4.57
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2020 | 0.46
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2025 | 0.45
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2030 | 0.44
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2040 | 0.42
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | ctrl | 2050 | 0.41
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | lower | 2025 | 0.76
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | lower | 2050 | 0.69
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | upper | 2025 | 0.17
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 1 | upper | 2050 | 0.15
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2020 | 5.57
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2025 | 5.6792
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2030 | 5.7884
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2040 | 6.0069
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | ctrl | 2050 | 6.1161
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | lower | 2025 | 5.6792
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | lower | 2050 | 6.1161
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | upper | 2025 | 5.6792
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | [A, N] |  | upper | 2050 | 6.1161
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2020 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2025 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2030 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2040 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | ctrl | 2050 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | lower | 2025 | 3
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | lower | 2050 | 3
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | upper | 2025 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of injection wells |  |  | [L, N] | 1 | upper | 2050 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2020 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2025 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2030 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2040 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | ctrl | 2050 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | lower | 2025 | 3
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | lower | 2050 | 3
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | upper | 2025 | 1
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Technology-specific data | Number of production wells |  |  | [L, N] | 1 | upper | 2050 | 1
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | 2, 3; 4 | ctrl | 2020 | 0.096257
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | 2, 3; 4 | ctrl | 2025 | 0.096257
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | 2, 3; 4 | ctrl | 2030 | 0.096257
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | 2, 3; 4 | ctrl | 2040 | 0.095
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | 2, 3; 4 | ctrl | 2050 | 0.094
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | 2, 3; 4 | lower | 2025 | 0.096257
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | 2, 3; 4 | lower | 2050 | 0.096257
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | 2, 3; 4 | upper | 2025 | 0.096257
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  | B | 2, 3; 4 | upper | 2050 | 0.094
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2020 | 4.5
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2025 | 4.5
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2030 | 4
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2040 | 4
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Construction time [years] | years |  |  | 5 | ctrl | 2050 | 4
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2025 | 4
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Construction time [years] | years |  |  | 5 | lower | 2050 | 3
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2025 | 5
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Construction time [years] | years |  |  | 5 | upper | 2050 | 5
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2020 | 0.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2025 | 0.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2030 | 0.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2040 | 0.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Forced outage [] |  |  |  | 5 | ctrl | 2050 | 0.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2025 | 0.01
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Forced outage [] |  |  |  | 5 | lower | 2050 | 0.01
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2025 | 0.03
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Forced outage [] |  |  |  | 5 | upper | 2050 | 0.03
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | I,A | 1, 2 | ctrl | 2020 | 121
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | I,A | 1, 2 | ctrl | 2025 | 120.77
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | I,A | 1, 2 | ctrl | 2030 | 120.38
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | I,A | 1, 2 | ctrl | 2040 | 119.67
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | I,A | 1, 2 | ctrl | 2050 | 119.32
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | I,A | 1, 2 | lower | 2025 | 120.77
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | I,A | 1, 2 | lower | 2050 | 119.32
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | I,A | 1, 2 | upper | 2025 | 120.77
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Generating capacity for one unit [MW_h] | MW_h |  | I,A | 1, 2 | upper | 2050 | 119.32
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | A,G |  | ctrl | 2020 | 3.74
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | A,G |  | ctrl | 2025 | 3.74
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | A,G |  | ctrl | 2030 | 3.74
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | A,G |  | ctrl | 2040 | 3.7816
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | A,G |  | ctrl | 2050 | 3.8529
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | A,G |  | lower | 2025 | 3.74
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | A,G |  | lower | 2050 | 3.853
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | A,G |  | upper | 2025 | 3.74
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | A,G |  | upper | 2050 | 3.853
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2020 | 2
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2025 | 2
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2030 | 2
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2040 | 2
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | ctrl | 2050 | 2
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2025 | 1
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | lower | 2050 | 1
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2025 | 4
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 5 | upper | 2050 | 4
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2020 | 5
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2025 | 5
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2030 | 5
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2040 | 5
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | ctrl | 2050 | 5
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | lower | 2025 | 3
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | lower | 2050 | 3
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | upper | 2025 | 7
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Space requirement [1000 m2/MW_h] | 1000m2/MW_h |  | D | 5 | upper | 2050 | 7
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2020 | 25
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2025 | 25
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2030 | 30
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2040 | 30
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | ctrl | 2050 | 30
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | lower | 2025 | 25
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | lower | 2050 | 25
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | upper | 2025 | 30
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Energy/technical data | Technical lifetime [years] | years |  |  | 5 | upper | 2050 | 35
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | E,J | 2, 4 | ctrl | 2020 | 18791.95
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | E,J | 2, 4 | ctrl | 2025 | 18255.03
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | E,J | 2, 4 | ctrl | 2030 | 17718.12
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | E,J | 2, 4 | ctrl | 2040 | 17104.51
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | E,J | 2, 4 | ctrl | 2050 | 16567.59
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | E,J | 2, 4 | lower | 2025 | 15516.78
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | E,J | 2, 4 | lower | 2050 | 14082.45
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | E,J | 2, 4 | upper | 2025 | 20993.29
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | E,J | 2, 4 | upper | 2050 | 19052.73
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | C,K | 2, 4, 7 | ctrl | 2020 | 1.34
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | C,K | 2, 4, 7 | ctrl | 2025 | 1.3
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | C,K | 2, 4, 7 | ctrl | 2030 | 1.27
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | C,K | 2, 4, 7 | ctrl | 2040 | 1.23
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | C,K | 2, 4, 7 | ctrl | 2050 | 1.2
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | C,K | 2, 4, 7 | lower | 2025 | 1.11
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | C,K | 2, 4, 7 | lower | 2050 | 1.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | C,K | 2, 4, 7 | upper | 2025 | 1.5
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | C,K | 2, 4, 7 | upper | 2050 | 1.38
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | J | 2, 4 | ctrl | 2020 | 0.27
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | J | 2, 4 | ctrl | 2025 | 0.26
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | J | 2, 4 | ctrl | 2030 | 0.25
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | J | 2, 4 | ctrl | 2040 | 0.25
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | J | 2, 4 | ctrl | 2050 | 0.24
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | J | 2, 4 | lower | 2025 | 0.22
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | J | 2, 4 | lower | 2050 | 0.2
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | J | 2, 4 | upper | 2025 | 0.3
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (heatpump, installation incl) [MEUR/MW_h] | MEUR/MW_h | 2020 | J | 2, 4 | upper | 2050 | 0.28
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (surface installation excl. heatpump) [MEUR/MW_h] | MEUR/MW_h | 2020 | J |  | ctrl | 2020 | 0.4
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (surface installation excl. heatpump) [MEUR/MW_h] | MEUR/MW_h | 2020 | J |  | ctrl | 2025 | 0.39
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (surface installation excl. heatpump) [MEUR/MW_h] | MEUR/MW_h | 2020 | J |  | ctrl | 2030 | 0.38
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (surface installation excl. heatpump) [MEUR/MW_h] | MEUR/MW_h | 2020 | J |  | ctrl | 2040 | 0.37
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (surface installation excl. heatpump) [MEUR/MW_h] | MEUR/MW_h | 2020 | J |  | ctrl | 2050 | 0.36
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (surface installation excl. heatpump) [MEUR/MW_h] | MEUR/MW_h | 2020 | J |  | lower | 2025 | 0.33
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (surface installation excl. heatpump) [MEUR/MW_h] | MEUR/MW_h | 2020 | J |  | lower | 2050 | 0.31
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (surface installation excl. heatpump) [MEUR/MW_h] | MEUR/MW_h | 2020 | J |  | upper | 2025 | 0.45
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (surface installation excl. heatpump) [MEUR/MW_h] | MEUR/MW_h | 2020 | J |  | upper | 2050 | 0.41
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (wells and down hole eq.) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | 2, 4 | ctrl | 2020 | 0.67
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (wells and down hole eq.) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | 2, 4 | ctrl | 2025 | 0.65
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (wells and down hole eq.) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | 2, 4 | ctrl | 2030 | 0.63
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (wells and down hole eq.) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | 2, 4 | ctrl | 2040 | 0.62
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (wells and down hole eq.) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | 2, 4 | ctrl | 2050 | 0.6
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (wells and down hole eq.) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | 2, 4 | lower | 2025 | 0.55
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (wells and down hole eq.) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | 2, 4 | lower | 2050 | 0.51
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (wells and down hole eq.) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | 2, 4 | upper | 2025 | 0.75
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Nominal investment (wells and down hole eq.) [MEUR/MW_h] | MEUR/MW_h | 2020 |  | 2, 4 | upper | 2050 | 0.69
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | F,J | 2, 4 | ctrl | 2020 | 2.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | F,J | 2, 4 | ctrl | 2025 | 2.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | F,J | 2, 4 | ctrl | 2030 | 2.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | F,J | 2, 4 | ctrl | 2040 | 2.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | F,J | 2, 4 | ctrl | 2050 | 2.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | F,J | 2, 4 | lower | 2025 | 2.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | F,J | 2, 4 | lower | 2050 | 2.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | F,J | 2, 4 | upper | 2025 | 2.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | F,J | 2, 4 | upper | 2050 | 2.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 0
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2025 | 0
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 0
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2040 | 0
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 0
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2025 | 0
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | lower | 2050 | 0
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2025 | 0
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | M |  | upper | 2050 | 0
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F | 2, 4 | ctrl | 2020 | 2.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F | 2, 4 | ctrl | 2025 | 2.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F | 2, 4 | ctrl | 2030 | 2.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F | 2, 4 | ctrl | 2040 | 2.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F | 2, 4 | ctrl | 2050 | 2.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F | 2, 4 | lower | 2025 | 2.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F | 2, 4 | lower | 2050 | 2.02
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F | 2, 4 | upper | 2025 | 3
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | F | 2, 4 | upper | 2050 | 3
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2020 | 10
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2025 | 10
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2030 | 10
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2040 | 10
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2050 | 10
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | lower | 2025 | 10
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | lower | 2050 | 10
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | upper | 2025 | 10
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Cold start-up time [hours] | hours |  |  | 3 | upper | 2050 | 10
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Minimum load (of full load) [] |  |  | H | 2; 5 | ctrl | 2020 | 0.2
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Minimum load (of full load) [] |  |  | H | 2; 5 | ctrl | 2025 | 0.2
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Minimum load (of full load) [] |  |  | H | 2; 5 | ctrl | 2030 | 0.2
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Minimum load (of full load) [] |  |  | H | 2; 5 | ctrl | 2040 | 0.2
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Minimum load (of full load) [] |  |  | H | 2; 5 | ctrl | 2050 | 0.2
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Minimum load (of full load) [] |  |  | H | 2; 5 | lower | 2025 | 0.2
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Minimum load (of full load) [] |  |  | H | 2; 5 | lower | 2050 | 0.2
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Minimum load (of full load) [] |  |  | H | 2; 5 | upper | 2025 | 0.2
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Minimum load (of full load) [] |  |  | H | 2; 5 | upper | 2050 | 0.2
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2020 | 4
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2025 | 4
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2030 | 4
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2040 | 4
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Warm start-up time [hours] | hours |  |  |  | ctrl | 2050 | 4
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2025 | 3
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Warm start-up time [hours] | hours |  |  |  | lower | 2050 | 3
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2025 | 5
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Regulation ability | Warm start-up time [hours] | hours |  |  |  | upper | 2050 | 5
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1, 2 | ctrl | 2020 | 2000
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1, 2 | ctrl | 2025 | 2000
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1, 2 | ctrl | 2030 | 2000
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1, 2 | ctrl | 2040 | 2000
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1, 2 | ctrl | 2050 | 2000
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1, 2 | lower | 2025 | 2000
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1, 2 | lower | 2050 | 2000
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1, 2 | upper | 2025 | 2000
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Depth of geothermal well [m] | m |  |  | 1, 2 | upper | 2050 | 2000
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | I,A,L,N | 2 | ctrl | 2020 | 100
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | I,A,L,N | 2 | ctrl | 2025 | 100
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | I,A,L,N | 2 | ctrl | 2030 | 100
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | I,A,L,N | 2 | ctrl | 2040 | 100
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | I,A,L,N | 2 | ctrl | 2050 | 100
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | I,A,L,N | 2 | lower | 2025 | 85
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | I,A,L,N | 2 | lower | 2050 | 85
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | I,A,L,N | 2 | upper | 2025 | 115
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat generation from geothermal ressource [MW_h] | MW_h |  | I,A,L,N | 2 | upper | 2050 | 115
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 2 | ctrl | 2020 | 21
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 2 | ctrl | 2025 | 20.77
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 2 | ctrl | 2030 | 20.38
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 2 | ctrl | 2040 | 19.67
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 2 | ctrl | 2050 | 19.32
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 2 | lower | 2025 | 17.65
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 2 | lower | 2050 | 16.43
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 2 | upper | 2025 | 23.88
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat generation from heat pumps [MW_h] | MW_h |  | A | 2 | upper | 2050 | 22.22
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | A, N |  | ctrl | 2020 | 3.77
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | A, N |  | ctrl | 2025 | 3.8119
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | A, N |  | ctrl | 2030 | 3.8838
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | A, N |  | ctrl | 2040 | 4.0251
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | A, N |  | ctrl | 2050 | 4.097
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | A, N |  | lower | 2025 | 3.81
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | A, N |  | lower | 2050 | 4.1
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | A, N |  | upper | 2025 | 3.81
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Heat pump SCOP (net, annual average) [] |  |  | A, N |  | upper | 2050 | 4.1
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Nominal Abandonment Cost (ABEX) [MEUR/MW_h] | MEUR/MW_h | 2020 | O | 2, 7 | ctrl | 2020 | 0.1
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Nominal Abandonment Cost (ABEX) [MEUR/MW_h] | MEUR/MW_h | 2020 | O | 2, 7 | ctrl | 2025 | 0.1
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Nominal Abandonment Cost (ABEX) [MEUR/MW_h] | MEUR/MW_h | 2020 | O | 2, 7 | ctrl | 2030 | 0.1
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Nominal Abandonment Cost (ABEX) [MEUR/MW_h] | MEUR/MW_h | 2020 | O | 2, 7 | ctrl | 2040 | 0.09
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Nominal Abandonment Cost (ABEX) [MEUR/MW_h] | MEUR/MW_h | 2020 | O | 2, 7 | ctrl | 2050 | 0.09
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Nominal Abandonment Cost (ABEX) [MEUR/MW_h] | MEUR/MW_h | 2020 | O | 2, 7 | lower | 2025 | 0.08
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Nominal Abandonment Cost (ABEX) [MEUR/MW_h] | MEUR/MW_h | 2020 | O | 2, 7 | lower | 2050 | 0.08
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Nominal Abandonment Cost (ABEX) [MEUR/MW_h] | MEUR/MW_h | 2020 | O | 2, 7 | upper | 2025 | 0.11
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Nominal Abandonment Cost (ABEX) [MEUR/MW_h] | MEUR/MW_h | 2020 | O | 2, 7 | upper | 2050 | 0.1
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Number of injection wells |  |  | L, N | 2 | ctrl | 2020 | 6
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Number of injection wells |  |  | L, N | 2 | ctrl | 2025 | 6
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Number of injection wells |  |  | L, N | 2 | ctrl | 2030 | 6
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Number of injection wells |  |  | L, N | 2 | ctrl | 2040 | 6
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Number of injection wells |  |  | L, N | 2 | ctrl | 2050 | 6
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Number of injection wells |  |  | L, N | 2 | lower | 2025 | 6
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Number of injection wells |  |  | L, N | 2 | lower | 2050 | 6
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Number of injection wells |  |  | L, N | 2 | upper | 2025 | 6
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Number of injection wells |  |  | L, N | 2 | upper | 2050 | 6
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Number of production wells |  |  | L | 2 | ctrl | 2020 | 6
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Number of production wells |  |  | L | 2 | ctrl | 2025 | 6
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Number of production wells |  |  | L | 2 | ctrl | 2030 | 6
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Number of production wells |  |  | L | 2 | ctrl | 2040 | 6
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Number of production wells |  |  | L | 2 | ctrl | 2050 | 6
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Number of production wells |  |  | L | 2 | lower | 2025 | 6
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Number of production wells |  |  | L | 2 | lower | 2050 | 6
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Number of production wells |  |  | L | 2 | upper | 2025 | 12
45.4 Geothermal DH, E lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Technology-specific data | Number of production wells |  |  | L | 2 | upper | 2050 | 12
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | ctrl | 2015 | 0.003
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | ctrl | 2020 | 0.003
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | ctrl | 2030 | 0.003
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | ctrl | 2050 | 0.003
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | lower | 2020 | 0.002
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | lower | 2050 | 0.002
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | upper | 2020 | 0.004
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] |  |  |  |  | upper | 2050 | 0.004
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2015 | 0.25
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | 0.25
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | 0.25
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | 0.25
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Construction time [years] | years |  |  |  | lower | 2020 | 0.25
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Construction time [years] | years |  |  |  | lower | 2050 | 0.25
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Construction time [years] | years |  |  |  | upper | 2020 | 0.25
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Construction time [years] | years |  |  |  | upper | 2050 | 0.25
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Forced outage [] |  |  | K |  | ctrl | 2015 | 0.005
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Forced outage [] |  |  | K |  | ctrl | 2020 | 0.005
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Forced outage [] |  |  | K |  | ctrl | 2030 | 0.005
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Forced outage [] |  |  | K |  | ctrl | 2050 | 0.005
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Forced outage [] |  |  | K |  | lower | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Forced outage [] |  |  | K |  | lower | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Forced outage [] |  |  | K |  | upper | 2020 | 0.01
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Forced outage [] |  |  | K |  | upper | 2050 | 0.01
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | P |  | ctrl | 2015 | 0.43
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | P |  | ctrl | 2020 | 0.45
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | P |  | ctrl | 2030 | 0.48
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | P |  | ctrl | 2050 | 0.49946
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | P |  | lower | 2020 | 0.42
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | P |  | lower | 2050 | 0.46
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | P |  | upper | 2020 | 0.49
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Heat efficiency (net, annual average) [] |  |  | P |  | upper | 2050 | 0.54
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Space requirement [1000 m2/MWh_h/y] | 1000m2/MWh_h/y |  | J |  | ctrl | 2015 | 6.7
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Space requirement [1000 m2/MWh_h/y] | 1000m2/MWh_h/y |  | J |  | ctrl | 2020 | 6.3
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Space requirement [1000 m2/MWh_h/y] | 1000m2/MWh_h/y |  | J |  | ctrl | 2030 | 6
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Space requirement [1000 m2/MWh_h/y] | 1000m2/MWh_h/y |  | J |  | ctrl | 2050 | 5.7
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Space requirement [1000 m2/MWh_h/y] | 1000m2/MWh_h/y |  | J |  | lower | 2020 | 6
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Space requirement [1000 m2/MWh_h/y] | 1000m2/MWh_h/y |  | J |  | lower | 2050 | 5.5
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Space requirement [1000 m2/MWh_h/y] | 1000m2/MWh_h/y |  | J |  | upper | 2020 | 6.7
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Space requirement [1000 m2/MWh_h/y] | 1000m2/MWh_h/y |  | J |  | upper | 2050 | 6
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Technical lifetime [years] | years |  | I | 17 | ctrl | 2015 | 30
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Technical lifetime [years] | years |  | I | 17 | ctrl | 2020 | 30
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Technical lifetime [years] | years |  | I | 17 | ctrl | 2030 | 30
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Technical lifetime [years] | years |  | I | 17 | ctrl | 2050 | 30
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Technical lifetime [years] | years |  | I | 17 | lower | 2020 | 30
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Technical lifetime [years] | years |  | I | 17 | lower | 2050 | 30
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Technical lifetime [years] | years |  | I | 17 | upper | 2020 | 30
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Energy/technical data | Technical lifetime [years] | years |  | I | 17 | upper | 2050 | 30
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2015 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | lower | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | lower | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | upper | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  |  | upper | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2015 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | lower | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | lower | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | upper | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  |  | upper | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2015 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | lower | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | lower | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | upper | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  |  | upper | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2015 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2030 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  |  | ctrl | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  |  | lower | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  |  | lower | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  |  | upper | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  |  | upper | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | B |  | ctrl | 2015 | 61.5267
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | B |  | ctrl | 2020 | 64.6637
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | B |  | ctrl | 2030 | 60.4102
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | B |  | ctrl | 2050 | 63.494
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | B |  | lower | 2020 | 60.272
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | B |  | lower | 2050 | 58.2516
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | B |  | upper | 2020 | 68.3642
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Fixed O&M (*total) [EUR/MW_h/y] | EUR/MW_h/y | 2020 | B |  | upper | 2050 | 60.4102
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, E, H, N, S] | [16, 18] | ctrl | 2015 | 0.32965
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, E, H, N, S] | [16, 18] | ctrl | 2020 | 0.32965
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, E, H, N, S] | [16, 18] | ctrl | 2030 | 0.31901
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, E, H, N, S] | [16, 18] | ctrl | 2050 | 0.29774
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, E, H, N, S] | [16, 18] | lower | 2020 | 0.30838
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, E, H, N, S] | [16, 18] | lower | 2050 | 0.27648
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, E, H, N, S] | [16, 18] | upper | 2020 | 0.34028
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (*total) [MEUR/MW_h] | MEUR/MW_h | 2020 | [C, E, H, N, S] | [16, 18] | upper | 2050 | 0.32965
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (diurnal heat storage) [MEUR/MW_h] | MEUR/MW_h | 2020 | [D, M] |  | ctrl | 2015 | 0.042535
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (diurnal heat storage) [MEUR/MW_h] | MEUR/MW_h | 2020 | [D, M] |  | ctrl | 2020 | 0.042535
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (diurnal heat storage) [MEUR/MW_h] | MEUR/MW_h | 2020 | [D, M] |  | ctrl | 2030 | 0.042535
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (diurnal heat storage) [MEUR/MW_h] | MEUR/MW_h | 2020 | [D, M] |  | ctrl | 2050 | 0.042535
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (diurnal heat storage) [MEUR/MW_h] | MEUR/MW_h | 2020 | [D, M] |  | lower | 2020 | 0.031901
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (diurnal heat storage) [MEUR/MW_h] | MEUR/MW_h | 2020 | [D, M] |  | lower | 2050 | 0.031901
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (diurnal heat storage) [MEUR/MW_h] | MEUR/MW_h | 2020 | [D, M] |  | upper | 2020 | 0.053169
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (diurnal heat storage) [MEUR/MW_h] | MEUR/MW_h | 2020 | [D, M] |  | upper | 2050 | 0.053169
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | O |  | ctrl | 2015 | 0.24458
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | O |  | ctrl | 2020 | 0.24458
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | O |  | ctrl | 2030 | 0.23394
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | O |  | ctrl | 2050 | 0.22331
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | O |  | lower | 2020 | 0.23394
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | O |  | lower | 2050 | 0.20204
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | O |  | upper | 2020 | 0.24458
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (equipment) [MEUR/MW_h] | MEUR/MW_h | 2020 | O |  | upper | 2050 | 0.23394
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | O |  | ctrl | 2015 | 0.042535
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | O |  | ctrl | 2020 | 0.042535
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | O |  | ctrl | 2030 | 0.042535
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | O |  | ctrl | 2050 | 0.042535
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | O |  | lower | 2020 | 0.042535
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | O |  | lower | 2050 | 0.031901
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | O |  | upper | 2020 | 0.042535
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Nominal investment (installation) [MEUR/MW_h] | MEUR/MW_h | 2020 | O |  | upper | 2050 | 0.042535
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | ctrl | 2015 | 0.20204
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | ctrl | 2020 | 0.22331
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | ctrl | 2030 | 0.31901
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | ctrl | 2050 | 0.37218
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | lower | 2020 | 0.14887
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | lower | 2050 | 0.24458
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | upper | 2020 | 0.29774
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (*total) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | upper | 2050 | 0.49979
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | R |  | ctrl | 2015 | 0.20204
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | R |  | ctrl | 2020 | 0.22331
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | R |  | ctrl | 2030 | 0.31901
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | R |  | ctrl | 2050 | 0.37218
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | R |  | lower | 2020 | 0.14887
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | R |  | lower | 2050 | 0.24458
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | R |  | upper | 2020 | 0.29774
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (electricity cost) [EUR/MWh_h] | EUR/MWh_h | 2020 | R |  | upper | 2050 | 0.49979
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | ctrl | 2015 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | ctrl | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | ctrl | 2030 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | ctrl | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | lower | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | lower | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | upper | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Financial data | Variable O&M (other O&M) [EUR/MWh_h] | EUR/MWh_h | 2020 | 0 |  | upper | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Collector input [MWh_i/m2/y] | MWh_i/m2/y |  | Q |  | ctrl | 2015 | 1.05
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Collector input [MWh_i/m2/y] | MWh_i/m2/y |  | Q |  | ctrl | 2020 | 1.05
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Collector input [MWh_i/m2/y] | MWh_i/m2/y |  | Q |  | ctrl | 2030 | 1.05
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Collector input [MWh_i/m2/y] | MWh_i/m2/y |  | Q |  | ctrl | 2050 | 1.05
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Collector input [MWh_i/m2/y] | MWh_i/m2/y |  | Q |  | lower | 2020 | 1.01
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Collector input [MWh_i/m2/y] | MWh_i/m2/y |  | Q |  | lower | 2050 | 1.01
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Collector input [MWh_i/m2/y] | MWh_i/m2/y |  | Q |  | upper | 2020 | 1.08
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Collector input [MWh_i/m2/y] | MWh_i/m2/y |  | Q |  | upper | 2050 | 1.08
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Collector output [MWh_h/m2/y] | MWh_h/m2/y |  | A | 4 | ctrl | 2015 | 0.45
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Collector output [MWh_h/m2/y] | MWh_h/m2/y |  | A | 4 | ctrl | 2020 | 0.47
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Collector output [MWh_h/m2/y] | MWh_h/m2/y |  | A | 4 | ctrl | 2030 | 0.5
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Collector output [MWh_h/m2/y] | MWh_h/m2/y |  | A | 4 | ctrl | 2050 | 0.52
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Collector output [MWh_h/m2/y] | MWh_h/m2/y |  | A | 4 | lower | 2020 | 0.45
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Collector output [MWh_h/m2/y] | MWh_h/m2/y |  | A | 4 | lower | 2050 | 0.5
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Collector output [MWh_h/m2/y] | MWh_h/m2/y |  | A | 4 | upper | 2020 | 0.5
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Collector output [MWh_h/m2/y] | MWh_h/m2/y |  | A | 4 | upper | 2050 | 0.55
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Fixed O&M (*total, per annual output) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | B |  | ctrl | 2015 | 0.095704
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Fixed O&M (*total, per annual output) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | B |  | ctrl | 2020 | 0.095704
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Fixed O&M (*total, per annual output) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | B |  | ctrl | 2030 | 0.08507
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Fixed O&M (*total, per annual output) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | B |  | ctrl | 2050 | 0.08507
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Fixed O&M (*total, per annual output) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | B |  | lower | 2020 | 0.08507
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Fixed O&M (*total, per annual output) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | B |  | lower | 2050 | 0.074436
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Fixed O&M (*total, per annual output) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | B |  | upper | 2020 | 0.10634
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Fixed O&M (*total, per annual output) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | B |  | upper | 2050 | 0.08507
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Fixed O&M (*total, per collector area) [EUR/m2/y] | EUR/m2/y | 2020 | B |  | ctrl | 2015 | 0.042535
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Fixed O&M (*total, per collector area) [EUR/m2/y] | EUR/m2/y | 2020 | B |  | ctrl | 2020 | 0.042535
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Fixed O&M (*total, per collector area) [EUR/m2/y] | EUR/m2/y | 2020 | B |  | ctrl | 2030 | 0.042535
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Fixed O&M (*total, per collector area) [EUR/m2/y] | EUR/m2/y | 2020 | B |  | ctrl | 2050 | 0.042535
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Fixed O&M (*total, per collector area) [EUR/m2/y] | EUR/m2/y | 2020 | B |  | lower | 2020 | 0.042535
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Fixed O&M (*total, per collector area) [EUR/m2/y] | EUR/m2/y | 2020 | B |  | lower | 2050 | 0.042535
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Fixed O&M (*total, per collector area) [EUR/m2/y] | EUR/m2/y | 2020 | B |  | upper | 2020 | 0.042535
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Fixed O&M (*total, per collector area) [EUR/m2/y] | EUR/m2/y | 2020 | B |  | upper | 2050 | 0.042535
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (diurnal heat storage) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | [D, M] |  | ctrl | 2015 | 63.8024
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (diurnal heat storage) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | [D, M] |  | ctrl | 2020 | 60.6122
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (diurnal heat storage) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | [D, M] |  | ctrl | 2030 | 57.4221
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (diurnal heat storage) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | [D, M] |  | ctrl | 2050 | 55.2954
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (diurnal heat storage) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | [D, M] |  | lower | 2020 | 43.5983
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (diurnal heat storage) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | [D, M] |  | lower | 2050 | 39.3448
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (diurnal heat storage) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | [D, M] |  | upper | 2020 | 79.753
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (diurnal heat storage) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | [D, M] |  | upper | 2050 | 72.3093
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | [C, H, N] |  | ctrl | 2015 | 456.0699
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | [C, H, N] |  | ctrl | 2020 | 420.4469
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | [C, H, N] |  | ctrl | 2030 | 385.0579
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | [C, H, N] |  | ctrl | 2050 | 346.0215
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | [C, H, N] |  | lower | 2020 | 394.5538
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | [C, H, N] |  | lower | 2050 | 310.5899
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | [C, H, N] |  | upper | 2020 | 448.9772
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage) [EUR/MWh_h/y] | EUR/MWh_h/y | 2020 | [C, H, N] |  | upper | 2050 | 385.0579
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage, per collector area) [EUR/m2] | EUR/m2 | 2020 | [G, H, N] | 16 | ctrl | 2015 | 205.2309
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage, per collector area) [EUR/m2] | EUR/m2 | 2020 | [G, H, N] | 16 | ctrl | 2020 | 198.8507
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage, per collector area) [EUR/m2] | EUR/m2 | 2020 | [G, H, N] | 16 | ctrl | 2030 | 191.4071
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage, per collector area) [EUR/m2] | EUR/m2 | 2020 | [G, H, N] | 16 | ctrl | 2050 | 180.7734
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage, per collector area) [EUR/m2] | EUR/m2 | 2020 | [G, H, N] | 16 | lower | 2020 | 195.6606
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage, per collector area) [EUR/m2] | EUR/m2 | 2020 | [G, H, N] | 16 | lower | 2050 | 170.1396
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage, per collector area) [EUR/m2] | EUR/m2 | 2020 | [G, H, N] | 16 | upper | 2020 | 202.0408
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage, per collector area) [EUR/m2] | EUR/m2 | 2020 | [G, H, N] | 16 | upper | 2050 | 191.4071
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Typical plant size (collector area) [m2] | m2 |  | L |  | ctrl | 2015 | 10000
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Typical plant size (collector area) [m2] | m2 |  | L |  | ctrl | 2020 | 13000
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Typical plant size (collector area) [m2] | m2 |  | L |  | ctrl | 2030 | 21000
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Typical plant size (collector area) [m2] | m2 |  | L |  | ctrl | 2050 | 55000
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Typical plant size (collector area) [m2] | m2 |  | L |  | lower | 2020 | 10000
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Typical plant size (collector area) [m2] | m2 |  | L |  | lower | 2050 | 10000
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Typical plant size (collector area) [m2] | m2 |  | L |  | upper | 2020 | 20000
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Technology-specific data | Typical plant size (collector area) [m2] | m2 |  | L |  | upper | 2050 | 100000
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2015 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2020 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2030 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Construction time [years] | years |  |  | 6 | ctrl | 2050 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | C |  | ctrl | 2015 | 0.35
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | C |  | ctrl | 2020 | 0.35
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | C |  | ctrl | 2030 | 0.35
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | C |  | ctrl | 2050 | 0.35
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | C |  | lower | 2020 | 0.33
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | C |  | upper | 2020 | 0.37
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [1, 2, 3] | ctrl | 2015 | 0.37
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [1, 2, 3] | ctrl | 2020 | 0.37
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [1, 2, 3] | ctrl | 2030 | 0.37
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [1, 2, 3] | ctrl | 2050 | 0.37
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [1, 2, 3] | lower | 2020 | 0.35
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  |  | [1, 2, 3] | upper | 2020 | 0.39
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Forced outage [] |  |  |  | 4 | ctrl | 2015 | 0.009
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Forced outage [] |  |  |  | 4 | ctrl | 2020 | 0.009
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Forced outage [] |  |  |  | 4 | ctrl | 2030 | 0.009
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Forced outage [] |  |  |  | 4 | ctrl | 2050 | 0.009
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2015 | 18
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | [D, E] | 5 | ctrl | 2015 | 0.17
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | [D, E] | 5 | ctrl | 2020 | 0.17
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | [D, E] | 5 | ctrl | 2030 | 0.17
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | [D, E] | 5 | ctrl | 2050 | 0.17
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2015 | 25
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2020 | 25
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2030 | 25
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2050 | 25
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2015 | 24
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2020 | 24
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2030 | 24
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2050 | 24
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2015 | 2.1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2020 | 2.1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2030 | 2.1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2050 | 2.1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2015 | 942
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2020 | 942
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2030 | 942
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2050 | 942
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2015 | 5
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2020 | 5
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2030 | 5
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2050 | 5
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | I | 8 | ctrl | 2015 | 23
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | I | 8 | ctrl | 2020 | 23
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | I | 8 | ctrl | 2030 | 23
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | I | 8 | ctrl | 2050 | 23
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [D, P, Q] | 6 | ctrl | 2015 | 9357.6799
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [D, P, Q] | 6 | ctrl | 2020 | 9357.6799
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [D, P, Q] | 6 | ctrl | 2030 | 8983.3727
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [D, P, Q] | 6 | ctrl | 2050 | 8609.0655
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [D, P, Q] | 6 | lower | 2020 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [D, P, Q] | 6 | lower | 2050 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [D, P, Q] | 6 | upper | 2020 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [D, P, Q] | 6 | upper | 2050 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [M, N, O] | [1, 6, 9, 10] | ctrl | 2015 | 0.37218
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [M, N, O] | [1, 6, 9, 10] | ctrl | 2020 | 0.36155
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [M, N, O] | [1, 6, 9, 10] | ctrl | 2030 | 0.36155
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [M, N, O] | [1, 6, 9, 10] | ctrl | 2050 | 0.36155
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [M, N, O] | [1, 6, 9, 10] | lower | 2020 | 0.28711
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [M, N, O] | [1, 6, 9, 10] | lower | 2050 | 0.25521
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [M, N, O] | [1, 6, 9, 10] | upper | 2020 | 0.43598
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [M, N, O] | [1, 6, 9, 10] | upper | 2050 | 0.46788
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | L |  | ctrl | 2015 | 0.24458
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | L |  | ctrl | 2020 | 0.23394
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | L |  | ctrl | 2030 | 0.23394
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | L |  | ctrl | 2050 | 0.23394
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | L |  | lower | 2020 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | L |  | lower | 2050 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | L |  | upper | 2020 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | L |  | upper | 2050 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | L |  | ctrl | 2015 | 0.1276
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | L |  | ctrl | 2020 | 0.1276
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | L |  | ctrl | 2030 | 0.1276
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | L |  | ctrl | 2050 | 0.1276
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | L |  | lower | 2020 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | L |  | lower | 2050 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | L |  | upper | 2020 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | L |  | upper | 2050 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | R | [6, 11] | ctrl | 2015 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | R | [6, 11] | ctrl | 2020 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | R | [6, 11] | ctrl | 2030 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | R | [6, 11] | ctrl | 2050 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | R | [6, 11] | lower | 2020 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | R | [6, 11] | lower | 2050 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | R | [6, 11] | upper | 2020 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | R | [6, 11] | upper | 2050 | 0
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [11, 12, 13] | ctrl | 2015 | 6.3802
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [11, 12, 13] | ctrl | 2020 | 6.3802
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [11, 12, 13] | ctrl | 2030 | 6.3802
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [11, 12, 13] | ctrl | 2050 | 6.3802
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [11, 12, 13] | lower | 2020 | 2.7648
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [11, 12, 13] | lower | 2050 | 2.7648
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [11, 12, 13] | upper | 2020 | 9.0387
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [11, 12, 13] | upper | 2050 | 9.0387
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Cold start-up time [hours] | hours |  | H | 6 | ctrl | 2015 | 0.09
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Cold start-up time [hours] | hours |  | H | 6 | ctrl | 2020 | 0.09
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Cold start-up time [hours] | hours |  | H | 6 | ctrl | 2030 | 0.09
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Cold start-up time [hours] | hours |  | H | 6 | ctrl | 2050 | 0.09
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Cold start-up time [hours] | hours |  | H | 6 | lower | 2020 | 0.05
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Cold start-up time [hours] | hours |  | H | 6 | upper | 2020 | 0.17
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Minimum load (of full load) [] |  |  | G |  | ctrl | 2015 | 0.01
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Minimum load (of full load) [] |  |  | G |  | ctrl | 2020 | 0.01
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Minimum load (of full load) [] |  |  | G |  | ctrl | 2030 | 0.01
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Minimum load (of full load) [] |  |  | G |  | ctrl | 2050 | 0.01
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F | 6 | ctrl | 2015 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F | 6 | ctrl | 2020 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F | 6 | ctrl | 2030 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | F | 6 | ctrl | 2050 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | F | 6 | ctrl | 2015 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | F | 6 | ctrl | 2020 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | F | 6 | ctrl | 2030 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | F | 6 | ctrl | 2050 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [6, 7] | ctrl | 2015 | 0.02
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [6, 7] | ctrl | 2020 | 0.02
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [6, 7] | ctrl | 2030 | 0.02
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [6, 7] | ctrl | 2050 | 0.02
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [6, 7] | lower | 2020 | 0.01
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Regulation ability | Warm start-up time [hours] | hours |  | H | [6, 7] | upper | 2020 | 0.03
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | [4, 5] | ctrl | 2015 | 1
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | [4, 5] | ctrl | 2020 | 1
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | [4, 5] | ctrl | 2030 | 1
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  |  | [4, 5] | ctrl | 2050 | 1
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | D | 2 | ctrl | 2015 | 0.46
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | D | 2 | ctrl | 2020 | 0.46
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | D | 2 | ctrl | 2030 | 0.48
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | D | 2 | ctrl | 2050 | 0.48
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | C | 1 | ctrl | 2015 | 0.48
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | C | 1 | ctrl | 2020 | 0.48
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | C | 1 | ctrl | 2030 | 0.5
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | C | 1 | ctrl | 2050 | 0.5
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 3 | ctrl | 2015 | 0.009
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 3 | ctrl | 2020 | 0.009
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 3 | ctrl | 2030 | 0.009
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 3 | ctrl | 2050 | 0.009
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2015 | 200
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2020 | 200
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2030 | 200
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | [A, B] |  | ctrl | 2050 | 200
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E |  | ctrl | 2015 | 0.03
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E |  | ctrl | 2020 | 0.03
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E |  | ctrl | 2030 | 0.03
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | E |  | ctrl | 2050 | 0.03
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | F |  | ctrl | 2015 | 25
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | F |  | ctrl | 2020 | 25
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | F |  | ctrl | 2030 | 25
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | F |  | ctrl | 2050 | 25
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 2 | ctrl | 2015 | 315
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 2 | ctrl | 2020 | 315
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 2 | ctrl | 2030 | 315
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | F | 2 | ctrl | 2050 | 315
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 2 | ctrl | 2015 | 0.6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 2 | ctrl | 2020 | 0.6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 2 | ctrl | 2030 | 0.6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | F | 2 | ctrl | 2050 | 0.6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 2 | ctrl | 2015 | 75
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 2 | ctrl | 2020 | 75
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 2 | ctrl | 2030 | 75
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | F | 2 | ctrl | 2050 | 75
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2015 | 0.76
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2020 | 0.76
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2030 | 0.76
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 8 | ctrl | 2050 | 0.76
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | F | 2 | ctrl | 2015 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | F | 2 | ctrl | 2020 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | F | 2 | ctrl | 2030 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | F | 2 | ctrl | 2050 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [O, P] | 7 | ctrl | 2015 | 6911.9227
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [O, P] | 7 | ctrl | 2020 | 6911.9227
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [O, P] | 7 | ctrl | 2030 | 6646.0795
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [O, P] | 7 | ctrl | 2050 | 6380.2363
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [O, P] | 7 | lower | 2020 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [O, P] | 7 | lower | 2050 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [O, P] | 7 | upper | 2020 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | [O, P] | 7 | upper | 2050 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [L, M, N, R] | [7, 5, 9] | ctrl | 2015 | 0.54232
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [L, M, N, R] | [7, 5, 9] | ctrl | 2020 | 0.52105
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [L, M, N, R] | [7, 5, 9] | ctrl | 2030 | 0.49979
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [L, M, N, R] | [7, 5, 9] | ctrl | 2050 | 0.47852
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [L, M, N, R] | [7, 5, 9] | lower | 2020 | 0.42535
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [L, M, N, R] | [7, 5, 9] | lower | 2050 | 0.32965
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [L, M, N, R] | [7, 5, 9] | upper | 2020 | 0.62739
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [L, M, N, R] | [7, 5, 9] | upper | 2050 | 0.61676
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 2 | ctrl | 2015 | 0.35091
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 2 | ctrl | 2020 | 0.34028
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 2 | ctrl | 2030 | 0.32965
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 2 | ctrl | 2050 | 0.30838
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 2 | lower | 2020 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 2 | lower | 2050 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 2 | upper | 2020 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 2 | upper | 2050 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 2 | ctrl | 2015 | 0.19141
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 2 | ctrl | 2020 | 0.18077
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 2 | ctrl | 2030 | 0.18077
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 2 | ctrl | 2050 | 0.17014
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 2 | lower | 2020 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 2 | lower | 2050 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 2 | upper | 2020 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | F | 2 | upper | 2050 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | Q | 10 | ctrl | 2015 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | Q | 10 | ctrl | 2020 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | Q | 10 | ctrl | 2030 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | Q | 10 | ctrl | 2050 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | Q | 10 | lower | 2020 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | Q | 10 | lower | 2050 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | Q | 10 | upper | 2020 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | Q | 10 | upper | 2050 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [10, 11, 12] | ctrl | 2015 | 6.3802
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [10, 11, 12] | ctrl | 2020 | 6.3802
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [10, 11, 12] | ctrl | 2030 | 6.3802
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [10, 11, 12] | ctrl | 2050 | 6.3802
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [10, 11, 12] | lower | 2020 | 2.7648
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [10, 11, 12] | lower | 2050 | 2.7648
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [10, 11, 12] | upper | 2020 | 9.0387
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [10, 11, 12] | upper | 2050 | 9.0387
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  | I | 7 | ctrl | 2015 | 0.17
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  | I | 7 | ctrl | 2020 | 0.17
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  | I | 7 | ctrl | 2030 | 0.17
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  | I | 7 | ctrl | 2050 | 0.17
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [6, 7] | ctrl | 2015 | 0.015
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [6, 7] | ctrl | 2020 | 0.015
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [6, 7] | ctrl | 2030 | 0.015
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | H | [6, 7] | ctrl | 2050 | 0.015
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | 6 | ctrl | 2015 | 0.6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | 6 | ctrl | 2020 | 0.6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | 6 | ctrl | 2030 | 0.6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | 6 | ctrl | 2050 | 0.6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | 6 | ctrl | 2015 | 1
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | 6 | ctrl | 2020 | 1
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | 6 | ctrl | 2030 | 1
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | G | 6 | ctrl | 2050 | 1
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | I | 7 | ctrl | 2015 | 0.03
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | I | 7 | ctrl | 2020 | 0.03
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | I | 7 | ctrl | 2030 | 0.03
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  | I | 7 | ctrl | 2050 | 0.03
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  | F | 5 | ctrl | 2015 | 0.2
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  | F | 5 | ctrl | 2020 | 0.2
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  | F | 5 | ctrl | 2030 | 0.2
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Construction time [years] | years |  | F | 5 | ctrl | 2050 | 0.2
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | C | 3 | ctrl | 2015 | 0.39
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | C | 3 | ctrl | 2020 | 0.4
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | C | 3 | ctrl | 2030 | 0.41
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | C | 3 | ctrl | 2050 | 0.43
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [B, C] | [1, 2] | ctrl | 2015 | 0.41
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [B, C] | [1, 2] | ctrl | 2020 | 0.42
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [B, C] | [1, 2] | ctrl | 2030 | 0.43
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | [B, C] | [1, 2] | ctrl | 2050 | 0.45
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 4 | ctrl | 2015 | 0.0137
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 4 | ctrl | 2020 | 0.0137
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 4 | ctrl | 2030 | 0.0137
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Forced outage [] |  |  |  | 4 | ctrl | 2050 | 0.0137
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2015 | 100
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2020 | 100
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2030 | 100
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Generating capacity for one unit [MW_e] | MW_e |  | A |  | ctrl | 2050 | 100
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | D | 1 | ctrl | 2015 | 0.11
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | D | 1 | ctrl | 2020 | 0.11
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | D | 1 | ctrl | 2030 | 0.11
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | D | 1 | ctrl | 2050 | 0.11
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | E | 3 | ctrl | 2015 | 25
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | E | 3 | ctrl | 2020 | 25
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | E | 3 | ctrl | 2030 | 25
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Energy/technical data | Technical lifetime [years] | years |  | E | 3 | ctrl | 2050 | 25
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2015 | 1.7
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2020 | 1.7
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2030 | 1.7
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2050 | 1.7
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2015 | 1
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2020 | 1
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2030 | 1
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2050 | 1
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2015 | 48
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2020 | 48
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2030 | 48
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2050 | 48
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2015 | 0.1
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2020 | 0.1
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2030 | 0.1
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2050 | 0.1
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2015 | 0.43
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2020 | 0.43
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2030 | 0.43
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  |  | 11 | ctrl | 2050 | 0.43
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P | 9 | ctrl | 2015 | 8579.2911
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P | 9 | ctrl | 2020 | 8579.2911
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P | 9 | ctrl | 2030 | 8236.1194
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P | 9 | ctrl | 2050 | 7892.9478
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P | 9 | lower | 2020 | 0
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P | 9 | lower | 2050 | 0
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P | 9 | upper | 2020 | 0
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | P | 9 | upper | 2050 | 0
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [M, N, O] | [7, 9, 10] | ctrl | 2015 | 0.49979
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [M, N, O] | [7, 9, 10] | ctrl | 2020 | 0.47852
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [M, N, O] | [7, 9, 10] | ctrl | 2030 | 0.46788
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [M, N, O] | [7, 9, 10] | ctrl | 2050 | 0.43598
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [M, N, O] | [7, 9, 10] | lower | 2020 | 0.38281
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [M, N, O] | [7, 9, 10] | lower | 2050 | 0.30838
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [M, N, O] | [7, 9, 10] | upper | 2020 | 0.57422
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [M, N, O] | [7, 9, 10] | upper | 2050 | 0.57422
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 12 | ctrl | 2015 | 0.39345
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 12 | ctrl | 2020 | 0.37218
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 12 | ctrl | 2030 | 0.36155
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 12 | ctrl | 2050 | 0.34028
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 12 | lower | 2020 | 0
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 12 | lower | 2050 | 0
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 12 | upper | 2020 | 0
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 12 | upper | 2050 | 0
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 12 | ctrl | 2015 | 0.10634
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 12 | ctrl | 2020 | 0.10634
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 12 | ctrl | 2030 | 0.10634
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 12 | ctrl | 2050 | 0.095704
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 12 | lower | 2020 | 0
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 12 | lower | 2050 | 0
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 12 | upper | 2020 | 0
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 12 | upper | 2050 | 0
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 | 9 | ctrl | 2015 | 45.725
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 | 9 | ctrl | 2020 | 45.725
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 | 9 | ctrl | 2030 | 45.725
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 | 9 | ctrl | 2050 | 45.725
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 | 9 | lower | 2020 | 0
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 | 9 | lower | 2050 | 0
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 | 9 | upper | 2020 | 0
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 | 9 | upper | 2050 | 0
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [5, 9, 10] | ctrl | 2015 | 4.7852
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [5, 9, 10] | ctrl | 2020 | 4.7852
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [5, 9, 10] | ctrl | 2030 | 4.7852
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [5, 9, 10] | ctrl | 2050 | 4.7852
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [5, 9, 10] | lower | 2020 | 3.7218
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [5, 9, 10] | lower | 2050 | 3.7218
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [5, 9, 10] | upper | 2020 | 5.3169
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 | [5, 9, 10] | upper | 2050 | 5.3169
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  | L | [1, 6, 8] | ctrl | 2015 | 0.17
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  | L | [1, 6, 8] | ctrl | 2020 | 0.17
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  | L | [1, 6, 8] | ctrl | 2030 | 0.17
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  | L | [1, 6, 8] | ctrl | 2050 | 0.17
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  | L | [1, 6, 8] | lower | 2020 | 0.12
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Cold start-up time [hours] | hours |  | L | [1, 6, 8] | upper | 2020 | 0.19
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | I | 8 | ctrl | 2015 | 0.25
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | I | 8 | ctrl | 2020 | 0.2
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | I | 8 | ctrl | 2030 | 0.2
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Minimum load (of full load) [] |  |  | I | 8 | ctrl | 2050 | 0.2
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | 5 | ctrl | 2015 | 0.3
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | 5 | ctrl | 2020 | 0.3
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | 5 | ctrl | 2030 | 0.3
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  | G | 5 | ctrl | 2050 | 0.3
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [5, 6, 7] | ctrl | 2015 | 0.3
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [5, 6, 7] | ctrl | 2020 | 0.3
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [5, 6, 7] | ctrl | 2030 | 0.3
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [5, 6, 7] | ctrl | 2050 | 0.3
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [5, 6, 7] | lower | 2020 | 0.15
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  | H | [5, 6, 7] | upper | 2020 | 0.5
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  |  | [8, 9, 10] | ctrl | 2015 | 0.08
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  |  | [8, 9, 10] | ctrl | 2020 | 0.08
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  |  | [8, 9, 10] | ctrl | 2030 | 0.08
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  |  | [8, 9, 10] | ctrl | 2050 | 0.08
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  |  | [8, 9, 10] | lower | 2020 | 0.08
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Regulation ability | Warm start-up time [hours] | hours |  |  | [8, 9, 10] | upper | 2020 | 0.11
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | 18 | ctrl | 2015 | 0.38
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | 18 | ctrl | 2020 | 0.39
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | 18 | ctrl | 2030 | 0.4
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | 18 | ctrl | 2050 | 0.42
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | 18 | lower | 2020 | 0.385
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Energy/technical data | Electrical efficiency (net, annual average) [] |  |  | A | 18 | upper | 2020 | 0.4
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | 18 | ctrl | 2015 | 0.04
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | 18 | ctrl | 2020 | 0.41
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | 18 | ctrl | 2030 | 0.42
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | 18 | ctrl | 2050 | 0.44
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | 18 | lower | 2020 | 0.405
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Energy/technical data | Electrical efficiency (net, name plate) [] |  |  | A | 18 | upper | 2020 | 0.42
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2015 | 3
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2020 | 3
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2030 | 3
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | CH4 [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2050 | 3
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2015 | 0.6
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2020 | 0.6
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2030 | 0.6
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | N2O [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2050 | 0.6
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2015 | 230
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2020 | 230
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2030 | 230
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | NOX [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2050 | 230
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2015 | 5
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2020 | 5
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2030 | 5
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | Particles [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2050 | 5
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2015 | 23
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2020 | 23
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2030 | 23
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Environment | SO2 [g/GJ_i] | g/GJ_i |  | B | 11 | ctrl | 2050 | 23
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2015 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2020 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2030 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | ctrl | 2050 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2020 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | lower | 2050 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2020 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Fixed O&M (*total) [EUR/MW_e/y] | EUR/MW_e/y | 2020 | 0 |  | upper | 2050 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, D] | 19 | ctrl | 2015 | 0.41472
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, D] | 19 | ctrl | 2020 | 0.40408
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, D] | 19 | ctrl | 2030 | 0.38281
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, D] | 19 | ctrl | 2050 | 0.36155
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, D] | 19 | lower | 2020 | 0.31901
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, D] | 19 | lower | 2050 | 0.25521
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, D] | 19 | upper | 2020 | 0.47852
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (*total) [MEUR/MW_e] | MEUR/MW_e | 2020 | [C, D] | 19 | upper | 2050 | 0.47852
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 20 | ctrl | 2015 | 0.31901
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 20 | ctrl | 2020 | 0.31901
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 20 | ctrl | 2030 | 0.29774
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 20 | ctrl | 2050 | 0.28711
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 20 | lower | 2020 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 20 | lower | 2050 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 20 | upper | 2020 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (equipment) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 20 | upper | 2050 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 20 | ctrl | 2015 | 0.095704
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 20 | ctrl | 2020 | 0.08507
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 20 | ctrl | 2030 | 0.08507
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 20 | ctrl | 2050 | 0.08507
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 20 | lower | 2020 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 20 | lower | 2050 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 20 | upper | 2020 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Nominal investment (installation) [MEUR/MW_e] | MEUR/MW_e | 2020 | 0 | 20 | upper | 2050 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | ctrl | 2015 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | ctrl | 2020 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | ctrl | 2030 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | ctrl | 2050 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | lower | 2020 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | lower | 2050 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | upper | 2020 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Startup cost [EUR/MW_e/startup] | EUR/MW_e/startup | 2020 | 0 |  | upper | 2050 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2015 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2020 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2030 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | ctrl | 2050 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | lower | 2020 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | lower | 2050 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | upper | 2020 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Financial data | Variable O&M (*total) [EUR/MWh_e] | EUR/MWh_e | 2020 | 0 |  | upper | 2050 | 0
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Regulation ability | Cold start-up time [hours] | hours |  | A | 18 | ctrl | 2015 | 0.18
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Regulation ability | Cold start-up time [hours] | hours |  | A | 18 | ctrl | 2020 | 0.18
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Regulation ability | Cold start-up time [hours] | hours |  | A | 18 | ctrl | 2030 | 0.18
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Regulation ability | Cold start-up time [hours] | hours |  | A | 18 | ctrl | 2050 | 0.18
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Regulation ability | Warm start-up time [hours] | hours |  | A | 18 | ctrl | 2015 | 0.09
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Regulation ability | Warm start-up time [hours] | hours |  | A | 18 | ctrl | 2020 | 0.09
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Regulation ability | Warm start-up time [hours] | hours |  | A | 18 | ctrl | 2030 | 0.09
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Regulation ability | Warm start-up time [hours] | hours |  | A | 18 | ctrl | 2050 | 0.09

## Notes
ws | description
01 Coal CHP | A. The Cb values have been calculated from the electricity efficiencies in condensation mode, the Cv values and a total efficiency (electricity plus heat) in full back-pressure mode of 90%. Cf. Annex 1.
01 Coal CHP | B. The data for SO2 and NOx emissions assume flue gas desulphurisation (wet gypsum) and DeNOx equipment of the "high dust" SCR type.
01 Coal CHP | C. Supercritical in 2010 and ultra-supercritical from 2020.
01 Coal CHP | D. Please refer to section 'Regulation ability' in the above qualitative description.
01 Coal CHP | E. Outage rates are generally about 5% for plants that are 10-20 years old. Unless the plant is refurbished, the rate increases to 20% for plants that are 40 years old (ref. 7)
01 Coal CHP | F. It is assumed that the cost is falling by 0.2 % p.a. \n Defaltor 2011-2015: 1.059
01 Coal CHP | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
01 Coal CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
01 Coal CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
03a Coal to wood pellets exi bo | A. Value depend on the original plant. Value indicate the estimated change from the original value (unit is the same as the paramter).
03a Coal to wood pellets exi bo | B. Typically the electricity efficiency will be 1-2 % point lower than that of the plant prior to conversion. The thermal efficiency is typically unchanged, thus the Cb value decreases, meaning more heat is produced compared to electricity.
03a Coal to wood pellets exi bo | C. Values for year 2050 are not considered relevant since it is assumed that all coal fired plants in Denmark have been rebuilt or decommissioned.
03a Coal to wood pellets exi bo | D. Some additional under roof space (or silos) will be required for storage of pellets compared to coal (estimated 50%-100% extra m3 storage). But not more floor space (m2).
03a Coal to wood pellets exi bo | E. The nominal investment assumes that the original plant is aged and therefore include investment for a general life time extension campaign
03a Coal to wood pellets exi bo | F. The variable O&M costs will be similar to those of the original plant, however fixed O&M costs are likely to increase by 10-20%
03a Coal to wood pellets exi bo | G. Assumed the same emission values from the datasheet of new biomass plants (wood chips). See references and notes in the datasheet '09 Biomass CHP, Steam Turbine - Large steam turbine, Woodchips'.
03a Coal to wood pellets exi bo | I. It is assumed that plants that are refurbished in 2015 have an electric efficiency of 41% and a CB coefficient of 0.556. Plants refurbished in 2020 have an electric efficiency of 42% and a CB coefficient of 0.64. Plants refurbished in 2030 have an electric efficiency of 44% and a CB coefficien...
03a Coal to wood pellets exi bo | J. It is assumed that that Flue Gas Desulphurization plant is bypassed (stopped) due to low Sulphur content in wood pellet fuel
03a Coal to wood pellets exi bo | K. O&M cost and CAPEX has been estimated by Ramboll in April 2019 based on input from DE/Ørsted and data from UK Department for Business, Energy & Industry strategy (BEIS) in their Electricity Generation Cost report from 2016.
03a Coal to wood pellets exi bo | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
03a Coal to wood pellets exi bo | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
03a Coal to wood pellets exi bo | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
03b Coal to wood chips n. boile | A. Value depend on the original plant.
03b Coal to wood chips n. boile | B. Typically the electricity efficiency will be 1-2 % point lower than that of the plant prior to conversion. The thermal efficiency will typically increase to around 105%. thus the Cb value decreases. meaning more heat is produced compared to electricity. This is mainly due to implementation o...
03b Coal to wood chips n. boile | C. Values for year 2050 are not considered relevant since it is assumed that all coal fired plants in Denmark have been rebuilt or decommissioned.
03b Coal to wood chips n. boile | D. Some additional space will be required for storage of chips (estimated 50%-100% extra).
03b Coal to wood chips n. boile | E. The nominal investment assumes that the original plant is aged and therefore include investment for a general life time extension campaign
03b Coal to wood chips n. boile | F. The fixed O&M costs are likely to increase by 10-20%. whereas the variable O&M costs are likely to increase approx. 50%.
03b Coal to wood chips n. boile | G. Emission values from the datasheet of new CFB biomass plants. See references and notes in the datasheet 'Large Biomass Circulating Fluidized Bed Combustion Systems (CFBC) for wood'.
03b Coal to wood chips n. boile | I. The regulation time of the boiler will often increase due to slower burning of chips compared to pulverized fuel. Depending of the other thermal limitations in the cycle (e.g. in the turbines) this will have no change or an increase in the regulation time.
03b Coal to wood chips n. boile | J. It is assumed that plants that are refurbished in 2015 have an electric efficiency of 41% and a CB coefficient of 0.56. Plants refurbished in 2020 have an electric efficiency of 42% and a CB coefficient of 0.64. Plants refurbished in 2030 have an electric efficiency of 44% and a CB coefficient...
03b Coal to wood chips n. boile | K. O&M cost are copied from 09 Large Wood Chip CHP corrected with efficiency. Note that all financial data are absolute values and not relative to coal.
03b Coal to wood chips n. boile | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
03b Coal to wood chips n. boile | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
03b Coal to wood chips n. boile | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
03c coal to wood chips exi. boi | A. Value depend on the original plant.
03c coal to wood chips exi. boi | B. Typically the electricity efficiency will be 3-4 % point lower than that of the plant prior to conversion. The thermal efficiency is increased to approximately 100% because of flue gas condensation in drying process, thus the Cb value decreases, meaning more heat is produced compared to elect...
03c coal to wood chips exi. boi | C. Values for year 2050 are not considered relevant since it is assumed that all coal fired plants in Denmark have been rebuilt or decommissioned.
03c coal to wood chips exi. boi | D. Some additional space will be required for storage of chips (estimated 50%-100% extra) and for the drying plant.
03c coal to wood chips exi. boi | E. The nominal investment assumes that the original plant is aged and therefore include investment for a general life time extension campaign
03c coal to wood chips exi. boi | F. Both variable and fixed O&M costs are likely to increase by 40-50% from the original plant.
03c coal to wood chips exi. boi | G. Assumed the same emission values from the datasheet of new biomass plants (wood chips). See references and notes in the datasheet '09 Biomass CHP, Steam Turbine - Large steam turbine, Woodchips'.
03c coal to wood chips exi. boi | I. It is assumed that plants that are refurbished in 2015 have an electric efficiency of 41% and a CB coefficient of 0.57. Plants refurbished in 2020 have an electric efficiency of 42% and a CB coefficient of 0.64. Plants refurbished in 2030 have an electric efficiency of 44% and a CB coefficient...
03c coal to wood chips exi. boi | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
03c coal to wood chips exi. boi | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
03c coal to wood chips exi. boi | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
03d coal to wood chips exi. boi | A. Based on existing converted coal plant 50-90 MW capacity
03d coal to wood chips exi. boi | B. The estimated electrcial efficiency is 27 %. It is assumed that plants are equipped with Flue Gas Condensation having total efficiency of 105 %
03d coal to wood chips exi. boi | C. Values are based on Data sheet for Wood Chips CHP, Large
03d coal to wood chips exi. boi | D. O&M data are based data sheet 09 Wood chips CHP, Large, the specific values based on electricity has been corrected base on efficiency
03d coal to wood chips exi. boi | E. Uncertainty estimate applies for 2015 value
03d coal to wood chips exi. boi | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
03d coal to wood chips exi. boi | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
03d coal to wood chips exi. boi | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
04 Gas turb. simple cycle, L | A. Very low efficiency at low loads and often increased Nox emisison
04 Gas turb. simple cycle, L | B. Insurance excluded, unknown. Daily start assumed
04 Gas turb. simple cycle, L | C. Power related
04 Gas turb. simple cycle, L | D. Based on Dry Low NOx (DLN) techniques
04 Gas turb. simple cycle, L | E. Technical- and design life most often > 25 years
04 Gas turb. simple cycle, L | F. Electrical output
04 Gas turb. simple cycle, L | G. Combined with DGC assumptions, CHP configuration
04 Gas turb. simple cycle, L | H. GT's (5 MWe) are available including internal recuperator; the electrical nominal efficiency is then 37 % (LCV basis)
04 Gas turb. simple cycle, L | I. No data available, no known use
04 Gas turb. simple cycle, L | J. Not relevant for this CHP configuration
04 Gas turb. simple cycle, L | K. No data available
04 Gas turb. simple cycle, L | L. DGC Estimate
04 Gas turb. simple cycle, L | M. Air preheating by internal recuperation included
04 Gas turb. simple cycle, L | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
04 Gas turb. simple cycle, L | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
04 Gas turb. simple cycle, L | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
04 Gas turb. simple cycle Sm-Me | A. Very low efficiency at low loads and often increased Nox emisison
04 Gas turb. simple cycle Sm-Me | B. Insurance excluded, unknown. Daily start assumed
04 Gas turb. simple cycle Sm-Me | C. Power related
04 Gas turb. simple cycle Sm-Me | D. Based on Dry Low NOx (DLN) techniques
04 Gas turb. simple cycle Sm-Me | E. Technical- and design life most often > 25 years
04 Gas turb. simple cycle Sm-Me | F. Electrical output
04 Gas turb. simple cycle Sm-Me | G. Combined with DGC assumptions, CHP configuration
04 Gas turb. simple cycle Sm-Me | H. GT's (5 MWe) are available including internal recuperator; the electrical nominal efficiency is then 37 % (LCV basis)
04 Gas turb. simple cycle Sm-Me | I. No data available, no known use
04 Gas turb. simple cycle Sm-Me | J. Not relevant for this CHP configuration
04 Gas turb. simple cycle Sm-Me | K. No data available
04 Gas turb. simple cycle Sm-Me | L. DGC Estimate
04 Gas turb. simple cycle Sm-Me | M. Air preheating by internal recuperation included
04 Gas turb. simple cycle Sm-Me | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
04 Gas turb. simple cycle Sm-Me | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
04 Gas turb. simple cycle Sm-Me | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
04 Gas turb. simple cycle Micro | A. Very low efficiency at low loads and often increased Nox emisison
04 Gas turb. simple cycle Micro | B. Insurance excluded, unknown. Daily start assumed
04 Gas turb. simple cycle Micro | C. Power related
04 Gas turb. simple cycle Micro | D. Based on Dry Low NOx (DLN) techniques
04 Gas turb. simple cycle Micro | E. Technical- and design life most often > 25 years
04 Gas turb. simple cycle Micro | F. Electrical output
04 Gas turb. simple cycle Micro | G. Combined with DGC assumptions, CHP configuration
04 Gas turb. simple cycle Micro | H. GT's (5 MWe) are available including internal recuperator; the electrical nominal efficiency is then 37 % (LCV basis)
04 Gas turb. simple cycle Micro | I. No data available, no known use
04 Gas turb. simple cycle Micro | J. Not relevant for this CHP configuration
04 Gas turb. simple cycle Micro | K. No data available
04 Gas turb. simple cycle Micro | L. DGC Estimate
04 Gas turb. simple cycle Micro | M. Air preheating by internal recuperation included
04 Gas turb. simple cycle Micro | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
04 Gas turb. simple cycle Micro | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
04 Gas turb. simple cycle Micro | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
05 Gas turb. CC, steam extract. | A. Low efficiency at low loads and often increased NOx emission
05 Gas turb. CC, steam extract. | B. Limited availability of data
05 Gas turb. CC, steam extract. | C. Power related
05 Gas turb. CC, steam extract. | D. Based on Dry Low NOx (DLN) techniques
05 Gas turb. CC, steam extract. | E. Technical- and design life most often > 25 years
05 Gas turb. CC, steam extract. | F. Electrical output
05 Gas turb. CC, steam extract. | G. CHP configuration, Including DGC assumptions
05 Gas turb. CC, steam extract. | H. Manufacturers says down to 30 minute
05 Gas turb. CC, steam extract. | I. No data available
05 Gas turb. CC, steam extract. | J. Data on Cv from the 2012 version roughly adjusted for higher electricity efficiency
05 Gas turb. CC, steam extract. | K. No known use
05 Gas turb. CC, steam extract. | L. No Relevance for Back Pressure Lay Out
05 Gas turb. CC, steam extract. | M. Upward regulation is typically 10 - 15 %/min, while downward regulation is > 30 % /min
05 Gas turb. CC, steam extract. | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
05 Gas turb. CC, steam extract. | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
05 Gas turb. CC, steam extract. | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
05 Gas turb. CC, Back-pressure | A. Low efficiency at low loads and often increased NOx emission
05 Gas turb. CC, Back-pressure | B. Limited availability of data
05 Gas turb. CC, Back-pressure | C. Power related
05 Gas turb. CC, Back-pressure | D. Based on Dry Low NOx (DLN) techniques
05 Gas turb. CC, Back-pressure | E. Technical- and design life most often > 25 years
05 Gas turb. CC, Back-pressure | F. Electrical output
05 Gas turb. CC, Back-pressure | G. CHP configuration, Including DGC assumptions
05 Gas turb. CC, Back-pressure | H. Manufacturers says down to 30 minute
05 Gas turb. CC, Back-pressure | I. No data available
05 Gas turb. CC, Back-pressure | J. Data on Cv from the 2012 version roughly adjusted for higher electricity efficiency
05 Gas turb. CC, Back-pressure | K. No known use
05 Gas turb. CC, Back-pressure | L. No Relevance for Back Pressure Lay Out
05 Gas turb. CC, Back-pressure | M. Upward regulation is typically 10 - 15 %/min, while downward regulation is > 30 % /min
05 Gas turb. CC, Back-pressure | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
05 Gas turb. CC, Back-pressure | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
05 Gas turb. CC, Back-pressure | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
06 Gas engines, natural gas | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
06 Gas engines, natural gas | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
06 Gas engines, natural gas | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
06 Gas engines, natural gas | D. Technical- and design life most often > 25 years
06 Gas engines, natural gas | E. For a medium size engine; small engines with less thermal mass might be faster
06 Gas engines, natural gas | F. When operating 4000 hours a year
06 Gas engines, natural gas | G. Only relevant for steam based CHP
06 Gas engines, natural gas | H. No data available
06 Gas engines, natural gas | I. DGC estimate for years 2030, 2050
06 Gas engines, natural gas | J. No known use, data from n-gas engines
06 Gas engines, natural gas | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
06 Gas engines, natural gas | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
06 Gas engines, natural gas | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
06 Gas engines, natural gas | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
06 Gas engines, natural gas | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
06 Gas engines, natural gas | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
06 Gas engines, biogas | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
06 Gas engines, biogas | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
06 Gas engines, biogas | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
06 Gas engines, biogas | D. Technical- and design life most often > 25 years
06 Gas engines, biogas | E. For a medium size engine; small engines with less thermal mass might be faster
06 Gas engines, biogas | F. When operating 4000 hours a year
06 Gas engines, biogas | G. Only relevant for steam based CHP
06 Gas engines, biogas | H. No data available
06 Gas engines, biogas | I. DGC estimate for years 2030, 2050
06 Gas engines, biogas | J. No known use, data from n-gas engines
06 Gas engines, biogas | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
06 Gas engines, biogas | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
06 Gas engines, biogas | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
06 Gas engines, biogas | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
06 Gas engines, biogas | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
06 Gas engines, biogas | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Large, 40 degree | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
08 WtE CHP, Large, 40 degree | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
08 WtE CHP, Large, 40 degree | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
08 WtE CHP, Large, 40 degree | D. Technical- and design life most often > 25 years
08 WtE CHP, Large, 40 degree | E. For a medium size engine; small engines with less thermal mass might be faster
08 WtE CHP, Large, 40 degree | F. When operating 4000 hours a year
08 WtE CHP, Large, 40 degree | G. Only relevant for steam based CHP
08 WtE CHP, Large, 40 degree | H. No data available
08 WtE CHP, Large, 40 degree | I. DGC estimate for years 2030, 2050
08 WtE CHP, Large, 40 degree | J. No known use, data from n-gas engines
08 WtE CHP, Large, 40 degree | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
08 WtE CHP, Large, 40 degree | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
08 WtE CHP, Large, 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Large, 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Large, 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Large, 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Large, 40 degree | A. Assumed lower heating value 10.6 MJ/kg, waste input 74.7 tph = tonnes per hour (incineration capacity) divided in two, equally sized furnace/boiler units , corresponding to thermal input of 2x110 MW. One common turbine/generator set is foreseen. Live steam pressure in base case 50 bara, temper...
08 WtE CHP, Large, 40 degree | B. With flue gas condensation (condensation through heat exchange with DH-water, only) and a back-pressure turbine/condenser system optimised at DH return temperature 40°C and flow 80°C.
08 WtE CHP, Large, 40 degree | C. Annual average heat output is higher than nameplate because the total efficiency is constant, and the annual average electricity generation is lower than nameplate electricity output. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
08 WtE CHP, Large, 40 degree | D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 ...
08 WtE CHP, Large, 40 degree | E. Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
08 WtE CHP, Large, 40 degree | F. Regulation and start-up refer to electricity generation controlled by the turbine operation.The WtE facility would usually be operating at 100% thermal input, and the electricity output is controlled to the desired level by use of turbine by-pass, by which excess steam is used to produce DH-...
08 WtE CHP, Large, 40 degree | G. The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (in stead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the re...
08 WtE CHP, Large, 40 degree | H. Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream the flue gas treatment system. Sulphur content in fuel 270 g/GJ.
08 WtE CHP, Large, 40 degree | I. Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2030 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2050. The SCR-technology entails additional investment.
08 WtE CHP, Large, 40 degree | J. N2O is expected to be related primarily to the use of SNCR using urea injection. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
08 WtE CHP, Large, 40 degree | K. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues f...
08 WtE CHP, Large, 40 degree | L. Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
08 WtE CHP, Large, 40 degree | M. Installation includes civils works (including waste bunker) and project cost.
08 WtE CHP, Large, 40 degree | N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract.
08 WtE CHP, Large, 40 degree | O. Binary value where 1 = yes and 0 = no
08 WtE CHP, Large, 40 degree | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
08 WtE CHP, Large, 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Large, 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Large, 50 degree | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
08 WtE CHP, Large, 50 degree | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
08 WtE CHP, Large, 50 degree | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
08 WtE CHP, Large, 50 degree | D. Technical- and design life most often > 25 years
08 WtE CHP, Large, 50 degree | E. For a medium size engine; small engines with less thermal mass might be faster
08 WtE CHP, Large, 50 degree | F. When operating 4000 hours a year
08 WtE CHP, Large, 50 degree | G. Only relevant for steam based CHP
08 WtE CHP, Large, 50 degree | H. No data available
08 WtE CHP, Large, 50 degree | I. DGC estimate for years 2030, 2050
08 WtE CHP, Large, 50 degree | J. No known use, data from n-gas engines
08 WtE CHP, Large, 50 degree | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
08 WtE CHP, Large, 50 degree | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
08 WtE CHP, Large, 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Large, 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Large, 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Large, 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Large, 50 degree | A. Assumed lower heating value 10.6 MJ/kg, waste input 74.7 tph = tonnes per hour (incineration capacity) divided in two, equally sized furnace/boiler units , corresponding to thermal input of 2x110 MW. One common turbine/generator set is foreseen. Live steam pressure in base case 50 bara, temper...
08 WtE CHP, Large, 50 degree | B. With flue gas condensation (condensation through heat exchange with DH-water, only) and a back-pressure turbine/condenser system optimised at DH return temperature 50°C and flow 100°C.
08 WtE CHP, Large, 50 degree | C. Annual average heat output is higher than nameplate because the total efficiency is constant, and the annual average electricity generation is lower than nameplate electricity output. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
08 WtE CHP, Large, 50 degree | D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 ...
08 WtE CHP, Large, 50 degree | E. Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
08 WtE CHP, Large, 50 degree | F. Regulation and start-up refer to electricity generation controlled by the turbine operation.The WtE facility would usually be operating at 100% thermal input, and the electricity output is controlled to the desired level by use of turbine by-pass, by which excess steam is used to produce DH-...
08 WtE CHP, Large, 50 degree | G. The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (in stead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the re...
08 WtE CHP, Large, 50 degree | H. Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream the flue gas treatment system. Sulphur content in fuel 270 g/GJ.
08 WtE CHP, Large, 50 degree | I. Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2030 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2050. The SCR-technology entails additional investment.
08 WtE CHP, Large, 50 degree | J. N2O is expected to be related primarily to the use of SNCR using urea injection. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
08 WtE CHP, Large, 50 degree | K. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues f...
08 WtE CHP, Large, 50 degree | L. Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
08 WtE CHP, Large, 50 degree | M. Installation includes civils works (including waste bunker) and project cost.
08 WtE CHP, Large, 50 degree | N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract.
08 WtE CHP, Large, 50 degree | O. Binary value where 1 = yes and 0 = no
08 WtE CHP, Large, 50 degree | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
08 WtE CHP, Large, 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Large, 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Medium | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
08 WtE CHP, Medium | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
08 WtE CHP, Medium | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
08 WtE CHP, Medium | D. Technical- and design life most often > 25 years
08 WtE CHP, Medium | E. For a medium size engine; small engines with less thermal mass might be faster
08 WtE CHP, Medium | F. When operating 4000 hours a year
08 WtE CHP, Medium | G. Only relevant for steam based CHP
08 WtE CHP, Medium | H. No data available
08 WtE CHP, Medium | I. DGC estimate for years 2030, 2050
08 WtE CHP, Medium | J. No known use, data from n-gas engines
08 WtE CHP, Medium | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
08 WtE CHP, Medium | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
08 WtE CHP, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Medium | A. Assumed lower heating value 10.6 MJ/kg, waste input 27.2 tph = tonnes per hour (incineration capacity), corresponding to thermal input of 80 MW. Live steam pressure in base case 50 bara, temperature 425 °C of 2015 and 2020, increasing to 440 °C and 450 °C, in 2030 and 2050, restpectively. Effi...
08 WtE CHP, Medium | B. With flue gas condensation (condensation through heat exchange with DH-water, only) and a back-pressure turbine/condenser system optimised for DH return temperature 40°C and flow 80°C
08 WtE CHP, Medium | C. Annual average heat output is higher than nameplate because the total efficiency is constant, and the annual average electricity generation is lower than nameplate electricity output. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
08 WtE CHP, Medium | D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 ...
08 WtE CHP, Medium | E. Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
08 WtE CHP, Medium | F. Regulation and start-up refer to electricity generation controlled by the turbine operation.The WtE facility would usually be operating at 100% thermal input, and the electricity output is controlled to the desired level by use of turbine by-pass, by which excess steam is used to produce DH-...
08 WtE CHP, Medium | G. The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (in stead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the re...
08 WtE CHP, Medium | H. Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream the flue gas treatment system. Sulphur content in fuel 270 g/GJ.
08 WtE CHP, Medium | I. Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2020 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2030. The SCR-technology entails additional investment.
08 WtE CHP, Medium | J. N2O is expected to be related primarily to the use of SNCR using urea injection. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
08 WtE CHP, Medium | K. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues f...
08 WtE CHP, Medium | L. Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
08 WtE CHP, Medium | M. Installation includes civils works (including waste bunker) and project cost
08 WtE CHP, Medium | N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract.
08 WtE CHP, Medium | O. Through a turbine by-pass all the produced steam energy can be used for District Heat production. It can be assumed that all electricity production is converted into heat production in by-pass.
08 WtE CHP, Medium | P. Binary value where 1 = yes and 0 = no
08 WtE CHP, Medium | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
08 WtE CHP, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Small | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
08 WtE CHP, Small | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
08 WtE CHP, Small | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
08 WtE CHP, Small | D. Technical- and design life most often > 25 years
08 WtE CHP, Small | E. For a medium size engine; small engines with less thermal mass might be faster
08 WtE CHP, Small | F. When operating 4000 hours a year
08 WtE CHP, Small | G. Only relevant for steam based CHP
08 WtE CHP, Small | H. No data available
08 WtE CHP, Small | I. DGC estimate for years 2030, 2050
08 WtE CHP, Small | J. No known use, data from n-gas engines
08 WtE CHP, Small | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
08 WtE CHP, Small | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
08 WtE CHP, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Small | A. Assumed lower heating value 10.6 MJ/kg, waste input 11.9 tph = tonnes per hour (incineration capacity), corresponding to thermal input of 35 MW. Live steam pressure in base case 50 bara, temperature 425 °C of 2015 and 2020, increasing to 440 °C and 450 °C, in 2030 and 2050, respectively. Effic...
08 WtE CHP, Small | B. With flue gas condensation (condensation through heat exchange with DH-water, only) and a back-pressure turbine/condenser system optimised for DH return temperature 40°C and flow 80°C
08 WtE CHP, Small | C. Annual average heat output is higher than nameplate because the total efficiency is constant, and the annual average electricity generation is lower than nameplate electricity output. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
08 WtE CHP, Small | D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 ...
08 WtE CHP, Small | E. Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
08 WtE CHP, Small | F. Regulation and start-up refer to electricity generation controlled by the turbine operation.The WtE facility would usually be operating at 100% thermal input, and the electricity output is controlled to the desired level by use of turbine by-pass, by which excess steam is used to produce DH-...
08 WtE CHP, Small | G. The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (in stead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the re...
08 WtE CHP, Small | H. Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream the flue gas treatment system. Sulphur content in fuel 270 g/GJ.
08 WtE CHP, Small | I. Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2020 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2030. The SCR-technology entails additional investment.
08 WtE CHP, Small | J. N2O is expected to be related primarily to the use of SNCR using urea injection. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
08 WtE CHP, Small | K. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues f...
08 WtE CHP, Small | L. Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
08 WtE CHP, Small | M. Installation includes civils works (including waste bunker) and project cost
08 WtE CHP, Small | N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract..
08 WtE CHP, Small | O. Binary value where 1 = yes and 0 = no
08 WtE CHP, Small | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
08 WtE CHP, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE CHP, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE HOP | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
08 WtE HOP | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
08 WtE HOP | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
08 WtE HOP | D. Technical- and design life most often > 25 years
08 WtE HOP | E. For a medium size engine; small engines with less thermal mass might be faster
08 WtE HOP | F. When operating 4000 hours a year
08 WtE HOP | G. Only relevant for steam based CHP
08 WtE HOP | H. No data available
08 WtE HOP | I. DGC estimate for years 2030, 2050
08 WtE HOP | J. No known use, data from n-gas engines
08 WtE HOP | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
08 WtE HOP | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
08 WtE HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE HOP | A. Assumed lower heating value 10.6 MJ/kg, waste input 11.9 tph = tonnes per hour (incineration capacity), corresponding to thermal input of 35 MW. Efficiencies refer to lower heating value.
08 WtE HOP | B. With flue gas condensation (condensation through heat exchange with DH-water, only), DH return temperature 40°C and flow 80°C.
08 WtE HOP | C. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency.
08 WtE HOP | D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 ...
08 WtE HOP | E. Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
08 WtE HOP | G. The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (instead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the req...
08 WtE HOP | H. Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream of the flue gas treatment system. Sulphur content in fuel 270 g/GJ
08 WtE HOP | I. Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2020 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2030. The SCR-technology entails additional investment.
08 WtE HOP | J. N2O is expected to be related primarily to the use of SNCR. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
08 WtE HOP | K. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate ...
08 WtE HOP | L. Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
08 WtE HOP | M. Installation includes civils works (including waste bunker) and project cost .
08 WtE HOP | N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract.
08 WtE HOP | O. Binary value where 1 = yes and 0 = no
08 WtE HOP | P. Reference to heat output because of the lack of electricity production.
08 WtE HOP | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
08 WtE HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
08 WtE HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Large 40 degree | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
09a Wood Chips, Large 40 degree | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
09a Wood Chips, Large 40 degree | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
09a Wood Chips, Large 40 degree | D. Technical- and design life most often > 25 years
09a Wood Chips, Large 40 degree | E. For a medium size engine; small engines with less thermal mass might be faster
09a Wood Chips, Large 40 degree | F. When operating 4000 hours a year
09a Wood Chips, Large 40 degree | G. Only relevant for steam based CHP
09a Wood Chips, Large 40 degree | H. No data available
09a Wood Chips, Large 40 degree | I. DGC estimate for years 2030, 2050
09a Wood Chips, Large 40 degree | J. No known use, data from n-gas engines
09a Wood Chips, Large 40 degree | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
09a Wood Chips, Large 40 degree | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips, Large 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Large 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Large 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Large 40 degree | A. The boiler in the plant is a circulating fluid bed boiler (CFB) producing steam to be used in a subsequent back-pressure steam turbine without steam re-heat. The system is optimised at DH return temperature 40°C and flow 80°C.\n At DH return temperature 40 °C and flow 80 °C, for year 2015, th...
09a Wood Chips, Large 40 degree | B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
09a Wood Chips, Large 40 degree | C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
09a Wood Chips, Large 40 degree | D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
09a Wood Chips, Large 40 degree | E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator). Warm start-up time is particularly low for fluid bed types of plants.
09a Wood Chips, Large 40 degree | F. It is to be expected that the NOx level is low from the CFB, and that the necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 20 g/GJ, in which case SCR is used. From 2017 NOx (and other emissions) must fulfill the BAT_AEL values of the LCP BREF n...
09a Wood Chips, Large 40 degree | G. Warm start is starting with a glowing bed and a warm deaerator.
09a Wood Chips, Large 40 degree | H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power productio...
09a Wood Chips, Large 40 degree | I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
09a Wood Chips, Large 40 degree | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. \nFinancial data and Technological specific data...
09a Wood Chips, Large 40 degree | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. \nThe additional investment is listed in the bottom row.
09a Wood Chips, Large 40 degree | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity an...
09a Wood Chips, Large 40 degree | M. Binary value where 1 = yes and 0 = no
09a Wood Chips, Large 40 degree | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips, Large 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Large 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Large 40 degree | N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract..
09a Wood Chips, Large 40 degree | O. Binary value where 1 = yes and 0 = no
09a Wood Chips, Large 40 degree | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips, Large 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Large 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Large 50 degree | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
09a Wood Chips, Large 50 degree | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
09a Wood Chips, Large 50 degree | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
09a Wood Chips, Large 50 degree | D. Technical- and design life most often > 25 years
09a Wood Chips, Large 50 degree | E. For a medium size engine; small engines with less thermal mass might be faster
09a Wood Chips, Large 50 degree | F. When operating 4000 hours a year
09a Wood Chips, Large 50 degree | G. Only relevant for steam based CHP
09a Wood Chips, Large 50 degree | H. No data available
09a Wood Chips, Large 50 degree | I. DGC estimate for years 2030, 2050
09a Wood Chips, Large 50 degree | J. No known use, data from n-gas engines
09a Wood Chips, Large 50 degree | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
09a Wood Chips, Large 50 degree | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips, Large 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Large 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Large 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Large 50 degree | A. The boiler in the plant is a circulating fluid bed boiler (CFB) producing steam to be used in a subsequent back-pressure steam turbine without steam re-heat. The system is optimised at DH return temperature 50°C and flow 100°C.\n At DH return temperature 40 °C and flow 80 °C, for year 2015, t...
09a Wood Chips, Large 50 degree | B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
09a Wood Chips, Large 50 degree | C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
09a Wood Chips, Large 50 degree | D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
09a Wood Chips, Large 50 degree | E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator). Warm start-up time is particularly low for fluid bed types of plants.
09a Wood Chips, Large 50 degree | F. It is to be expected that the NOx level is low from the CFB, and that the necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 20 g/GJ, in which case SCR is used. From 2017 NOx (and other emissions) must fulfill the BAT_AEL values of the LCP BREF n...
09a Wood Chips, Large 50 degree | G. Warm start is starting with a glowing bed and a warm deaerator.
09a Wood Chips, Large 50 degree | H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power productio...
09a Wood Chips, Large 50 degree | I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
09a Wood Chips, Large 50 degree | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. \nFinancial data and Technological specific data...
09a Wood Chips, Large 50 degree | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. \nThe additional investment is listed in the bottom row.
09a Wood Chips, Large 50 degree | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity an...
09a Wood Chips, Large 50 degree | M. Binary value where 1 = yes and 0 = no
09a Wood Chips, Large 50 degree | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips, Large 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Large 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Large 50 degree | P. Reference to heat output because of the lack of electricity production.
09a Wood Chips, Large 50 degree | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips, Large 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Large 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Large 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Large 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Medium | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
09a Wood Chips, Medium | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
09a Wood Chips, Medium | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
09a Wood Chips, Medium | D. Technical- and design life most often > 25 years
09a Wood Chips, Medium | E. For a medium size engine; small engines with less thermal mass might be faster
09a Wood Chips, Medium | F. When operating 4000 hours a year
09a Wood Chips, Medium | G. Only relevant for steam based CHP
09a Wood Chips, Medium | H. No data available
09a Wood Chips, Medium | I. DGC estimate for years 2030, 2050
09a Wood Chips, Medium | J. No known use, data from n-gas engines
09a Wood Chips, Medium | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
09a Wood Chips, Medium | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Medium | A. The boiler in the plant is a grate fired boiler producing steam to be used in a subsequent back pressure steam turbine. Though a grate is reasonable flexible with respect to combusting different fuels the fuel feed system will be dependent on the type of fuel. It is to be expected that it is n...
09a Wood Chips, Medium | B. Through a turbine by-pass all the produced steam energy is used for District Heat production.
09a Wood Chips, Medium | C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
09a Wood Chips, Medium | D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
09a Wood Chips, Medium | E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
09a Wood Chips, Medium | F. It is to be expected that necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 40 g/GJ in which case SCR is used with slight adverse effect on electricity efficiency. From 2017 NOx (and other emissions) must fulfill the BAT_AEL values of the LCP ...
09a Wood Chips, Medium | G. Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
09a Wood Chips, Medium | H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power productio...
09a Wood Chips, Medium | I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
09a Wood Chips, Medium | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. \nFinancial data and Technological specific data...
09a Wood Chips, Medium | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. \nThe additional investment is listed in the bottom row.
09a Wood Chips, Medium | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity an...
09a Wood Chips, Medium | M. Binary value where 1 = yes and 0 = no
09a Wood Chips, Medium | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Medium | N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract..
09a Wood Chips, Medium | O. Binary value where 1 = yes and 0 = no
09a Wood Chips, Medium | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Small | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
09a Wood Chips, Small | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
09a Wood Chips, Small | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
09a Wood Chips, Small | D. Technical- and design life most often > 25 years
09a Wood Chips, Small | E. For a medium size engine; small engines with less thermal mass might be faster
09a Wood Chips, Small | F. When operating 4000 hours a year
09a Wood Chips, Small | G. Only relevant for steam based CHP
09a Wood Chips, Small | H. No data available
09a Wood Chips, Small | I. DGC estimate for years 2030, 2050
09a Wood Chips, Small | J. No known use, data from n-gas engines
09a Wood Chips, Small | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
09a Wood Chips, Small | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Small | A. The plant is directly producing hot water for District Heating by burning fuel on a grate. The electric power is produced by an ORC module (Organic Rankine Cycle; Waste Heat Recovery - WHR). Refer for instance to the following link for further information about technology and suppliers: http:/...
09a Wood Chips, Small | B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
09a Wood Chips, Small | C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
09a Wood Chips, Small | D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance. Though, the load control of the heat production is important and most units will perform better than the figure shown. Also, minimum load could be substantially lower.
09a Wood Chips, Small | E. Since electricity generation is only a secondary objective for minor heat producers, it may make more sense to relate the total investment only to the heat production capacity.
09a Wood Chips, Small | F. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emis...
09a Wood Chips, Small | G. Warm start is starting with a glowing fuel layer on the grate.
09a Wood Chips, Small | H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power productio...
09a Wood Chips, Small | I. Cv=1 describes turbine by-pass operation. During operation the turbine can be by-passed fully or partly for direct district heating production, at operator choice.
09a Wood Chips, Small | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. \nFinancial data and Technological specific data...
09a Wood Chips, Small | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. \nThe additional investment is listed in the bottom row.
09a Wood Chips, Small | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity an...
09a Wood Chips, Small | M. Binary value where 1 = yes and 0 = no
09a Wood Chips, Small | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Small | P. Reference to heat output because of the lack of electricity production.
09a Wood Chips, Small | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Large 40 degr | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
09b Wood Pellets, Large 40 degr | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
09b Wood Pellets, Large 40 degr | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
09b Wood Pellets, Large 40 degr | D. Technical- and design life most often > 25 years
09b Wood Pellets, Large 40 degr | E. For a medium size engine; small engines with less thermal mass might be faster
09b Wood Pellets, Large 40 degr | F. When operating 4000 hours a year
09b Wood Pellets, Large 40 degr | G. Only relevant for steam based CHP
09b Wood Pellets, Large 40 degr | H. No data available
09b Wood Pellets, Large 40 degr | I. DGC estimate for years 2030, 2050
09b Wood Pellets, Large 40 degr | J. No known use, data from n-gas engines
09b Wood Pellets, Large 40 degr | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
09b Wood Pellets, Large 40 degr | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09b Wood Pellets, Large 40 degr | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Large 40 degr | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Large 40 degr | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Large 40 degr | A. The boiler in the plant is a suspension fired boiler producing steam to be used in a subsequent steam turbine. Currently, the steam turbine is expected to be a back-pressure turbine with no re-heat. In some of the future scenarios it is assumed that the prices on electricity will allow for an ...
09b Wood Pellets, Large 40 degr | B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
09b Wood Pellets, Large 40 degr | C. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except ...
09b Wood Pellets, Large 40 degr | D. This is given by grid code (Energinet.dk)
09b Wood Pellets, Large 40 degr | E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
09b Wood Pellets, Large 40 degr | F. This plant is equiped with an SCR catalyst for DeNOx and an electrostatic precipitator for catching dust/fly ash
09b Wood Pellets, Large 40 degr | G. Warm start is starting with the steam system being pressurized.
09b Wood Pellets, Large 40 degr | H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power productio...
09b Wood Pellets, Large 40 degr | I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
09b Wood Pellets, Large 40 degr | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. \nFinancial data and Technological specific data...
09b Wood Pellets, Large 40 degr | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. \nThe additional investment is listed in the bottom row.
09b Wood Pellets, Large 40 degr | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity an...
09b Wood Pellets, Large 40 degr | M. Binary value where 1 = yes and 0 = no
09b Wood Pellets, Large 40 degr | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09b Wood Pellets, Large 40 degr | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Large 40 degr | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Large 40 degr | N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract..
09b Wood Pellets, Large 40 degr | O. Binary value where 1 = yes and 0 = no
09b Wood Pellets, Large 40 degr | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09b Wood Pellets, Large 40 degr | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Large 40 degr | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Large 50 degr | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
09b Wood Pellets, Large 50 degr | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
09b Wood Pellets, Large 50 degr | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
09b Wood Pellets, Large 50 degr | D. Technical- and design life most often > 25 years
09b Wood Pellets, Large 50 degr | E. For a medium size engine; small engines with less thermal mass might be faster
09b Wood Pellets, Large 50 degr | F. When operating 4000 hours a year
09b Wood Pellets, Large 50 degr | G. Only relevant for steam based CHP
09b Wood Pellets, Large 50 degr | H. No data available
09b Wood Pellets, Large 50 degr | I. DGC estimate for years 2030, 2050
09b Wood Pellets, Large 50 degr | J. No known use, data from n-gas engines
09b Wood Pellets, Large 50 degr | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
09b Wood Pellets, Large 50 degr | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09b Wood Pellets, Large 50 degr | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Large 50 degr | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Large 50 degr | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Large 50 degr | A. The boiler in the plant is a suspension fired boiler producing steam to be used in a subsequent steam turbine. Currently, the steam turbine is expected to be a back-pressure turbine with no re-heat. In some of the future scenarios it is assumed that the prices on electricity will allow for an ...
09b Wood Pellets, Large 50 degr | B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
09b Wood Pellets, Large 50 degr | C. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except ...
09b Wood Pellets, Large 50 degr | D. This is given by grid code (Energinet.dk)
09b Wood Pellets, Large 50 degr | E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
09b Wood Pellets, Large 50 degr | F. This plant is equiped with an SCR catalyst for DeNOx and an electrostatic precipitator for catching dust/fly ash
09b Wood Pellets, Large 50 degr | G. Warm start is starting with the steam system being pressurized.
09b Wood Pellets, Large 50 degr | H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power productio...
09b Wood Pellets, Large 50 degr | I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
09b Wood Pellets, Large 50 degr | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. \nFinancial data and Technological specific data...
09b Wood Pellets, Large 50 degr | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. \nThe additional investment is listed in the bottom row.
09b Wood Pellets, Large 50 degr | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity an...
09b Wood Pellets, Large 50 degr | M. Binary value where 1 = yes and 0 = no
09b Wood Pellets, Large 50 degr | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09b Wood Pellets, Large 50 degr | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Large 50 degr | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Large 50 degr | P. Reference to heat output because of the lack of electricity production.
09b Wood Pellets, Large 50 degr | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09b Wood Pellets, Large 50 degr | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Large 50 degr | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Large 50 degr | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Large 50 degr | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Medium | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
09b Wood Pellets, Medium | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
09b Wood Pellets, Medium | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
09b Wood Pellets, Medium | D. Technical- and design life most often > 25 years
09b Wood Pellets, Medium | E. For a medium size engine; small engines with less thermal mass might be faster
09b Wood Pellets, Medium | F. When operating 4000 hours a year
09b Wood Pellets, Medium | G. Only relevant for steam based CHP
09b Wood Pellets, Medium | H. No data available
09b Wood Pellets, Medium | I. DGC estimate for years 2030, 2050
09b Wood Pellets, Medium | J. No known use, data from n-gas engines
09b Wood Pellets, Medium | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
09b Wood Pellets, Medium | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09b Wood Pellets, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Medium | A. The boiler in the plant is a suspension fired boiler producing steam to be used in a subsequent back pressure steam turbine. It is possible to pulverize wood pellets and use it for suspension firing but it has not been possible to find an appropriate reference.\n The system is optimised at DH ...
09b Wood Pellets, Medium | B. Through a turbine by-pass all the produced steam energy is used for District Heat production.
09b Wood Pellets, Medium | C. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except ...
09b Wood Pellets, Medium | D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
09b Wood Pellets, Medium | E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
09b Wood Pellets, Medium | F. SNCR is assumed at NOx emissions at no less than 40 g/GJ. At lower NOx-levels it is chosen to include a tail-end SCR catalyst with slight adverse effect on electricity efficiency.
09b Wood Pellets, Medium | G. Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
09b Wood Pellets, Medium | H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power productio...
09b Wood Pellets, Medium | I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
09b Wood Pellets, Medium | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. \nFinancial data and Technological specific data...
09b Wood Pellets, Medium | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. \nThe additional investment is listed in the bottom row.
09b Wood Pellets, Medium | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity an...
09b Wood Pellets, Medium | M. Binary value where 1 = yes and 0 = no
09b Wood Pellets, Medium | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09b Wood Pellets, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Medium | N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract..
09b Wood Pellets, Medium | O. Binary value where 1 = yes and 0 = no
09b Wood Pellets, Medium | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09b Wood Pellets, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Small | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
09b Wood Pellets, Small | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
09b Wood Pellets, Small | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
09b Wood Pellets, Small | D. Technical- and design life most often > 25 years
09b Wood Pellets, Small | E. For a medium size engine; small engines with less thermal mass might be faster
09b Wood Pellets, Small | F. When operating 4000 hours a year
09b Wood Pellets, Small | G. Only relevant for steam based CHP
09b Wood Pellets, Small | H. No data available
09b Wood Pellets, Small | I. DGC estimate for years 2030, 2050
09b Wood Pellets, Small | J. No known use, data from n-gas engines
09b Wood Pellets, Small | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
09b Wood Pellets, Small | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09b Wood Pellets, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Small | A. The plant is directly producing hot water for District Heating by burning fuel on a grate. The electric power is produced by an ORC module (Organic Rankine Cycle; Waste Heat Recovery - WHR). Refer for instance to the following link for further information about technology and suppliers: http:/...
09b Wood Pellets, Small | B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
09b Wood Pellets, Small | C. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except ...
09b Wood Pellets, Small | D. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except ...
09b Wood Pellets, Small | E. Since electricity generation is only a secondary objective for minor heat producers, it may make more sense to relate the total investment only to the thermail input.
09b Wood Pellets, Small | F. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emis...
09b Wood Pellets, Small | G. Warm start is starting with a glowing fuel layer on the grate.
09b Wood Pellets, Small | H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power productio...
09b Wood Pellets, Small | I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
09b Wood Pellets, Small | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. \nFinancial data and Technological specific data...
09b Wood Pellets, Small | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. \nThe additional investment is listed in the bottom row.
09b Wood Pellets, Small | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity an...
09b Wood Pellets, Small | M. Binary value where 1 = yes and 0 = no
09b Wood Pellets, Small | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09b Wood Pellets, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Small | P. Reference to heat output because of the lack of electricity production.
09b Wood Pellets, Small | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09b Wood Pellets, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Large, 40 degree | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
09c Straw, Large, 40 degree | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
09c Straw, Large, 40 degree | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
09c Straw, Large, 40 degree | D. Technical- and design life most often > 25 years
09c Straw, Large, 40 degree | E. For a medium size engine; small engines with less thermal mass might be faster
09c Straw, Large, 40 degree | F. When operating 4000 hours a year
09c Straw, Large, 40 degree | G. Only relevant for steam based CHP
09c Straw, Large, 40 degree | H. No data available
09c Straw, Large, 40 degree | I. DGC estimate for years 2030, 2050
09c Straw, Large, 40 degree | J. No known use, data from n-gas engines
09c Straw, Large, 40 degree | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
09c Straw, Large, 40 degree | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09c Straw, Large, 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Large, 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Large, 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Large, 40 degree | A. The boiler in the plant is grate fired producing steam to be used in a subsequent back pressure steam turbine. Though a grate is reasonable flexible with respect to combusting different fuels the fuel feed system will be dependent on the type of fuel used. \n The system is optimised at DH retu...
09c Straw, Large, 40 degree | B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
09c Straw, Large, 40 degree | C. Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower...
09c Straw, Large, 40 degree | D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
09c Straw, Large, 40 degree | E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
09c Straw, Large, 40 degree | F. For NOx-emissions no lower than 40 g/GJ SNCR is assumed. It is probably necessary to include a tail-end SCR catalyst to fulfill expected BREF requirements, particularly after year 2030. \nThis has slight adverse effect on the electricity efficiency.
09c Straw, Large, 40 degree | G. Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
09c Straw, Large, 40 degree | H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power productio...
09c Straw, Large, 40 degree | I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
09c Straw, Large, 40 degree | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. \nFinancial data and Technological specific data...
09c Straw, Large, 40 degree | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. \nThe additional investment is listed in the bottom row.
09c Straw, Large, 40 degree | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity an...
09c Straw, Large, 40 degree | M. Binary value where 1 = yes and 0 = no
09c Straw, Large, 40 degree | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09c Straw, Large, 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Large, 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Large, 40 degree | N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract..
09c Straw, Large, 40 degree | O. Binary value where 1 = yes and 0 = no
09c Straw, Large, 40 degree | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09c Straw, Large, 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Large, 40 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Large, 50 degree | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
09c Straw, Large, 50 degree | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
09c Straw, Large, 50 degree | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
09c Straw, Large, 50 degree | D. Technical- and design life most often > 25 years
09c Straw, Large, 50 degree | E. For a medium size engine; small engines with less thermal mass might be faster
09c Straw, Large, 50 degree | F. When operating 4000 hours a year
09c Straw, Large, 50 degree | G. Only relevant for steam based CHP
09c Straw, Large, 50 degree | H. No data available
09c Straw, Large, 50 degree | I. DGC estimate for years 2030, 2050
09c Straw, Large, 50 degree | J. No known use, data from n-gas engines
09c Straw, Large, 50 degree | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
09c Straw, Large, 50 degree | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09c Straw, Large, 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Large, 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Large, 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Large, 50 degree | A. The boiler in the plant is grate fired producing steam to be used in a subsequent back pressure steam turbine. Though a grate is reasonable flexible with respect to combusting different fuels the fuel feed system will be dependent on the type of fuel used. \n The system is optimised at DH retu...
09c Straw, Large, 50 degree | B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
09c Straw, Large, 50 degree | C. Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower...
09c Straw, Large, 50 degree | D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
09c Straw, Large, 50 degree | E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
09c Straw, Large, 50 degree | F. For NOx-emissions no lower than 40 g/GJ SNCR is assumed. It is probably necessary to include a tail-end SCR catalyst to fulfill expected BREF requirements, particularly after year 2030. \nThis has slight adverse effect on the electricity efficiency.
09c Straw, Large, 50 degree | G. Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
09c Straw, Large, 50 degree | H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power productio...
09c Straw, Large, 50 degree | I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
09c Straw, Large, 50 degree | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. \nFinancial data and Technological specific data...
09c Straw, Large, 50 degree | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. \nThe additional investment is listed in the bottom row.
09c Straw, Large, 50 degree | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity an...
09c Straw, Large, 50 degree | M. Binary value where 1 = yes and 0 = no
09c Straw, Large, 50 degree | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09c Straw, Large, 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Large, 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Large, 50 degree | P. Reference to heat output because of the lack of electricity production.
09c Straw, Large, 50 degree | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09c Straw, Large, 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Large, 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Large, 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Large, 50 degree | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Medium | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
09c Straw, Medium | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
09c Straw, Medium | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
09c Straw, Medium | D. Technical- and design life most often > 25 years
09c Straw, Medium | E. For a medium size engine; small engines with less thermal mass might be faster
09c Straw, Medium | F. When operating 4000 hours a year
09c Straw, Medium | G. Only relevant for steam based CHP
09c Straw, Medium | H. No data available
09c Straw, Medium | I. DGC estimate for years 2030, 2050
09c Straw, Medium | J. No known use, data from n-gas engines
09c Straw, Medium | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
09c Straw, Medium | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09c Straw, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Medium | A. The boiler in the plant is grate fired producing steam to be used in a subsequent back pressure steam turbine. Though a grate is reasonable flexible with respect to combusting different fuels the fuel feed system will be dependent on the type of fuel used. \n The system is optimised at DH retu...
09c Straw, Medium | B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
09c Straw, Medium | C. Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower...
09c Straw, Medium | D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
09c Straw, Medium | E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
09c Straw, Medium | F. For NOx-emissions no lower than 40 g/GJ SNCR is assumed. It is probably necessary to include a tail-end SCR catalyst to fulfill expected BREF requirements, particularly after year 2030. This has slight adverse effect on the electricity efficiency.
09c Straw, Medium | G. Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
09c Straw, Medium | H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power productio...
09c Straw, Medium | I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
09c Straw, Medium | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. \nFinancial data and Technological specific data...
09c Straw, Medium | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. \nThe additional investment is listed in the bottom row.
09c Straw, Medium | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity an...
09c Straw, Medium | M. Binary value where 1 = yes and 0 = no
09c Straw, Medium | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09c Straw, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Medium | N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract..
09c Straw, Medium | O. Binary value where 1 = yes and 0 = no
09c Straw, Medium | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09c Straw, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Small | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
09c Straw, Small | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
09c Straw, Small | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
09c Straw, Small | D. Technical- and design life most often > 25 years
09c Straw, Small | E. For a medium size engine; small engines with less thermal mass might be faster
09c Straw, Small | F. When operating 4000 hours a year
09c Straw, Small | G. Only relevant for steam based CHP
09c Straw, Small | H. No data available
09c Straw, Small | I. DGC estimate for years 2030, 2050
09c Straw, Small | J. No known use, data from n-gas engines
09c Straw, Small | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
09c Straw, Small | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09c Straw, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Small | A. The plant is directly producing hot water for District Heating by burning fuel on a grate. The electric power is produced by an ORC module (Organic Rankine Cycle; Waste Heat Recovery - WHR). Refer for instance to the following link for further information about technology and suppliers: http:/...
09c Straw, Small | B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
09c Straw, Small | C. Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower...
09c Straw, Small | D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance. Though, the load control of the heat production is important and most units will perform better than the figure shown. Also, minimum load could be substantially lower.
09c Straw, Small | E. Since electricity generation is only a secondary objective for minor heat producers, it may make more sense to relate the total investment only to the heat production capacity.
09c Straw, Small | F. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emis...
09c Straw, Small | G. Warm start is starting with a glowing fuel layer on the grate.
09c Straw, Small | H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power productio...
09c Straw, Small | I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
09c Straw, Small | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. \nFinancial data and Technological specific data...
09c Straw, Small | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. \nThe additional investment is listed in the bottom row.
09c Straw, Small | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity an...
09c Straw, Small | M. Binary value where 1 = yes and 0 = no
09c Straw, Small | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09c Straw, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Small | P. Reference to heat output because of the lack of electricity production.
09c Straw, Small | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09c Straw, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw, Small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, small | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
09a Wood Chips HOP, small | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
09a Wood Chips HOP, small | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
09a Wood Chips HOP, small | D. Technical- and design life most often > 25 years
09a Wood Chips HOP, small | E. For a medium size engine; small engines with less thermal mass might be faster
09a Wood Chips HOP, small | F. When operating 4000 hours a year
09a Wood Chips HOP, small | G. Only relevant for steam based CHP
09a Wood Chips HOP, small | H. No data available
09a Wood Chips HOP, small | I. DGC estimate for years 2030, 2050
09a Wood Chips HOP, small | J. No known use, data from n-gas engines
09a Wood Chips HOP, small | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
09a Wood Chips HOP, small | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips HOP, small | A. The plant is directly producing hot water for District Heating by burning fuel on a grate.\n The system is optimised at DH return temperature 40°C and flow 80°C.
09a Wood Chips HOP, small | B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
09a Wood Chips HOP, small | C. Efficiencies refer to lower heating value. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the n...
09a Wood Chips HOP, small | D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
09a Wood Chips HOP, small | E. Load control of the heat production is important and units of this size can make rapid load variations. Similarly, the minimum load is quite low
09a Wood Chips HOP, small | F. Reference to heat output because of the lack of electricity production
09a Wood Chips HOP, small | G. Assuming content of sulphur in fuel of 20 g/GJ
09a Wood Chips HOP, small | H. Warm start is starting with a glowing fuel layer on the grate.
09a Wood Chips HOP, small | I. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emis...
09a Wood Chips HOP, small | J. The nominal investment is in the range 0.6 to 1.1 MEUR/MWth
09a Wood Chips HOP, small | K. Result of model calculation, there are reports of DH plants operating at lower power consumption, down to 1% of heat generation.
09a Wood Chips HOP, small | L. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. \nThe additional investment is listed in the bottom row.
09a Wood Chips HOP, small | M. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate ...
09a Wood Chips HOP, small | N. Binary value where 1 = yes and 0 = no
09a Wood Chips HOP, small | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips HOP, small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, small | N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract..
09a Wood Chips HOP, small | O. Binary value where 1 = yes and 0 = no
09a Wood Chips HOP, small | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips HOP, small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, medium | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
09a Wood Chips HOP, medium | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
09a Wood Chips HOP, medium | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
09a Wood Chips HOP, medium | D. Technical- and design life most often > 25 years
09a Wood Chips HOP, medium | E. For a medium size engine; small engines with less thermal mass might be faster
09a Wood Chips HOP, medium | F. When operating 4000 hours a year
09a Wood Chips HOP, medium | G. Only relevant for steam based CHP
09a Wood Chips HOP, medium | H. No data available
09a Wood Chips HOP, medium | I. DGC estimate for years 2030, 2050
09a Wood Chips HOP, medium | J. No known use, data from n-gas engines
09a Wood Chips HOP, medium | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
09a Wood Chips HOP, medium | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips HOP, medium | A. The plant is directly producing hot water for District Heating by burning fuel on a grate as the basis assumption. Fluid-bed combustion technology may be an alternative.It can be assumed that the data for this does not differ significantly from grate fired boilers. Data in this sheet is applic...
09a Wood Chips HOP, medium | B. Boilers larger than approx. 20 MW fuel input for hot water production are designed-for-purpose products with a high degree of fuel flexibility (type of biomass, humidity etc.)
09a Wood Chips HOP, medium | C. Efficiencies refer to lower heating value. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the n...
09a Wood Chips HOP, medium | D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
09a Wood Chips HOP, medium | E. Load control of the heat production is important and units of this size can make rapid load variations.
09a Wood Chips HOP, medium | F. Reference to heat output because of the lack of electricity production
09a Wood Chips HOP, medium | G. assuming content of sulphur in fuel of 20 g/GJ
09a Wood Chips HOP, medium | H. Warm start is starting with a glowing fuel layer on the grate.
09a Wood Chips HOP, medium | I. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emis...
09a Wood Chips HOP, medium | K. Result of model calculation, there are reports of DH plants operating at lower power consumption, down to 1% of heat generation.
09a Wood Chips HOP, medium | L. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. \nThe additional investment is listed in the bottom row.
09a Wood Chips HOP, medium | M. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate ...
09a Wood Chips HOP, medium | N. Binary value where 1 = yes and 0 = no
09a Wood Chips HOP, medium | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips HOP, medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, medium | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips HOP, medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, medium | P. Reference to heat output because of the lack of electricity production.
09a Wood Chips HOP, medium | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips HOP, medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, medium | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, large | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
09a Wood Chips HOP, large | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
09a Wood Chips HOP, large | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
09a Wood Chips HOP, large | D. Technical- and design life most often > 25 years
09a Wood Chips HOP, large | E. For a medium size engine; small engines with less thermal mass might be faster
09a Wood Chips HOP, large | F. When operating 4000 hours a year
09a Wood Chips HOP, large | G. Only relevant for steam based CHP
09a Wood Chips HOP, large | H. No data available
09a Wood Chips HOP, large | I. DGC estimate for years 2030, 2050
09a Wood Chips HOP, large | J. No known use, data from n-gas engines
09a Wood Chips HOP, large | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
09a Wood Chips HOP, large | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips HOP, large | A. The plant is directly producing hot water for District Heating by burning fuel on a grate. Fluid-bed combustion technology may be an alternative. It can be assumed that the data for this does not differ significantly from grate fired boilers. Data in this sheet is applicable for plants in the ...
09a Wood Chips HOP, large | B. Boilers larger than approx. 20 MW fuel input for hot water production are designed-for-purpose products with a high degree of fuel flexibility (type of biomass, humidity etc.)
09a Wood Chips HOP, large | C. Efficiencies refer to lower heating value. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the n...
09a Wood Chips HOP, large | D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
09a Wood Chips HOP, large | E. Load control of the heat production is important and units of this size can make rapid load variations.
09a Wood Chips HOP, large | F. Reference to heat output because of the lack of electricity production
09a Wood Chips HOP, large | G. Assuming content of sulphur in fuel of 20 g/GJ
09a Wood Chips HOP, large | H. Warm start is starting with a glowing fuel layer on the grate.
09a Wood Chips HOP, large | K. Result of model calculation, there are reports of DH plants operating at lower power consumption, down to 1% of heat generation.
09a Wood Chips HOP, large | L. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. \nThe additional investment is listed in the bottom row.
09a Wood Chips HOP, large | M. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate ...
09a Wood Chips HOP, large | N. Binary value where 1 = yes and 0 = no
09a Wood Chips HOP, large | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips HOP, large | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, large | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, large | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, large | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, large | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, large | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, large | N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract..
09a Wood Chips HOP, large | O. Binary value where 1 = yes and 0 = no
09a Wood Chips HOP, large | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips HOP, large | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips HOP, large | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets HOP | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
09b Wood Pellets HOP | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
09b Wood Pellets HOP | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
09b Wood Pellets HOP | D. Technical- and design life most often > 25 years
09b Wood Pellets HOP | E. For a medium size engine; small engines with less thermal mass might be faster
09b Wood Pellets HOP | F. When operating 4000 hours a year
09b Wood Pellets HOP | G. Only relevant for steam based CHP
09b Wood Pellets HOP | H. No data available
09b Wood Pellets HOP | I. DGC estimate for years 2030, 2050
09b Wood Pellets HOP | J. No known use, data from n-gas engines
09b Wood Pellets HOP | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
09b Wood Pellets HOP | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09b Wood Pellets HOP | A. The plant is directly producing hot water for District Heating by burning fuel on a grate.\n The system is optimised at DH return temperature 40°C and flow 80°C.
09b Wood Pellets HOP | B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
09b Wood Pellets HOP | C. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency.
09b Wood Pellets HOP | D. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except ...
09b Wood Pellets HOP | E. Load control of the heat production is important and units of this size can make rapid load variations. Similarly, the minimum load is quite low
09b Wood Pellets HOP | F. Reference to heat output because of the lack of electricity production
09b Wood Pellets HOP | G. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emis...
09b Wood Pellets HOP | I. Warm start is starting with a glowing fuel layer on the grate.
09b Wood Pellets HOP | J. The nominal investment is in the range 0.6 to 1.1 MEUR/Mwth
09b Wood Pellets HOP | K. Result of model calculation, there are reports of DH plants operating at lower power consumption
09b Wood Pellets HOP | L. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. \nThe additional investment is listed in the bottom row.
09b Wood Pellets HOP | M. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate ...
09b Wood Pellets HOP | N. Binary value where 1 = yes and 0 = no
09b Wood Pellets HOP | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09b Wood Pellets HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets HOP | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09b Wood Pellets HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets HOP | P. Reference to heat output because of the lack of electricity production.
09b Wood Pellets HOP | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09b Wood Pellets HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw HOP | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
09c Straw HOP | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
09c Straw HOP | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
09c Straw HOP | D. Technical- and design life most often > 25 years
09c Straw HOP | E. For a medium size engine; small engines with less thermal mass might be faster
09c Straw HOP | F. When operating 4000 hours a year
09c Straw HOP | G. Only relevant for steam based CHP
09c Straw HOP | H. No data available
09c Straw HOP | I. DGC estimate for years 2030, 2050
09c Straw HOP | J. No known use, data from n-gas engines
09c Straw HOP | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
09c Straw HOP | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09c Straw HOP | A. The plant is directly producing hot water for District Heating by burning fuel on a grate.
09c Straw HOP | B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
09c Straw HOP | C. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency.
09c Straw HOP | D. Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower...
09c Straw HOP | E. Load control of the heat production is important and units of this size can make rapid load variations. Similarly, the minimum load is quite low
09c Straw HOP | F. Reference to heat output because of the lack of electricity production
09c Straw HOP | G. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emis...
09c Straw HOP | I. The nominal investment is in the range 0.6 to 1.1 MEUR/MWth
09c Straw HOP | J. Result of model calculation, there are reports of DH plants operating at lower power consumption
09c Straw HOP | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. \nThe additional investment is listed in the bottom row.
09c Straw HOP | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate ...
09c Straw HOP | M. Binary value where 1 = yes and 0 = no
09c Straw HOP | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09c Straw HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw HOP | N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract..
09c Straw HOP | O. Binary value where 1 = yes and 0 = no
09c Straw HOP | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09c Straw HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09c Straw HOP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips extract. plant | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
09a Wood Chips extract. plant | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
09a Wood Chips extract. plant | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
09a Wood Chips extract. plant | D. Technical- and design life most often > 25 years
09a Wood Chips extract. plant | E. For a medium size engine; small engines with less thermal mass might be faster
09a Wood Chips extract. plant | F. When operating 4000 hours a year
09a Wood Chips extract. plant | G. Only relevant for steam based CHP
09a Wood Chips extract. plant | H. No data available
09a Wood Chips extract. plant | I. DGC estimate for years 2030, 2050
09a Wood Chips extract. plant | J. No known use, data from n-gas engines
09a Wood Chips extract. plant | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
09a Wood Chips extract. plant | A. The boiler in the plant is a circulating fluid bed boiler (CFB) producing steam to be used in a subsequent \n extraction steam turbine with steam re-heat.
09a Wood Chips extract. plant | C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). This comes in addition to direct condensation that may yield 22% (of thermal input) when operated with combustion air humi...
09a Wood Chips extract. plant | D. Secondary regulation normally relates to power production.
09a Wood Chips extract. plant | E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator). Warm start-up time is \n particularly low for fluid bed types of plants.
09a Wood Chips extract. plant | F. It is to be expected that the NOx level is low from the CFB, and that the necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 20 g/GJ, in which case SCR is used. From 2017 NOx (and other emissions) must fulfil the BAT_AEL values of the LCP BREF note.
09a Wood Chips extract. plant | G. Warm start is starting with a glowing bed and a warm deaerator.
09a Wood Chips extract. plant | H. The electricity efficiency is applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to the effects of load variations, turbine outages and other incidents. Efficiencies refer to thermal input by lower heatin...
09a Wood Chips extract. plant | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. \n Financial data and Technological specific dat...
09a Wood Chips extract. plant | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply \n opportunities and energy supply obligations, amongst other things.\n The additional investment is listed in the bottom row.
09a Wood Chips extract. plant | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate, if applicable, is not included. Electricity consumption is not included as a cost for CHP, and revenues from sale of electricity and heat are ...
09a Wood Chips extract. plant | M. Binary value where 1 = yes and 0 = no
09a Wood Chips extract. plant | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips extract. plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips extract. plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips extract. plant | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips extract. plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips extract. plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips extract. plant | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips extract. plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips extract. plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips extract. plant | P. Reference to heat output because of the lack of electricity production.
09a Wood Chips extract. plant | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09a Wood Chips extract. plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips extract. plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips extract. plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09a Wood Chips extract. plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets extract. plant | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
09b Wood Pellets extract. plant | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
09b Wood Pellets extract. plant | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
09b Wood Pellets extract. plant | D. Technical- and design life most often > 25 years
09b Wood Pellets extract. plant | E. For a medium size engine; small engines with less thermal mass might be faster
09b Wood Pellets extract. plant | F. When operating 4000 hours a year
09b Wood Pellets extract. plant | G. Only relevant for steam based CHP
09b Wood Pellets extract. plant | H. No data available
09b Wood Pellets extract. plant | I. DGC estimate for years 2030, 2050
09b Wood Pellets extract. plant | J. No known use, data from n-gas engines
09b Wood Pellets extract. plant | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
09b Wood Pellets extract. plant | A. The boiler in the plant is a suspension fired boiler producing steam to be used in a subsequent extraction steam turbine \n with steam reheat.
09b Wood Pellets extract. plant | C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). This comes in addition to direct condensation that may yield additional 6% (of thermal input) when operated with combustio...
09b Wood Pellets extract. plant | D. This is given by grid code (Energinet.dk)
09b Wood Pellets extract. plant | E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
09b Wood Pellets extract. plant | F. This plant is equipped with a Tail-end SCR catalyst for DeNOx and an electrostatic precipitator for catching dust/fly ash
09b Wood Pellets extract. plant | G. Warm start is starting with the steam system being pressurized.
09b Wood Pellets extract. plant | H. The electricity efficiency is applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to due to the effects of load variations, turbine outages and other incidents. Efficiencies refer to thermal input by lower...
09b Wood Pellets extract. plant | I. The Cv value may vary according to the optimisation of the plant. A modest value representing a choice with current \n power/heat prices is shown.
09b Wood Pellets extract. plant | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total \n investment, e.g. additional fuel storage, conditions for foundation and harbour facilities.\n Financial data and Technological specific data are essentially the total cos...
09b Wood Pellets extract. plant | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities energy supply obligations, amongst other things. The additional investment is listed in the bottom row.
09b Wood Pellets extract. plant | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate, if applicable, is not included. Electricity consumption is not included as a cost for CHP, and revenues from sale of electricity and heat are ...
09b Wood Pellets extract. plant | M. Binary value where 1 = yes and 0 = no
09b Wood Pellets extract. plant | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09b Wood Pellets extract. plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets extract. plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets extract. plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets extract. plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets extract. plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets extract. plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets extract. plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets extract. plant | N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract..
09b Wood Pellets extract. plant | O. Binary value where 1 = yes and 0 = no
09b Wood Pellets extract. plant | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
09b Wood Pellets extract. plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
09b Wood Pellets extract. plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
10 Stirling | A. The efficiency of the gasifier is 97%, while the total efficiency for the whole system is 90% (2020).
10 Stirling | B. The plants may be delivered as pre-assembled container solutions reducing construction times on site to a couple of weeks.
10 Stirling | C. Complete plant, including gasifier, combustion chambers, engines, control system, piping, and instrumentation.
10 Stirling | D. O&M for the Stirling engine itself is (2010) around 16 EUR/MWh, while the remianing O&M costs are for biomass feeding, gasification, heat exchangers etc.
10 Stirling | E. Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
10 Stirling | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
10 Stirling | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
10 Stirling | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
10 Stirling | A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
10 Stirling | B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
10 Stirling | C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
10 Stirling | D. Technical- and design life most often > 25 years
10 Stirling | E. For a medium size engine; small engines with less thermal mass might be faster
10 Stirling | F. When operating 4000 hours a year
10 Stirling | G. Only relevant for steam based CHP
10 Stirling | H. No data available
10 Stirling | I. DGC estimate for years 2030, 2050
10 Stirling | J. No known use, data from n-gas engines
10 Stirling | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
10 Stirling | A. The boiler in the plant is a circulating fluid bed boiler (CFB) producing steam to be used in a subsequent \n extraction steam turbine with steam re-heat.
10 Stirling | C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). This comes in addition to direct condensation that may yield 22% (of thermal input) when operated with combustion air humi...
10 Stirling | D. Secondary regulation normally relates to power production.
10 Stirling | E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator). Warm start-up time is \n particularly low for fluid bed types of plants.
10 Stirling | F. It is to be expected that the NOx level is low from the CFB, and that the necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 20 g/GJ, in which case SCR is used. From 2017 NOx (and other emissions) must fulfil the BAT_AEL values of the LCP BREF note.
10 Stirling | G. Warm start is starting with a glowing bed and a warm deaerator.
10 Stirling | H. The electricity efficiency is applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to the effects of load variations, turbine outages and other incidents. Efficiencies refer to thermal input by lower heatin...
10 Stirling | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. \n Financial data and Technological specific dat...
10 Stirling | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply \n opportunities and energy supply obligations, amongst other things.\n The additional investment is listed in the bottom row.
10 Stirling | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate, if applicable, is not included. Electricity consumption is not included as a cost for CHP, and revenues from sale of electricity and heat are ...
10 Stirling | M. Binary value where 1 = yes and 0 = no
10 Stirling | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
10 Stirling | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
10 Stirling | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
10 Stirling | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
10 Stirling | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
10 Stirling | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
10 Stirling | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
10 Stirling | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
10 Stirling | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
10 Stirling | P. Reference to heat output because of the lack of electricity production.
10 Stirling | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
10 Stirling | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
10 Stirling | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
10 Stirling | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
10 Stirling | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
11 SOFC-CHP | A. Installed systems consist of modules of app. 200 kWel power, these modules can be clustered into larger units. Today, often up to app. 2 MWel power and upwards. [5,8]
11 SOFC-CHP | B. The electrical efficiency (based on the lower heating value, LHV) of Bloom Energy's systems decreases from an initial value of 60 % to 52 % by the end-of life for the stacks. This gives an average electrical efficiency of 56 % for the life-time of a stack. Uncertainties represent the aforement...
11 SOFC-CHP | C. No CHP-systems in this power range are available, therefore, Bloom Energy ES-5710 unit has been chosen as the reference system. This system is a power producing system and does not take the produced heat into account. . The produced heat can be used as thermal storage, hot water production, he...
11 SOFC-CHP | D. Values correspond to the durability for the whole plant; the stack may be exchanged several times during the life time of the plant.
11 SOFC-CHP | E. Start up from outdoor temperature or room temperature takes rather long time, this is mainly due to the large amount of ceramic material which require slow heating ramps. If the system is at operating temperature the stack can be started up quickly, assuming that gases are supplied and help sy...
11 SOFC-CHP | F. Value for SOFC microCHP systems used here, since SOFC-CHP's has the same operating principle.
11 SOFC-CHP | G. A bloom unit costs approximately 6600 euro per kWel. To this must the installation costs be added, which of course depends on the location and the size of the unit. Additional costs are also to cover for necessary modifications of the system, e.g. implementation of hot water storage and subsys...
11 SOFC-CHP | H. Start up from outdoor temperature or room temperature takes rather long time, this is mainly due to the large amount of ceramic material which require slow heating ramps. If the system is at operating temperature the stack can be started up quickly, assuming that gases are supplied and help sy...
11 SOFC-CHP | I. The best estimates for nominal investments in 2020, 2030 and 2050 are estimated from [9]. In 2020 an annual production of 50 units is assumed, in 2030 a yearly production of 250 units is assumed, and in 2050 a production of 4000 units per year is assumed.
11 SOFC-CHP | J. Estimation of uncertainties for investment costs are estimated from [9] with an annual production of 10/150 units in 2020 and 1000/10000 units in 2050
11 SOFC-CHP | K. Fixed O&M costs are estimated as 5% of the investment cost.
11 SOFC-CHP | L. The heat efficiency, which can be derived, depends on the return temperature of the cooling circuit and the size of the heat exchanger.
11 SOFC-CHP | M. An asterisk (*) in the reference indicate high uncertainty or "guesstimate", where more certain data where not available
11 SOFC-CHP | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
11 SOFC-CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
11 SOFC-CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
11 SOFC-CHP | F. This plant is equipped with a Tail-end SCR catalyst for DeNOx and an electrostatic precipitator for catching dust/fly ash
11 SOFC-CHP | G. Warm start is starting with the steam system being pressurized.
11 SOFC-CHP | H. The electricity efficiency is applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to due to the effects of load variations, turbine outages and other incidents. Efficiencies refer to thermal input by lower...
11 SOFC-CHP | I. The Cv value may vary according to the optimisation of the plant. A modest value representing a choice with current \n power/heat prices is shown.
11 SOFC-CHP | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total \n investment, e.g. additional fuel storage, conditions for foundation and harbour facilities.\n Financial data and Technological specific data are essentially the total cos...
11 SOFC-CHP | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities energy supply obligations, amongst other things. The additional investment is listed in the bottom row.
11 SOFC-CHP | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate, if applicable, is not included. Electricity consumption is not included as a cost for CHP, and revenues from sale of electricity and heat are ...
11 SOFC-CHP | M. Binary value where 1 = yes and 0 = no
11 SOFC-CHP | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
11 SOFC-CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
11 SOFC-CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
11 SOFC-CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
11 SOFC-CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
11 SOFC-CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
11 SOFC-CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
11 SOFC-CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
11 SOFC-CHP | N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract..
11 SOFC-CHP | O. Binary value where 1 = yes and 0 = no
11 SOFC-CHP | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
11 SOFC-CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
11 SOFC-CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
12 LT-PEMFC CHP | A. The efficiency of the gasifier is 97%, while the total efficiency for the whole system is 90% (2020).
12 LT-PEMFC CHP | B. The plants may be delivered as pre-assembled container solutions reducing construction times on site to a couple of weeks.
12 LT-PEMFC CHP | C. Complete plant, including gasifier, combustion chambers, engines, control system, piping, and instrumentation.
12 LT-PEMFC CHP | D. O&M for the Stirling engine itself is (2010) around 16 EUR/MWh, while the remianing O&M costs are for biomass feeding, gasification, heat exchangers etc.
12 LT-PEMFC CHP | E. Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
12 LT-PEMFC CHP | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
12 LT-PEMFC CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
12 LT-PEMFC CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
12 LT-PEMFC CHP | A. Uncertainties for efficiency based on [2]
12 LT-PEMFC CHP | B. Estimation of uncertainties for nominal investment costs based on [2]
12 LT-PEMFC CHP | C. Fixed O&M costs are estimated to 5% of the investment cost based on [2]
12 LT-PEMFC CHP | D. The heat efficiency, which can be derived, depends on the return temperature of the cooling circuit and the size of the heat exchanger.
12 LT-PEMFC CHP | E. An asterisk (*) in the reference indicate high uncertainty or "guesstimate", where more certain data where not available.
12 LT-PEMFC CHP | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
12 LT-PEMFC CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
12 LT-PEMFC CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
12 LT-PEMFC CHP | J. No known use, data from n-gas engines
12 LT-PEMFC CHP | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
12 LT-PEMFC CHP | A. The boiler in the plant is a circulating fluid bed boiler (CFB) producing steam to be used in a subsequent \n extraction steam turbine with steam re-heat.
12 LT-PEMFC CHP | C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). This comes in addition to direct condensation that may yield 22% (of thermal input) when operated with combustion air humi...
12 LT-PEMFC CHP | D. Secondary regulation normally relates to power production.
12 LT-PEMFC CHP | E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator). Warm start-up time is \n particularly low for fluid bed types of plants.
12 LT-PEMFC CHP | F. It is to be expected that the NOx level is low from the CFB, and that the necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 20 g/GJ, in which case SCR is used. From 2017 NOx (and other emissions) must fulfil the BAT_AEL values of the LCP BREF note.
12 LT-PEMFC CHP | G. Warm start is starting with a glowing bed and a warm deaerator.
12 LT-PEMFC CHP | H. The electricity efficiency is applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to the effects of load variations, turbine outages and other incidents. Efficiencies refer to thermal input by lower heatin...
12 LT-PEMFC CHP | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. \n Financial data and Technological specific dat...
12 LT-PEMFC CHP | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply \n opportunities and energy supply obligations, amongst other things.\n The additional investment is listed in the bottom row.
12 LT-PEMFC CHP | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate, if applicable, is not included. Electricity consumption is not included as a cost for CHP, and revenues from sale of electricity and heat are ...
12 LT-PEMFC CHP | M. Binary value where 1 = yes and 0 = no
12 LT-PEMFC CHP | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
12 LT-PEMFC CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
12 LT-PEMFC CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
12 LT-PEMFC CHP | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
12 LT-PEMFC CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
12 LT-PEMFC CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
12 LT-PEMFC CHP | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
12 LT-PEMFC CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
12 LT-PEMFC CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
12 LT-PEMFC CHP | P. Reference to heat output because of the lack of electricity production.
12 LT-PEMFC CHP | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
12 LT-PEMFC CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
12 LT-PEMFC CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
12 LT-PEMFC CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
12 LT-PEMFC CHP | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Onshore turbines | A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present m...
20 Onshore turbines | A. The full load hours (annual produktion (MWh) per installed power (MW)) depending on the actual location of the wind farm, wake losses and technological characteristics of the individual turbine. The value is an average for the expected locations of the wind farms. FLH also depends on wake los...
20 Onshore turbines | B. Modern turbines has typically higher forced outage than older smaller turbines had when they were newer due to more complex technology.
20 Onshore turbines | C. Planned outage is typically 1-2 service visits a year, with a maximum duration of one work day, but there can also be planned outage due to shadow flicker stop or sector management (protect turbines at given wind speeds and directions, where they are dense spaced).
20 Onshore turbines | D. The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine
20 Onshore turbines | E. The construction time is the periode from FID to commissioning. But from first "dig" to turbines are in operation less than ½ a year is needed for smaller wind farms (clusters), where the similar periode for larger wind farms will be longer. The planning time from idea to construction starts w...
20 Onshore turbines | F. An area of around 50 m x 50 m is needed for a modern wind turbine. Another way of defining the "area use" could be the noise zone, which ranges up to 600-800 m from the wind turbine in worst case.
20 Onshore turbines | G. Wind turbines can be downward regulated within very short time and can therefore (if the wind is blowing) be used in both the primary and secondary downward regulation.
20 Onshore turbines | H. 2015 Investment costs are based on a number of prospects for projects published in relation to Køberetsordningen. 2020 investment costs are based on updated data from Køberetsordningen. Note that the investment costs listed here includes construction loan interests
20 Onshore turbines | I. 75 % of the total yearly O&M costs are assumed to be fixed cost and 25 % are assumed to be variable cost.
20 Onshore turbines | K. Currently only turbines up to 150 m total height is installed commercially in Denmark because of strict demands to higher turbines. No change in the national regulation is assumed until after 2020. Some test sites allow for larger turbines. Aboard e.g. in Germany turbines with at total higher...
20 Onshore turbines | L. It is expected that the production (FLH) increase 13% from 2015 to 2020 and 3% from 2020-2030 and 1% per decade from 2030-2050
20 Onshore turbines | M. Includes development cost.
20 Onshore turbines | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
20 Onshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Onshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Onshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Onshore turbines | F. This plant is equipped with a Tail-end SCR catalyst for DeNOx and an electrostatic precipitator for catching dust/fly ash
20 Onshore turbines | G. Warm start is starting with the steam system being pressurized.
20 Onshore turbines | H. The electricity efficiency is applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to due to the effects of load variations, turbine outages and other incidents. Efficiencies refer to thermal input by lower...
20 Onshore turbines | I. The Cv value may vary according to the optimisation of the plant. A modest value representing a choice with current \n power/heat prices is shown.
20 Onshore turbines | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total \n investment, e.g. additional fuel storage, conditions for foundation and harbour facilities.\n Financial data and Technological specific data are essentially the total cos...
20 Onshore turbines | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities energy supply obligations, amongst other things. The additional investment is listed in the bottom row.
20 Onshore turbines | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate, if applicable, is not included. Electricity consumption is not included as a cost for CHP, and revenues from sale of electricity and heat are ...
20 Onshore turbines | M. Binary value where 1 = yes and 0 = no
20 Onshore turbines | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
20 Onshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Onshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Onshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Onshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Onshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Onshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Onshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Onshore turbines | N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract..
20 Onshore turbines | O. Binary value where 1 = yes and 0 = no
20 Onshore turbines | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
20 Onshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Onshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Domestic turbines | A. The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
20 Domestic turbines | B. The maintenance normally consists of 1 -2 annual service visits.
20 Domestic turbines | C. An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
20 Domestic turbines | D. Not considered relevant for small domestic turbines.
20 Domestic turbines | E. Based on information from manufacturers and resellers. The
20 Domestic turbines | F. The prices depends significantly on turbine size (5 kW - 6 MEUR/MW; 10 kW - 4 MEUR/MW ; 25 kW - 3 MEUR/MW)
20 Domestic turbines | G. The service cost is assumed fixed to 100EUR/kW/y.
20 Domestic turbines | H. Domestic turbines have a maximum total height of 25 m according to Danish regulations.
20 Domestic turbines | J. No development in the capacity factor is expected, because no changing in the size limitation (legislation) is expected. And because location is crucial and one must expect the turbines is put up at the best positions already. But change in legislation i
20 Domestic turbines | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
20 Domestic turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Domestic turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Domestic turbines | E. An asterisk (*) in the reference indicate high uncertainty or "guesstimate", where more certain data where not available.
20 Domestic turbines | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
20 Domestic turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Domestic turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Domestic turbines | J. No known use, data from n-gas engines
20 Domestic turbines | K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
20 Domestic turbines | A. The boiler in the plant is a circulating fluid bed boiler (CFB) producing steam to be used in a subsequent \n extraction steam turbine with steam re-heat.
20 Domestic turbines | C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). This comes in addition to direct condensation that may yield 22% (of thermal input) when operated with combustion air humi...
20 Domestic turbines | D. Secondary regulation normally relates to power production.
20 Domestic turbines | E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator). Warm start-up time is \n particularly low for fluid bed types of plants.
20 Domestic turbines | F. It is to be expected that the NOx level is low from the CFB, and that the necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 20 g/GJ, in which case SCR is used. From 2017 NOx (and other emissions) must fulfil the BAT_AEL values of the LCP BREF note.
20 Domestic turbines | G. Warm start is starting with a glowing bed and a warm deaerator.
20 Domestic turbines | H. The electricity efficiency is applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to the effects of load variations, turbine outages and other incidents. Efficiencies refer to thermal input by lower heatin...
20 Domestic turbines | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. \n Financial data and Technological specific dat...
20 Domestic turbines | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply \n opportunities and energy supply obligations, amongst other things.\n The additional investment is listed in the bottom row.
20 Domestic turbines | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate, if applicable, is not included. Electricity consumption is not included as a cost for CHP, and revenues from sale of electricity and heat are ...
20 Domestic turbines | M. Binary value where 1 = yes and 0 = no
20 Domestic turbines | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
20 Domestic turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Domestic turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Domestic turbines | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
20 Domestic turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Domestic turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Domestic turbines | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
20 Domestic turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Domestic turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Domestic turbines | P. Reference to heat output because of the lack of electricity production.
20 Domestic turbines | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
20 Domestic turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Domestic turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Domestic turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
20 Domestic turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Offshore turbines | A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present m...
21 Offshore turbines | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
21 Offshore turbines | A. Starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
21 Offshore turbines | B. Offshore turbines have typically higher forced outage than onshore due to access problems in harsh weather. In total a loss of ca. 5% is expected, of which 2% is assumed grid losses and thereby 3% outage is converted to 1 week outage in total
21 Offshore turbines | C. The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine
21 Offshore turbines | D. The construction time is the period from FID to commissioning. The construction time depends on the size of the project, vessel availability and weather conditions.
21 Offshore turbines | E. Calculated based on average spacing of 8 RD between turbines and a square layout. Horns Rev 3 has 9.5, but also quite low wake losses. With 2020 WTG size 8RD corresponds to 6 MW/km^2
21 Offshore turbines | F. The cost includes cost of wind turbines, foundation, installation, planning & development and financing, internal and external grid (array cable, substation, and export cable).
21 Offshore turbines | G. Other is planning & development, environmental impact assessment, insurances and finance costs.
21 Offshore turbines | H. Roughly 70 % of the total yearly O&M costs are assumed to be fixed cost and 30 % are assumed to be variable cost depending on capacity factor. [A previous version listed this share wrongly as 80/20.]
21 Offshore turbines | I. The Specific power is assumed to increase slightly in time because of better wind resource due to larger hub heights
21 Offshore turbines | J. The full load hours are reduced with outage time mentioned under "Energy/technical data" according to the Technology Catalogue guideline. Full load hours are thus net full load hours after outages.
21 Offshore turbines | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
21 Offshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Offshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Offshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Offshore turbines | F. This plant is equipped with a Tail-end SCR catalyst for DeNOx and an electrostatic precipitator for catching dust/fly ash
21 Offshore turbines | G. Warm start is starting with the steam system being pressurized.
21 Offshore turbines | H. The electricity efficiency is applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to due to the effects of load variations, turbine outages and other incidents. Efficiencies refer to thermal input by lower...
21 Offshore turbines | I. The Cv value may vary according to the optimisation of the plant. A modest value representing a choice with current \n power/heat prices is shown.
21 Offshore turbines | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total \n investment, e.g. additional fuel storage, conditions for foundation and harbour facilities.\n Financial data and Technological specific data are essentially the total cos...
21 Offshore turbines | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities energy supply obligations, amongst other things. The additional investment is listed in the bottom row.
21 Offshore turbines | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate, if applicable, is not included. Electricity consumption is not included as a cost for CHP, and revenues from sale of electricity and heat are ...
21 Offshore turbines | M. Binary value where 1 = yes and 0 = no
21 Offshore turbines | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
21 Offshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Offshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Offshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Offshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Offshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Offshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Offshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Offshore turbines | N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract..
21 Offshore turbines | O. Binary value where 1 = yes and 0 = no
21 Offshore turbines | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
21 Offshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Offshore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Near shore turbines | A. The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
21 Near shore turbines | B. The maintenance normally consists of 1 -2 annual service visits.
21 Near shore turbines | C. An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
21 Near shore turbines | D. Not considered relevant for small domestic turbines.
21 Near shore turbines | E. Based on information from manufacturers and resellers. The
21 Near shore turbines | F. The prices depends significantly on turbine size (5 kW - 6 MEUR/MW; 10 kW - 4 MEUR/MW ; 25 kW - 3 MEUR/MW)
21 Near shore turbines | G. The service cost is assumed fixed to 100EUR/kW/y.
21 Near shore turbines | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
21 Near shore turbines | A. Starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
21 Near shore turbines | B. Offshore turbines have typically higher forced outage than onshore due to access problems in harsh weather. In total a loss of ca. 5% is expected, of which 2% is assumed grid losses and thereby 3% outage is converted to 1 week outage in total
21 Near shore turbines | C. The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine
21 Near shore turbines | D. The construction time is the period from FID to commissioning. The construction time depends on the size of the project, vessel availability and weather conditions.
21 Near shore turbines | E. For Nearshore the space requirements becomes "artificial", while typically 1-row projects will be expected. The space is here calculated based on square layout to give a number.
21 Near shore turbines | F. The cost includes cost of wind turbines, foundation, installation, planning & development and financing, internal and external grid (array cable, substation, and export cable).
21 Near shore turbines | G. Other is planning & development, environmental impact assessment, insurances and finance costs.
21 Near shore turbines | H. Roughly 70 % of the total yearly O&M costs are assumed to be fixed cost and 30 % are assumed to be variable cost depending on capacity factor. [A previous version listed this share wrongly as 80/20.]
21 Near shore turbines | I. The Specific power is assumed to increase slightly in time because of better wind resource due to larger hub heights
21 Near shore turbines | J. The full load hours are reduced with outage time mentioned under "Energy/technical data" according to the Technology Catalogue guideline. Full load hours are thus net full load hours after outages.
21 Near shore turbines | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
21 Near shore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Near shore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Near shore turbines | E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator). Warm start-up time is \n particularly low for fluid bed types of plants.
21 Near shore turbines | F. It is to be expected that the NOx level is low from the CFB, and that the necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 20 g/GJ, in which case SCR is used. From 2017 NOx (and other emissions) must fulfil the BAT_AEL values of the LCP BREF note.
21 Near shore turbines | G. Warm start is starting with a glowing bed and a warm deaerator.
21 Near shore turbines | H. The electricity efficiency is applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to the effects of load variations, turbine outages and other incidents. Efficiencies refer to thermal input by lower heatin...
21 Near shore turbines | J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. \n Financial data and Technological specific dat...
21 Near shore turbines | K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply \n opportunities and energy supply obligations, amongst other things.\n The additional investment is listed in the bottom row.
21 Near shore turbines | L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate, if applicable, is not included. Electricity consumption is not included as a cost for CHP, and revenues from sale of electricity and heat are ...
21 Near shore turbines | M. Binary value where 1 = yes and 0 = no
21 Near shore turbines | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
21 Near shore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Near shore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Near shore turbines | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
21 Near shore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Near shore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Near shore turbines | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
21 Near shore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Near shore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Near shore turbines | P. Reference to heat output because of the lack of electricity production.
21 Near shore turbines | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
21 Near shore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Near shore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Near shore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
21 Near shore turbines | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
22 Rooftop PV residential | A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present m...
22 Rooftop PV residential | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
22 Rooftop PV residential | A. Starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
22 Rooftop PV residential | B. Offshore turbines have typically higher forced outage than onshore due to access problems in harsh weather. In total a loss of ca. 5% is expected, of which 2% is assumed grid losses and thereby 3% outage is converted to 1 week outage in total
22 Rooftop PV residential | C. The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine
22 Rooftop PV residential | D. The construction time is the period from FID to commissioning. The construction time depends on the size of the project, vessel availability and weather conditions.
22 Rooftop PV residential | E. Calculated based on average spacing of 8 RD between turbines and a square layout. Horns Rev 3 has 9.5, but also quite low wake losses. With 2020 WTG size 8RD corresponds to 6 MW/km^2
22 Rooftop PV residential | F. The cost includes cost of wind turbines, foundation, installation, planning & development and financing, internal and external grid (array cable, substation, and export cable).
22 Rooftop PV residential | G. Other is planning & development, environmental impact assessment, insurances and finance costs.
22 Rooftop PV residential | H. Roughly 70 % of the total yearly O&M costs are assumed to be fixed cost and 30 % are assumed to be variable cost depending on capacity factor. [A previous version listed this share wrongly as 80/20.]
22 Rooftop PV residential | I. The Specific power is assumed to increase slightly in time because of better wind resource due to larger hub heights
22 Rooftop PV residential | J. The full load hours are reduced with outage time mentioned under "Energy/technical data" according to the Technology Catalogue guideline. Full load hours are thus net full load hours after outages.
22 Rooftop PV residential | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
22 Rooftop PV residential | A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Denmark as determined among 25 measurement stations is 1068 (kWh/m2/y) ± 3.1 %. The best sites demonstrate values around 1100 kWh/m2/y.
22 Rooftop PV residential | A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
22 Rooftop PV residential | A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
22 Rooftop PV residential | B. The area requirement decreases as the efficiency of PV panels increases.
22 Rooftop PV residential | B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the sp...
22 Rooftop PV residential | B2. 110 kWp corresponding to a panel area of approximately 400 - 700 m2.
22 Rooftop PV residential | B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
22 Rooftop PV residential | C. The peak power of the system is the max. power of the PV modules (DC).
22 Rooftop PV residential | D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desir...
22 Rooftop PV residential | E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, ...
22 Rooftop PV residential | F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflecte...
22 Rooftop PV residential | G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
22 Rooftop PV residential | H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added ...
22 Rooftop PV residential | I. Not relevant for small and medium size plants.
22 Rooftop PV residential | K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
22 Rooftop PV residential | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
22 Rooftop PV residential | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
22 Rooftop PV residential | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
22 Rooftop PV residential | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
22 Rooftop PV residential | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
22 Rooftop PV residential | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
22 Rooftop PV residential | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
22 Rooftop PV residential | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
22 Rooftop PV residential | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
22 Rooftop PV residential | T. The added tracker cost is based on interviews with Danish manufacturers.
22 Rooftop PV residential | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
22 Rooftop PV residential | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
22 Rooftop PV residential | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
22 Rooftop PV residential | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
22 Rooftop PV residential | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
22 Rooftop PV residential | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
22 Rooftop PV comm.&industrial | A. The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
22 Rooftop PV comm.&industrial | B. The maintenance normally consists of 1 -2 annual service visits.
22 Rooftop PV comm.&industrial | C. An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
22 Rooftop PV comm.&industrial | D. Not considered relevant for small domestic turbines.
22 Rooftop PV comm.&industrial | E. Based on information from manufacturers and resellers. The
22 Rooftop PV comm.&industrial | F. The prices depends significantly on turbine size (5 kW - 6 MEUR/MW; 10 kW - 4 MEUR/MW ; 25 kW - 3 MEUR/MW)
22 Rooftop PV comm.&industrial | G. The service cost is assumed fixed to 100EUR/kW/y.
22 Rooftop PV comm.&industrial | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
22 Rooftop PV comm.&industrial | A. Starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
22 Rooftop PV comm.&industrial | B. Offshore turbines have typically higher forced outage than onshore due to access problems in harsh weather. In total a loss of ca. 5% is expected, of which 2% is assumed grid losses and thereby 3% outage is converted to 1 week outage in total
22 Rooftop PV comm.&industrial | C. The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine
22 Rooftop PV comm.&industrial | D. The construction time is the period from FID to commissioning. The construction time depends on the size of the project, vessel availability and weather conditions.
22 Rooftop PV comm.&industrial | E. For Nearshore the space requirements becomes "artificial", while typically 1-row projects will be expected. The space is here calculated based on square layout to give a number.
22 Rooftop PV comm.&industrial | F. The cost includes cost of wind turbines, foundation, installation, planning & development and financing, internal and external grid (array cable, substation, and export cable).
22 Rooftop PV comm.&industrial | G. Other is planning & development, environmental impact assessment, insurances and finance costs.
22 Rooftop PV comm.&industrial | H. Roughly 70 % of the total yearly O&M costs are assumed to be fixed cost and 30 % are assumed to be variable cost depending on capacity factor. [A previous version listed this share wrongly as 80/20.]
22 Rooftop PV comm.&industrial | I. The Specific power is assumed to increase slightly in time because of better wind resource due to larger hub heights
22 Rooftop PV comm.&industrial | J. The full load hours are reduced with outage time mentioned under "Energy/technical data" according to the Technology Catalogue guideline. Full load hours are thus net full load hours after outages.
22 Rooftop PV comm.&industrial | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
22 Rooftop PV comm.&industrial | A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Denmark as determined among 25 measurement stations is 1068 (kWh/m2/y) ± 3.1 %. The best sites demonstrate values around 1100 kWh/m2/y.
22 Rooftop PV comm.&industrial | A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
22 Rooftop PV comm.&industrial | A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
22 Rooftop PV comm.&industrial | B. The area requirement decreases as the efficiency of PV panels increases.
22 Rooftop PV comm.&industrial | B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the sp...
22 Rooftop PV comm.&industrial | B2. 110 kWp corresponding to a panel area of approximately 400 - 700 m2.
22 Rooftop PV comm.&industrial | B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
22 Rooftop PV comm.&industrial | C. The peak power of the system is the max. power of the PV modules (DC).
22 Rooftop PV comm.&industrial | D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desir...
22 Rooftop PV comm.&industrial | E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, ...
22 Rooftop PV comm.&industrial | F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflecte...
22 Rooftop PV comm.&industrial | G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
22 Rooftop PV comm.&industrial | H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added ...
22 Rooftop PV comm.&industrial | I. Not relevant for small and medium size plants.
22 Rooftop PV comm.&industrial | K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
22 Rooftop PV comm.&industrial | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
22 Rooftop PV comm.&industrial | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
22 Rooftop PV comm.&industrial | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
22 Rooftop PV comm.&industrial | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
22 Rooftop PV comm.&industrial | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
22 Rooftop PV comm.&industrial | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
22 Rooftop PV comm.&industrial | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
22 Rooftop PV comm.&industrial | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
22 Rooftop PV comm.&industrial | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
22 Rooftop PV comm.&industrial | T. The added tracker cost is based on interviews with Danish manufacturers.
22 Rooftop PV comm.&industrial | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
22 Rooftop PV comm.&industrial | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
22 Rooftop PV comm.&industrial | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
22 Rooftop PV comm.&industrial | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
22 Rooftop PV comm.&industrial | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
22 Rooftop PV comm.&industrial | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
22 Utility-scale PV | A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present m...
22 Utility-scale PV | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
22 Utility-scale PV | A. Starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
22 Utility-scale PV | B. Offshore turbines have typically higher forced outage than onshore due to access problems in harsh weather. In total a loss of ca. 5% is expected, of which 2% is assumed grid losses and thereby 3% outage is converted to 1 week outage in total
22 Utility-scale PV | C. The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine
22 Utility-scale PV | D. The construction time is the period from FID to commissioning. The construction time depends on the size of the project, vessel availability and weather conditions.
22 Utility-scale PV | E. Calculated based on average spacing of 8 RD between turbines and a square layout. Horns Rev 3 has 9.5, but also quite low wake losses. With 2020 WTG size 8RD corresponds to 6 MW/km^2
22 Utility-scale PV | F. The cost includes cost of wind turbines, foundation, installation, planning & development and financing, internal and external grid (array cable, substation, and export cable).
22 Utility-scale PV | G. Other is planning & development, environmental impact assessment, insurances and finance costs.
22 Utility-scale PV | H. Roughly 70 % of the total yearly O&M costs are assumed to be fixed cost and 30 % are assumed to be variable cost depending on capacity factor. [A previous version listed this share wrongly as 80/20.]
22 Utility-scale PV | I. The Specific power is assumed to increase slightly in time because of better wind resource due to larger hub heights
22 Utility-scale PV | J. The full load hours are reduced with outage time mentioned under "Energy/technical data" according to the Technology Catalogue guideline. Full load hours are thus net full load hours after outages.
22 Utility-scale PV | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
22 Utility-scale PV | A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Denmark as determined among 25 measurement stations is 1068 (kWh/m2/y) ± 3.1 %. The best sites demonstrate values around 1100 kWh/m2/y.
22 Utility-scale PV | A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
22 Utility-scale PV | A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
22 Utility-scale PV | B. The area requirement decreases as the efficiency of PV panels increases.
22 Utility-scale PV | B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the sp...
22 Utility-scale PV | B2. 110 kWp corresponding to a panel area of approximately 400 - 700 m2.
22 Utility-scale PV | B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
22 Utility-scale PV | C. The peak power of the system is the max. power of the PV modules (DC).
22 Utility-scale PV | D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desir...
22 Utility-scale PV | E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, ...
22 Utility-scale PV | F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflecte...
22 Utility-scale PV | G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
22 Utility-scale PV | H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added ...
22 Utility-scale PV | I. Not relevant for small and medium size plants.
22 Utility-scale PV | K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
22 Utility-scale PV | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
22 Utility-scale PV | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
22 Utility-scale PV | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
22 Utility-scale PV | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
22 Utility-scale PV | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
22 Utility-scale PV | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
22 Utility-scale PV | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
22 Utility-scale PV | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
22 Utility-scale PV | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
22 Utility-scale PV | T. The added tracker cost is based on interviews with Danish manufacturers.
22 Utility-scale PV | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
22 Utility-scale PV | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
22 Utility-scale PV | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
22 Utility-scale PV | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
22 Utility-scale PV | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
22 Utility-scale PV | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
22 Utility-scale PV tracker | A. The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
22 Utility-scale PV tracker | B. The maintenance normally consists of 1 -2 annual service visits.
22 Utility-scale PV tracker | C. An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
22 Utility-scale PV tracker | D. Not considered relevant for small domestic turbines.
22 Utility-scale PV tracker | E. Based on information from manufacturers and resellers. The
22 Utility-scale PV tracker | F. The prices depends significantly on turbine size (5 kW - 6 MEUR/MW; 10 kW - 4 MEUR/MW ; 25 kW - 3 MEUR/MW)
22 Utility-scale PV tracker | G. The service cost is assumed fixed to 100EUR/kW/y.
22 Utility-scale PV tracker | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
22 Utility-scale PV tracker | A. Starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
22 Utility-scale PV tracker | B. Offshore turbines have typically higher forced outage than onshore due to access problems in harsh weather. In total a loss of ca. 5% is expected, of which 2% is assumed grid losses and thereby 3% outage is converted to 1 week outage in total
22 Utility-scale PV tracker | C. The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine
22 Utility-scale PV tracker | D. The construction time is the period from FID to commissioning. The construction time depends on the size of the project, vessel availability and weather conditions.
22 Utility-scale PV tracker | E. For Nearshore the space requirements becomes "artificial", while typically 1-row projects will be expected. The space is here calculated based on square layout to give a number.
22 Utility-scale PV tracker | F. The cost includes cost of wind turbines, foundation, installation, planning & development and financing, internal and external grid (array cable, substation, and export cable).
22 Utility-scale PV tracker | G. Other is planning & development, environmental impact assessment, insurances and finance costs.
22 Utility-scale PV tracker | H. Roughly 70 % of the total yearly O&M costs are assumed to be fixed cost and 30 % are assumed to be variable cost depending on capacity factor. [A previous version listed this share wrongly as 80/20.]
22 Utility-scale PV tracker | I. The Specific power is assumed to increase slightly in time because of better wind resource due to larger hub heights
22 Utility-scale PV tracker | J. The full load hours are reduced with outage time mentioned under "Energy/technical data" according to the Technology Catalogue guideline. Full load hours are thus net full load hours after outages.
22 Utility-scale PV tracker | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
22 Utility-scale PV tracker | A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Denmark as determined among 25 measurement stations is 1068 (kWh/m2/y) ± 3.1 %. The best sites demonstrate values around 1100 kWh/m2/y.
22 Utility-scale PV tracker | A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
22 Utility-scale PV tracker | A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Denmark as determined among 25 measurement stations is 1068 (kWh/m2/y) ± 3.1 %. The best sites demonstrate values around 1100 kWh/m2/y.
22 Utility-scale PV tracker | A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
22 Utility-scale PV tracker | A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
22 Utility-scale PV tracker | B. The area requirement decreases as the efficiency of PV panels increases.
22 Utility-scale PV tracker | B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the sp...
22 Utility-scale PV tracker | B2. 110 kWp corresponding to a panel area of approximately 400 - 700 m2.
22 Utility-scale PV tracker | B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
22 Utility-scale PV tracker | C. The peak power of the system is the max. power of the PV modules (DC).
22 Utility-scale PV tracker | D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desir...
22 Utility-scale PV tracker | E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, ...
22 Utility-scale PV tracker | F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflecte...
22 Utility-scale PV tracker | G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
22 Utility-scale PV tracker | H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added ...
22 Utility-scale PV tracker | I. Not relevant for small and medium size plants.
22 Utility-scale PV tracker | K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
22 Utility-scale PV tracker | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
22 Utility-scale PV tracker | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
22 Utility-scale PV tracker | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
22 Utility-scale PV tracker | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
22 Utility-scale PV tracker | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
22 Utility-scale PV tracker | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
22 Utility-scale PV tracker | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
22 Utility-scale PV tracker | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
22 Utility-scale PV tracker | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
22 Utility-scale PV tracker | T. The added tracker cost is based on interviews with Danish manufacturers.
22 Utility-scale PV tracker | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
22 Utility-scale PV tracker | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
22 Utility-scale PV tracker | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
22 Utility-scale PV tracker | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
22 Utility-scale PV tracker | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
22 Utility-scale PV tracker | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
23 Wave Energy | A. The cost presented provides an estimate for what capital cost and operating costs of wave power converters might be in the future assuming all R&D challenges have been overcome, that economics of scale have been realized and that efficiencies in production and operation due to the learning cur...
23 Wave Energy | B. Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
23 Wave Energy | C. Much dependent on plant size and location.
23 Wave Energy | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
23 Wave Energy | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
23 Wave Energy | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
23 Wave Energy | A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present m...
23 Wave Energy | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
23 Wave Energy | A. Starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
23 Wave Energy | B. Offshore turbines have typically higher forced outage than onshore due to access problems in harsh weather. In total a loss of ca. 5% is expected, of which 2% is assumed grid losses and thereby 3% outage is converted to 1 week outage in total
23 Wave Energy | C. The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine
23 Wave Energy | D. The construction time is the period from FID to commissioning. The construction time depends on the size of the project, vessel availability and weather conditions.
23 Wave Energy | E. Calculated based on average spacing of 8 RD between turbines and a square layout. Horns Rev 3 has 9.5, but also quite low wake losses. With 2020 WTG size 8RD corresponds to 6 MW/km^2
23 Wave Energy | F. The cost includes cost of wind turbines, foundation, installation, planning & development and financing, internal and external grid (array cable, substation, and export cable).
23 Wave Energy | G. Other is planning & development, environmental impact assessment, insurances and finance costs.
23 Wave Energy | H. Roughly 70 % of the total yearly O&M costs are assumed to be fixed cost and 30 % are assumed to be variable cost depending on capacity factor. [A previous version listed this share wrongly as 80/20.]
23 Wave Energy | I. The Specific power is assumed to increase slightly in time because of better wind resource due to larger hub heights
23 Wave Energy | J. The full load hours are reduced with outage time mentioned under "Energy/technical data" according to the Technology Catalogue guideline. Full load hours are thus net full load hours after outages.
23 Wave Energy | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
23 Wave Energy | A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Denmark as determined among 25 measurement stations is 1068 (kWh/m2/y) ± 3.1 %. The best sites demonstrate values around 1100 kWh/m2/y.
23 Wave Energy | A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
23 Wave Energy | A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
23 Wave Energy | B. The area requirement decreases as the efficiency of PV panels increases.
23 Wave Energy | B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the sp...
23 Wave Energy | B2. 110 kWp corresponding to a panel area of approximately 400 - 700 m2.
23 Wave Energy | B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
23 Wave Energy | C. The peak power of the system is the max. power of the PV modules (DC).
23 Wave Energy | D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desir...
23 Wave Energy | E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, ...
23 Wave Energy | F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflecte...
23 Wave Energy | G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
23 Wave Energy | H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added ...
23 Wave Energy | I. Not relevant for small and medium size plants.
23 Wave Energy | K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
23 Wave Energy | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
23 Wave Energy | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
23 Wave Energy | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
23 Wave Energy | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
23 Wave Energy | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
23 Wave Energy | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
23 Wave Energy | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
23 Wave Energy | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
23 Wave Energy | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
23 Wave Energy | T. The added tracker cost is based on interviews with Danish manufacturers.
23 Wave Energy | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
23 Wave Energy | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
23 Wave Energy | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
23 Wave Energy | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
23 Wave Energy | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
23 Wave Energy | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, airsource 1 MW | A. The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
40 Comp. hp, airsource 1 MW | B. The maintenance normally consists of 1 -2 annual service visits.
40 Comp. hp, airsource 1 MW | C. An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
40 Comp. hp, airsource 1 MW | D. Not considered relevant for small domestic turbines.
40 Comp. hp, airsource 1 MW | E. Based on information from manufacturers and resellers. The
40 Comp. hp, airsource 1 MW | F. The prices depends significantly on turbine size (5 kW - 6 MEUR/MW; 10 kW - 4 MEUR/MW ; 25 kW - 3 MEUR/MW)
40 Comp. hp, airsource 1 MW | G. The service cost is assumed fixed to 100EUR/kW/y.
40 Comp. hp, airsource 1 MW | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
40 Comp. hp, airsource 1 MW | A. Starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
40 Comp. hp, airsource 1 MW | A. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
40 Comp. hp, airsource 1 MW | A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of th...
40 Comp. hp, airsource 1 MW | B. Includes energy consumption for defrosting and auxiliary electricity consumption.
40 Comp. hp, airsource 1 MW | C. Total efficiency, net (%), name plate is at an ambient temperature of -1 °C. District heating temperatures are 35 °C return and 70 °C forward.
40 Comp. hp, airsource 1 MW | D. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
40 Comp. hp, airsource 1 MW | E. Auxiliary electricity consumption is included in the Total efficiency. Electricity for fans constitute appr. 0.3 %. Cost for electricity is therefore not accounted for in variable O&M
40 Comp. hp, airsource 1 MW | F. Does not include tendering and regulatory approvals.
40 Comp. hp, airsource 1 MW | G. The development within construction time will depend on future production figures and standardization of plants.
40 Comp. hp, airsource 1 MW | H. The regulation ablility will depend on the future markets for regulation services.
40 Comp. hp, airsource 1 MW | I. Cold start of time is starting a heat pump where stand by heating has not been applied
40 Comp. hp, airsource 1 MW | J. Operation at part load will usually increase COP but also variable O&M costs
40 Comp. hp, airsource 1 MW | K. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
40 Comp. hp, airsource 1 MW | L. Land is usually owned by the company
40 Comp. hp, airsource 1 MW | M. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
40 Comp. hp, airsource 1 MW | N. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
40 Comp. hp, airsource 1 MW | O. 1/4 MWh-heat per MW is lost during startup
40 Comp. hp, airsource 1 MW | P. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 15 % as compontents must be rated for higher pressure levels
40 Comp. hp, airsource 1 MW | Q. Including land for air coolers
40 Comp. hp, airsource 1 MW | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Comp. hp, airsource 1 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, airsource 1 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, airsource 1 MW | D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desir...
40 Comp. hp, airsource 1 MW | E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, ...
40 Comp. hp, airsource 1 MW | F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflecte...
40 Comp. hp, airsource 1 MW | G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
40 Comp. hp, airsource 1 MW | H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added ...
40 Comp. hp, airsource 1 MW | I. Not relevant for small and medium size plants.
40 Comp. hp, airsource 1 MW | K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
40 Comp. hp, airsource 1 MW | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
40 Comp. hp, airsource 1 MW | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
40 Comp. hp, airsource 1 MW | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
40 Comp. hp, airsource 1 MW | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
40 Comp. hp, airsource 1 MW | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
40 Comp. hp, airsource 1 MW | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
40 Comp. hp, airsource 1 MW | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
40 Comp. hp, airsource 1 MW | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
40 Comp. hp, airsource 1 MW | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
40 Comp. hp, airsource 1 MW | T. The added tracker cost is based on interviews with Danish manufacturers.
40 Comp. hp, airsource 1 MW | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
40 Comp. hp, airsource 1 MW | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
40 Comp. hp, airsource 1 MW | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
40 Comp. hp, airsource 1 MW | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Comp. hp, airsource 1 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, airsource 1 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, airsource 3 MW | A. The cost presented provides an estimate for what capital cost and operating costs of wave power converters might be in the future assuming all R&D challenges have been overcome, that economics of scale have been realized and that efficiencies in production and operation due to the learning cur...
40 Comp. hp, airsource 3 MW | B. Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
40 Comp. hp, airsource 3 MW | C. Much dependent on plant size and location.
40 Comp. hp, airsource 3 MW | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Comp. hp, airsource 3 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, airsource 3 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, airsource 3 MW | A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present m...
40 Comp. hp, airsource 3 MW | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
40 Comp. hp, airsource 3 MW | A. Starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
40 Comp. hp, airsource 3 MW | A. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
40 Comp. hp, airsource 3 MW | A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of th...
40 Comp. hp, airsource 3 MW | B. Includes energy consumption for defrosting and auxiliary electricity consumption.
40 Comp. hp, airsource 3 MW | C. Total efficiency, net (%), name plate is at an ambient temperature of -1 °C. District heating temperatures are 35 °C return and 70 °C forward.
40 Comp. hp, airsource 3 MW | D. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
40 Comp. hp, airsource 3 MW | E. Auxiliary electricity consumption is included in the Total efficiency. Electricity for fans constitute appr. 0.3 %. Cost for electricity is therefore not accounted for in variable O&M
40 Comp. hp, airsource 3 MW | F. Does not include tendering and regulatory approvals.
40 Comp. hp, airsource 3 MW | G. The development within construction time will depend on future production figures and standardization of plants.
40 Comp. hp, airsource 3 MW | H. The regulation ablility will depend on the future markets for regulation services.
40 Comp. hp, airsource 3 MW | I. Cold start of time is starting a heat pump where stand by heating has not been applied
40 Comp. hp, airsource 3 MW | J. Operation at part load will usually increase COP but also variable O&M costs
40 Comp. hp, airsource 3 MW | K. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
40 Comp. hp, airsource 3 MW | L. Land is usually owned by the company
40 Comp. hp, airsource 3 MW | M. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
40 Comp. hp, airsource 3 MW | N. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
40 Comp. hp, airsource 3 MW | O. 1/4 MWh-heat per MW is lost during startup
40 Comp. hp, airsource 3 MW | P. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 10 % as compontents must be rated for higher pressure levels
40 Comp. hp, airsource 3 MW | Q. Including land for air coolers
40 Comp. hp, airsource 3 MW | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Comp. hp, airsource 3 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, airsource 3 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, airsource 3 MW | F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflecte...
40 Comp. hp, airsource 3 MW | G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
40 Comp. hp, airsource 3 MW | H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added ...
40 Comp. hp, airsource 3 MW | I. Not relevant for small and medium size plants.
40 Comp. hp, airsource 3 MW | K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
40 Comp. hp, airsource 3 MW | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
40 Comp. hp, airsource 3 MW | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
40 Comp. hp, airsource 3 MW | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
40 Comp. hp, airsource 3 MW | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
40 Comp. hp, airsource 3 MW | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
40 Comp. hp, airsource 3 MW | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
40 Comp. hp, airsource 3 MW | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
40 Comp. hp, airsource 3 MW | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
40 Comp. hp, airsource 3 MW | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
40 Comp. hp, airsource 3 MW | T. The added tracker cost is based on interviews with Danish manufacturers.
40 Comp. hp, airsource 3 MW | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
40 Comp. hp, airsource 3 MW | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
40 Comp. hp, airsource 3 MW | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
40 Comp. hp, airsource 3 MW | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Comp. hp, airsource 3 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, airsource 3 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, airsource 10 MW | A. The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
40 Comp. hp, airsource 10 MW | B. The maintenance normally consists of 1 -2 annual service visits.
40 Comp. hp, airsource 10 MW | C. An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
40 Comp. hp, airsource 10 MW | D. Not considered relevant for small domestic turbines.
40 Comp. hp, airsource 10 MW | E. Based on information from manufacturers and resellers. The
40 Comp. hp, airsource 10 MW | F. The prices depends significantly on turbine size (5 kW - 6 MEUR/MW; 10 kW - 4 MEUR/MW ; 25 kW - 3 MEUR/MW)
40 Comp. hp, airsource 10 MW | G. The service cost is assumed fixed to 100EUR/kW/y.
40 Comp. hp, airsource 10 MW | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
40 Comp. hp, airsource 10 MW | A. Starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
40 Comp. hp, airsource 10 MW | A. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
40 Comp. hp, airsource 10 MW | A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of th...
40 Comp. hp, airsource 10 MW | B. Includes energy consumption for defrosting and auxiliary electricity consumption.
40 Comp. hp, airsource 10 MW | C. Total efficiency, net (%), name plate is at an ambient temperature of -1 °C. District heating temperatures are 35 °C return and 70 °C forward.
40 Comp. hp, airsource 10 MW | D. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
40 Comp. hp, airsource 10 MW | E. Auxiliary electricity consumption is included in the Total efficiency. Electricity for fans constitute appr. 0.3 %. Cost for electricity is therefore not accounted for in variable O&M
40 Comp. hp, airsource 10 MW | F. Does not include tendering and regulatory approvals.
40 Comp. hp, airsource 10 MW | G. The development within construction time will depend on future production figures and standardization of plants.
40 Comp. hp, airsource 10 MW | H. The regulation ablility will depend on the future markets for regulation services.
40 Comp. hp, airsource 10 MW | I. Cold start of time is starting a heat pump where stand by heating has not been applied
40 Comp. hp, airsource 10 MW | J. Operation at part load will usually increase COP but also variable O&M costs
40 Comp. hp, airsource 10 MW | K. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
40 Comp. hp, airsource 10 MW | L. Land is usually owned by the company
40 Comp. hp, airsource 10 MW | M. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
40 Comp. hp, airsource 10 MW | N. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
40 Comp. hp, airsource 10 MW | O. 1/4 MWh-heat per MW is lost during startup
40 Comp. hp, airsource 10 MW | P. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 5 % as compontents must be rated for higher pressure levels
40 Comp. hp, airsource 10 MW | Q. Including land for air coolers
40 Comp. hp, airsource 10 MW | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Comp. hp, airsource 10 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, airsource 10 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, airsource 10 MW | D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desir...
40 Comp. hp, airsource 10 MW | E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, ...
40 Comp. hp, airsource 10 MW | F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflecte...
40 Comp. hp, airsource 10 MW | G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
40 Comp. hp, airsource 10 MW | H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added ...
40 Comp. hp, airsource 10 MW | I. Not relevant for small and medium size plants.
40 Comp. hp, airsource 10 MW | K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
40 Comp. hp, airsource 10 MW | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
40 Comp. hp, airsource 10 MW | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
40 Comp. hp, airsource 10 MW | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
40 Comp. hp, airsource 10 MW | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
40 Comp. hp, airsource 10 MW | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
40 Comp. hp, airsource 10 MW | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
40 Comp. hp, airsource 10 MW | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
40 Comp. hp, airsource 10 MW | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
40 Comp. hp, airsource 10 MW | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
40 Comp. hp, airsource 10 MW | T. The added tracker cost is based on interviews with Danish manufacturers.
40 Comp. hp, airsource 10 MW | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
40 Comp. hp, airsource 10 MW | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
40 Comp. hp, airsource 10 MW | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
40 Comp. hp, airsource 10 MW | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Comp. hp, airsource 10 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, airsource 10 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 1 MW | A. The cost presented provides an estimate for what capital cost and operating costs of wave power converters might be in the future assuming all R&D challenges have been overcome, that economics of scale have been realized and that efficiencies in production and operation due to the learning cur...
40 Comp. hp, excess heat 1 MW | B. Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
40 Comp. hp, excess heat 1 MW | C. Much dependent on plant size and location.
40 Comp. hp, excess heat 1 MW | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Comp. hp, excess heat 1 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 1 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 1 MW | A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present m...
40 Comp. hp, excess heat 1 MW | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
40 Comp. hp, excess heat 1 MW | A. Starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
40 Comp. hp, excess heat 1 MW | A. Based on cooling water that is cooled from 25 to 15 °C. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
40 Comp. hp, excess heat 1 MW | A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of th...
40 Comp. hp, excess heat 1 MW | B. Total efficiency, net (%), name plate is at district heating temperatures of 35 °C return and 70 °C forward.
40 Comp. hp, excess heat 1 MW | C. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
40 Comp. hp, excess heat 1 MW | D. Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M
40 Comp. hp, excess heat 1 MW | E. Does not include tendering and regulatory approvals.
40 Comp. hp, excess heat 1 MW | F. The development within construction time will depend on future production figures and standardization of plants.
40 Comp. hp, excess heat 1 MW | G. The regulation ability will depend on the future marktes for regulation services.
40 Comp. hp, excess heat 1 MW | H. Cold start of time is starting a heat pump where stand by heating has not been applied
40 Comp. hp, excess heat 1 MW | I. Operation at part load will usually increase COP but also variable O&M costs
40 Comp. hp, excess heat 1 MW | J. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
40 Comp. hp, excess heat 1 MW | K. Land is usually owned by the company
40 Comp. hp, excess heat 1 MW | L. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
40 Comp. hp, excess heat 1 MW | M. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
40 Comp. hp, excess heat 1 MW | N. 1/4 MWh-heat per MW is lost during startup
40 Comp. hp, excess heat 1 MW | O. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 15 % as compontents must be rated for higher pressure levels
40 Comp. hp, excess heat 1 MW | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Comp. hp, excess heat 1 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 1 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 1 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 1 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 1 MW | F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflecte...
40 Comp. hp, excess heat 1 MW | G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
40 Comp. hp, excess heat 1 MW | H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added ...
40 Comp. hp, excess heat 1 MW | I. Not relevant for small and medium size plants.
40 Comp. hp, excess heat 1 MW | K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
40 Comp. hp, excess heat 1 MW | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
40 Comp. hp, excess heat 1 MW | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
40 Comp. hp, excess heat 1 MW | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
40 Comp. hp, excess heat 1 MW | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
40 Comp. hp, excess heat 1 MW | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
40 Comp. hp, excess heat 1 MW | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
40 Comp. hp, excess heat 1 MW | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
40 Comp. hp, excess heat 1 MW | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
40 Comp. hp, excess heat 1 MW | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
40 Comp. hp, excess heat 1 MW | T. The added tracker cost is based on interviews with Danish manufacturers.
40 Comp. hp, excess heat 1 MW | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
40 Comp. hp, excess heat 1 MW | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
40 Comp. hp, excess heat 1 MW | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
40 Comp. hp, excess heat 1 MW | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Comp. hp, excess heat 1 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 1 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 3 MW | A. The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
40 Comp. hp, excess heat 3 MW | B. The maintenance normally consists of 1 -2 annual service visits.
40 Comp. hp, excess heat 3 MW | C. An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
40 Comp. hp, excess heat 3 MW | D. Not considered relevant for small domestic turbines.
40 Comp. hp, excess heat 3 MW | E. Based on information from manufacturers and resellers. The
40 Comp. hp, excess heat 3 MW | F. The prices depends significantly on turbine size (5 kW - 6 MEUR/MW; 10 kW - 4 MEUR/MW ; 25 kW - 3 MEUR/MW)
40 Comp. hp, excess heat 3 MW | G. The service cost is assumed fixed to 100EUR/kW/y.
40 Comp. hp, excess heat 3 MW | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
40 Comp. hp, excess heat 3 MW | A. Starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
40 Comp. hp, excess heat 3 MW | A. Based on cooling water that is cooled from 25 to 15 °C. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
40 Comp. hp, excess heat 3 MW | A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of th...
40 Comp. hp, excess heat 3 MW | B. Total efficiency, net (%), name plate is at district heating temperatures of 35 °C return and 70 °C forward.
40 Comp. hp, excess heat 3 MW | C. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
40 Comp. hp, excess heat 3 MW | D. Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M
40 Comp. hp, excess heat 3 MW | E. Does not include tendering and regulatory approvals.
40 Comp. hp, excess heat 3 MW | F. The development within construction time will depend on future production figures and standardization of plants.
40 Comp. hp, excess heat 3 MW | G. The regulation ability will depend on the future marktes for regulation services.
40 Comp. hp, excess heat 3 MW | H. Cold start of time is starting a heat pump where stand by heating has not been applied
40 Comp. hp, excess heat 3 MW | I. Operation at part load will usually increase COP but also variable O&M costs
40 Comp. hp, excess heat 3 MW | J. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
40 Comp. hp, excess heat 3 MW | K. Land is usually owned by the company
40 Comp. hp, excess heat 3 MW | L. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
40 Comp. hp, excess heat 3 MW | M. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
40 Comp. hp, excess heat 3 MW | N. 1/4 MWh-heat per MW is lost during startup
40 Comp. hp, excess heat 3 MW | O. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 10 % as compontents must be rated for higher pressure levels
40 Comp. hp, excess heat 3 MW | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Comp. hp, excess heat 3 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 3 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 3 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 3 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 3 MW | D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desir...
40 Comp. hp, excess heat 3 MW | E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, ...
40 Comp. hp, excess heat 3 MW | F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflecte...
40 Comp. hp, excess heat 3 MW | G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
40 Comp. hp, excess heat 3 MW | H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added ...
40 Comp. hp, excess heat 3 MW | I. Not relevant for small and medium size plants.
40 Comp. hp, excess heat 3 MW | K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
40 Comp. hp, excess heat 3 MW | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
40 Comp. hp, excess heat 3 MW | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
40 Comp. hp, excess heat 3 MW | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
40 Comp. hp, excess heat 3 MW | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
40 Comp. hp, excess heat 3 MW | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
40 Comp. hp, excess heat 3 MW | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
40 Comp. hp, excess heat 3 MW | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
40 Comp. hp, excess heat 3 MW | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
40 Comp. hp, excess heat 3 MW | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
40 Comp. hp, excess heat 3 MW | T. The added tracker cost is based on interviews with Danish manufacturers.
40 Comp. hp, excess heat 3 MW | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
40 Comp. hp, excess heat 3 MW | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
40 Comp. hp, excess heat 3 MW | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
40 Comp. hp, excess heat 3 MW | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Comp. hp, excess heat 3 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 3 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 10 MW | A. The cost presented provides an estimate for what capital cost and operating costs of wave power converters might be in the future assuming all R&D challenges have been overcome, that economics of scale have been realized and that efficiencies in production and operation due to the learning cur...
40 Comp. hp, excess heat 10 MW | B. Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
40 Comp. hp, excess heat 10 MW | C. Much dependent on plant size and location.
40 Comp. hp, excess heat 10 MW | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Comp. hp, excess heat 10 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 10 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 10 MW | A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present m...
40 Comp. hp, excess heat 10 MW | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
40 Comp. hp, excess heat 10 MW | A. Starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
40 Comp. hp, excess heat 10 MW | A. Based on cooling water that is cooled from 25 to 15 °C. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
40 Comp. hp, excess heat 10 MW | A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of th...
40 Comp. hp, excess heat 10 MW | B. Total efficiency, net (%), name plate is at district heating temperatures of 35 °C return and 70 °C forward.
40 Comp. hp, excess heat 10 MW | C. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
40 Comp. hp, excess heat 10 MW | D. Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M
40 Comp. hp, excess heat 10 MW | E. Does not include tendering and regulatory approvals.
40 Comp. hp, excess heat 10 MW | F. The development within construction time will depend on future production figures and standardization of plants.
40 Comp. hp, excess heat 10 MW | G. The regulation ability will depend on the future marktes for regulation services.
40 Comp. hp, excess heat 10 MW | H. Cold start of time is starting a heat pump where stand by heating has not been applied
40 Comp. hp, excess heat 10 MW | I. Operation at part load will usually increase COP but also variable O&M costs
40 Comp. hp, excess heat 10 MW | J. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
40 Comp. hp, excess heat 10 MW | K. Land is usually owned by the company
40 Comp. hp, excess heat 10 MW | L. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
40 Comp. hp, excess heat 10 MW | M. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
40 Comp. hp, excess heat 10 MW | N. 1/4 MWh-heat per MW is lost during startup
40 Comp. hp, excess heat 10 MW | O. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 5 % as compontents must be rated for higher pressure levels
40 Comp. hp, excess heat 10 MW | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Comp. hp, excess heat 10 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 10 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 10 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 10 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 10 MW | F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflecte...
40 Comp. hp, excess heat 10 MW | G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
40 Comp. hp, excess heat 10 MW | H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added ...
40 Comp. hp, excess heat 10 MW | I. Not relevant for small and medium size plants.
40 Comp. hp, excess heat 10 MW | K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
40 Comp. hp, excess heat 10 MW | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
40 Comp. hp, excess heat 10 MW | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
40 Comp. hp, excess heat 10 MW | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
40 Comp. hp, excess heat 10 MW | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
40 Comp. hp, excess heat 10 MW | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
40 Comp. hp, excess heat 10 MW | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
40 Comp. hp, excess heat 10 MW | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
40 Comp. hp, excess heat 10 MW | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
40 Comp. hp, excess heat 10 MW | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
40 Comp. hp, excess heat 10 MW | T. The added tracker cost is based on interviews with Danish manufacturers.
40 Comp. hp, excess heat 10 MW | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
40 Comp. hp, excess heat 10 MW | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
40 Comp. hp, excess heat 10 MW | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
40 Comp. hp, excess heat 10 MW | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Comp. hp, excess heat 10 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, excess heat 10 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, seawater 20 MW | A. The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
40 Comp. hp, seawater 20 MW | B. The maintenance normally consists of 1 -2 annual service visits.
40 Comp. hp, seawater 20 MW | C. An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
40 Comp. hp, seawater 20 MW | D. Not considered relevant for small domestic turbines.
40 Comp. hp, seawater 20 MW | E. Based on information from manufacturers and resellers. The
40 Comp. hp, seawater 20 MW | F. The prices depends significantly on turbine size (5 kW - 6 MEUR/MW; 10 kW - 4 MEUR/MW ; 25 kW - 3 MEUR/MW)
40 Comp. hp, seawater 20 MW | G. The service cost is assumed fixed to 100EUR/kW/y.
40 Comp. hp, seawater 20 MW | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
40 Comp. hp, seawater 20 MW | A. Starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
40 Comp. hp, seawater 20 MW | A. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
40 Comp. hp, seawater 20 MW | B. Total efficiency, net (%), name plate is at a sea water temperature of 4 °C and district heating temperatures of 40 °C return and 80 °C forward.
40 Comp. hp, seawater 20 MW | C. Annual average is at varying sea water temperatures and district heating temperatures of 40 °C return and 80 °C forward.
40 Comp. hp, seawater 20 MW | D. Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M
40 Comp. hp, seawater 20 MW | E. Does not include tendering and regulatory approvals.
40 Comp. hp, seawater 20 MW | F. The development within construction time will depend on future production figures and standardization of plants.
40 Comp. hp, seawater 20 MW | G. The regulation ability will depend on the future marktes for regulation services.
40 Comp. hp, seawater 20 MW | H. Cold start of time is starting a heat pump where stand by heating has not been applied
40 Comp. hp, seawater 20 MW | I. Operation at part load will usually increase COP but also variable O&M costs
40 Comp. hp, seawater 20 MW | J. It is assumed that heat pumps is connected to existing power stations
40 Comp. hp, seawater 20 MW | K. Land is usually owned by the company
40 Comp. hp, seawater 20 MW | L. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
40 Comp. hp, seawater 20 MW | M. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
40 Comp. hp, seawater 20 MW | N. 1/4 MWh-heat per MW is lost during startup
40 Comp. hp, seawater 20 MW | O. Regards heat pumps that are installed at existing power plants utilizing existing infra structure such as power supply, seawater intake, DH pipes etc. For stand alone plants it is estimated that the total investment is around the upper uncertainty in the table.
40 Comp. hp, seawater 20 MW | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Comp. hp, seawater 20 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, seawater 20 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, seawater 20 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, seawater 20 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, seawater 20 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, seawater 20 MW | D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desir...
40 Comp. hp, seawater 20 MW | E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, ...
40 Comp. hp, seawater 20 MW | F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflecte...
40 Comp. hp, seawater 20 MW | G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
40 Comp. hp, seawater 20 MW | H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added ...
40 Comp. hp, seawater 20 MW | I. Not relevant for small and medium size plants.
40 Comp. hp, seawater 20 MW | K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
40 Comp. hp, seawater 20 MW | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
40 Comp. hp, seawater 20 MW | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
40 Comp. hp, seawater 20 MW | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
40 Comp. hp, seawater 20 MW | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
40 Comp. hp, seawater 20 MW | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
40 Comp. hp, seawater 20 MW | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
40 Comp. hp, seawater 20 MW | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
40 Comp. hp, seawater 20 MW | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
40 Comp. hp, seawater 20 MW | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
40 Comp. hp, seawater 20 MW | T. The added tracker cost is based on interviews with Danish manufacturers.
40 Comp. hp, seawater 20 MW | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
40 Comp. hp, seawater 20 MW | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
40 Comp. hp, seawater 20 MW | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
40 Comp. hp, seawater 20 MW | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Comp. hp, seawater 20 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Comp. hp, seawater 20 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Absorption heat pump, DH | A. The cost presented provides an estimate for what capital cost and operating costs of wave power converters might be in the future assuming all R&D challenges have been overcome, that economics of scale have been realized and that efficiencies in production and operation due to the learning cur...
40 Absorption heat pump, DH | B. Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
40 Absorption heat pump, DH | C. Much dependent on plant size and location.
40 Absorption heat pump, DH | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Absorption heat pump, DH | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Absorption heat pump, DH | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Absorption heat pump, DH | A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present m...
40 Absorption heat pump, DH | A. The heat pump itself only represents a small part of the total investment. Depending on size the heat pump typically represents 0.2 MEUR per. MW heating (excluding drive energy).
40 Absorption heat pump, DH | A1. Capacity is excluding drive energy.
40 Absorption heat pump, DH | B. The heat is assumed delivered at 80 °C in 2015 and 60 °C in 2050
40 Absorption heat pump, DH | C. May vary depending on availability of heat source
40 Absorption heat pump, DH | D. May vary depending on specific type, heat source etc.
40 Absorption heat pump, DH | E. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
40 Absorption heat pump, DH | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Absorption heat pump, DH | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Absorption heat pump, DH | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Absorption heat pump, DH | F. The development within construction time will depend on future production figures and standardization of plants.
40 Absorption heat pump, DH | G. The regulation ability will depend on the future marktes for regulation services.
40 Absorption heat pump, DH | H. Cold start of time is starting a heat pump where stand by heating has not been applied
40 Absorption heat pump, DH | I. Operation at part load will usually increase COP but also variable O&M costs
40 Absorption heat pump, DH | J. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
40 Absorption heat pump, DH | K. Land is usually owned by the company
40 Absorption heat pump, DH | L. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
40 Absorption heat pump, DH | M. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
40 Absorption heat pump, DH | N. 1/4 MWh-heat per MW is lost during startup
40 Absorption heat pump, DH | O. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 5 % as compontents must be rated for higher pressure levels
40 Absorption heat pump, DH | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Absorption heat pump, DH | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Absorption heat pump, DH | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Absorption heat pump, DH | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Absorption heat pump, DH | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Absorption heat pump, DH | F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflecte...
40 Absorption heat pump, DH | G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
40 Absorption heat pump, DH | H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added ...
40 Absorption heat pump, DH | I. Not relevant for small and medium size plants.
40 Absorption heat pump, DH | K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
40 Absorption heat pump, DH | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
40 Absorption heat pump, DH | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
40 Absorption heat pump, DH | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
40 Absorption heat pump, DH | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
40 Absorption heat pump, DH | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
40 Absorption heat pump, DH | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
40 Absorption heat pump, DH | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
40 Absorption heat pump, DH | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
40 Absorption heat pump, DH | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
40 Absorption heat pump, DH | T. The added tracker cost is based on interviews with Danish manufacturers.
40 Absorption heat pump, DH | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
40 Absorption heat pump, DH | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
40 Absorption heat pump, DH | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
40 Absorption heat pump, DH | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 Absorption heat pump, DH | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 Absorption heat pump, DH | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 co2. hp, seawater 50-100 MW | A. The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
40 co2. hp, seawater 50-100 MW | B. The maintenance normally consists of 1 -2 annual service visits.
40 co2. hp, seawater 50-100 MW | C. An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
40 co2. hp, seawater 50-100 MW | D. Not considered relevant for small domestic turbines.
40 co2. hp, seawater 50-100 MW | E. Based on information from manufacturers and resellers. The
40 co2. hp, seawater 50-100 MW | F. The prices depends significantly on turbine size (5 kW - 6 MEUR/MW; 10 kW - 4 MEUR/MW ; 25 kW - 3 MEUR/MW)
40 co2. hp, seawater 50-100 MW | G. The service cost is assumed fixed to 100EUR/kW/y.
40 co2. hp, seawater 50-100 MW | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
40 co2. hp, seawater 50-100 MW | A. Starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
40 co2. hp, seawater 50-100 MW | A. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
40 co2. hp, seawater 50-100 MW | B. Total efficiency, net (%), name plate is at a sea water temperature of 4 °C and district heating temperatures of 40 °C return and 80 °C forward.
40 co2. hp, seawater 50-100 MW | C. Annual average is at varying sea water temperatures and district heating temperatures of 40 °C return and 80 °C forward.
40 co2. hp, seawater 50-100 MW | D. Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M
40 co2. hp, seawater 50-100 MW | E. Does not include tendering and regulatory approvals.
40 co2. hp, seawater 50-100 MW | F. The development within construction time will depend on future production figures and standardization of plants.
40 co2. hp, seawater 50-100 MW | A. Design temperatures are 4 °C seawater and DH temperatues of 70/33 °C.
40 co2. hp, seawater 50-100 MW | B. 45 MW at 1 °C seawater, 64,5 at 4 °C seawater (the design temperature), and 68,4 MW at 14 °C seawater.
40 co2. hp, seawater 50-100 MW | C. Actual development within COP optimization and reduced investment cost depend on the development in fuel and electricity prices.
40 co2. hp, seawater 50-100 MW | D. Name plate efficiency is at 4 °C seawater temperature and DH temperatures are 70/33 °C. Total efficiency is in the range of 2,4 to 3,6 depending on the temperature of the seawater and DH. The plant is not in use in the summer period, otherwise, the efficiency could have been even higher.
40 co2. hp, seawater 50-100 MW | E. The primary auxililary electricity consumption is related to the seawater pumps.
40 co2. hp, seawater 50-100 MW | F. Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M.
40 co2. hp, seawater 50-100 MW | G. Tecnical lifetime is calculated with an outage time of 3 month per year.
40 co2. hp, seawater 50-100 MW | H. Does not include tendering and regulatory approvals.
40 co2. hp, seawater 50-100 MW | I. The development within construction time will depend on future production figures and standardization of plants.
40 co2. hp, seawater 50-100 MW | J. Note that this is only valid for upregulation (i.e. load increase of the heat pump). Downregulation (i.e. load reduction on the heat pump) is at a lower rate, however, this can be compesated by other units in the portfolio.
40 co2. hp, seawater 50-100 MW | K. CO2 heat pumps regulate a lot faster than e.g. ammonia. The regulation ability will depend on the future markets for regulation services.
40 co2. hp, seawater 50-100 MW | L. This is the continous minimum load with only 1 of 2 HP's enabled.
40 co2. hp, seawater 50-100 MW | M. All inputs are based on a single case, DIN Forsyning Heat Pump in Esbjerg.
40 co2. hp, seawater 50-100 MW | N. The warm start-up time is guaranteed to take 0,5 hours but it is, however, expected to take 0,2 hours.
40 co2. hp, seawater 50-100 MW | O. Cold start-up time includes starting a heat pump where stand by heating has not been applied.
40 co2. hp, seawater 50-100 MW | P. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M. DH distribution system is not included.
40 co2. hp, seawater 50-100 MW | Q. 1/4 MWh-heat per MW is lost during startup
40 co2. hp, seawater 50-100 MW | R. The forecast for future prices is an estimate since this is the first CO2 heat pump plant in this size.
40 co2. hp, seawater 50-100 MW | S. The CO2 heat pumps are made with magnetic barrings and are oilfree, therefore the O&M are lower compared to traditional heat pumps
40 co2. hp, seawater 50-100 MW | T. The price is also included in nominal investment (equipment)
40 co2. hp, seawater 50-100 MW | V. The heat pumps produce heating at a higher temperature compared to Name plate several months of the year therefore the Name plate COP is higher than the yearly COP.
40 co2. hp, seawater 50-100 MW | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 co2. hp, seawater 50-100 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 co2. hp, seawater 50-100 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 co2. hp, seawater 50-100 MW | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
40 co2. hp, seawater 50-100 MW | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
40 co2. hp, seawater 50-100 MW | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
40 co2. hp, seawater 50-100 MW | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
40 co2. hp, seawater 50-100 MW | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
40 co2. hp, seawater 50-100 MW | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
40 co2. hp, seawater 50-100 MW | T. The added tracker cost is based on interviews with Danish manufacturers.
40 co2. hp, seawater 50-100 MW | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
40 co2. hp, seawater 50-100 MW | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
40 co2. hp, seawater 50-100 MW | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
40 co2. hp, seawater 50-100 MW | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
40 co2. hp, seawater 50-100 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
40 co2. hp, seawater 50-100 MW | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
41 Electric boiler, small | A. The cost presented provides an estimate for what capital cost and operating costs of wave power converters might be in the future assuming all R&D challenges have been overcome, that economics of scale have been realized and that efficiencies in production and operation due to the learning cur...
41 Electric boiler, small | B. Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
41 Electric boiler, small | C. Much dependent on plant size and location.
41 Electric boiler, small | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
41 Electric boiler, small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
41 Electric boiler, small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
41 Electric boiler, small | A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present m...
41 Electric boiler, small | A. The heat pump itself only represents a small part of the total investment. Depending on size the heat pump typically represents 0.2 MEUR per. MW heating (excluding drive energy).
41 Electric boiler, small | A. The investment and O&M costs are assessed in relation to an approx. operation in 500 hours/year.
41 Electric boiler, small | B. The installation at low voltage necessitates a transformer substation & expansion of the distribution board. Costs for these are included in the stated equipment costs.
41 Electric boiler, small | C. Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
41 Electric boiler, small | D. The installation costs include costs for electrical integration & grid connection fees.
41 Electric boiler, small | E. The forced outage of electric boilers is very limited and typically well below 1 %. The planned outage is typically limited to 1 day/year.
41 Electric boiler, small | F. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
41 Electric boiler, small | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
41 Electric boiler, small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
41 Electric boiler, small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
41 Electric boiler, small | H. Cold start of time is starting a heat pump where stand by heating has not been applied
41 Electric boiler, small | I. Operation at part load will usually increase COP but also variable O&M costs
41 Electric boiler, small | J. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
41 Electric boiler, small | K. Land is usually owned by the company
41 Electric boiler, small | L. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
41 Electric boiler, small | M. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
41 Electric boiler, small | N. 1/4 MWh-heat per MW is lost during startup
41 Electric boiler, small | O. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 5 % as compontents must be rated for higher pressure levels
41 Electric boiler, small | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
41 Electric boiler, small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
41 Electric boiler, small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
41 Electric boiler, small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
41 Electric boiler, small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
41 Electric boiler, small | F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflecte...
41 Electric boiler, small | G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
41 Electric boiler, small | H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added ...
41 Electric boiler, small | I. Not relevant for small and medium size plants.
41 Electric boiler, small | K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
41 Electric boiler, small | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
41 Electric boiler, small | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
41 Electric boiler, small | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
41 Electric boiler, small | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
41 Electric boiler, small | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
41 Electric boiler, small | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
41 Electric boiler, small | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
41 Electric boiler, small | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
41 Electric boiler, small | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
41 Electric boiler, small | T. The added tracker cost is based on interviews with Danish manufacturers.
41 Electric boiler, small | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
41 Electric boiler, small | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
41 Electric boiler, small | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
41 Electric boiler, small | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
41 Electric boiler, small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
41 Electric boiler, small | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
41 Electric boiler, large | A. The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
41 Electric boiler, large | B. The maintenance normally consists of 1 -2 annual service visits.
41 Electric boiler, large | C. An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
41 Electric boiler, large | D. Not considered relevant for small domestic turbines.
41 Electric boiler, large | E. Based on information from manufacturers and resellers. The
41 Electric boiler, large | F. The prices depends significantly on turbine size (5 kW - 6 MEUR/MW; 10 kW - 4 MEUR/MW ; 25 kW - 3 MEUR/MW)
41 Electric boiler, large | G. The service cost is assumed fixed to 100EUR/kW/y.
41 Electric boiler, large | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
41 Electric boiler, large | A. The investment and O&M costs are assessed in relation to an approx. operation in 500 hours/year.
41 Electric boiler, large | B. The installation at low voltage necessitates a transformer substation & expansion of the distribution board. Costs for these are included in the stated equipment costs.
41 Electric boiler, large | C. Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
41 Electric boiler, large | D. The installation costs include costs for electrical integration & grid connection fees.
41 Electric boiler, large | E. The forced outage of electric boilers is very limited and typically well below 1 %. The planned outage is typically limited to 1 day/year.
41 Electric boiler, large | F. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
41 Electric boiler, large | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
41 Electric boiler, large | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
41 Electric boiler, large | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
41 Electric boiler, large | B. 45 MW at 1 °C seawater, 64,5 at 4 °C seawater (the design temperature), and 68,4 MW at 14 °C seawater.
41 Electric boiler, large | C. Actual development within COP optimization and reduced investment cost depend on the development in fuel and electricity prices.
41 Electric boiler, large | D. Name plate efficiency is at 4 °C seawater temperature and DH temperatures are 70/33 °C. Total efficiency is in the range of 2,4 to 3,6 depending on the temperature of the seawater and DH. The plant is not in use in the summer period, otherwise, the efficiency could have been even higher.
41 Electric boiler, large | E. The primary auxililary electricity consumption is related to the seawater pumps.
41 Electric boiler, large | F. Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M.
41 Electric boiler, large | G. Tecnical lifetime is calculated with an outage time of 3 month per year.
41 Electric boiler, large | H. Does not include tendering and regulatory approvals.
41 Electric boiler, large | I. The development within construction time will depend on future production figures and standardization of plants.
41 Electric boiler, large | J. Note that this is only valid for upregulation (i.e. load increase of the heat pump). Downregulation (i.e. load reduction on the heat pump) is at a lower rate, however, this can be compesated by other units in the portfolio.
41 Electric boiler, large | K. CO2 heat pumps regulate a lot faster than e.g. ammonia. The regulation ability will depend on the future markets for regulation services.
41 Electric boiler, large | L. This is the continous minimum load with only 1 of 2 HP's enabled.
41 Electric boiler, large | M. All inputs are based on a single case, DIN Forsyning Heat Pump in Esbjerg.
41 Electric boiler, large | N. The warm start-up time is guaranteed to take 0,5 hours but it is, however, expected to take 0,2 hours.
41 Electric boiler, large | O. Cold start-up time includes starting a heat pump where stand by heating has not been applied.
41 Electric boiler, large | P. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M. DH distribution system is not included.
41 Electric boiler, large | Q. 1/4 MWh-heat per MW is lost during startup
41 Electric boiler, large | R. The forecast for future prices is an estimate since this is the first CO2 heat pump plant in this size.
41 Electric boiler, large | S. The CO2 heat pumps are made with magnetic barrings and are oilfree, therefore the O&M are lower compared to traditional heat pumps
41 Electric boiler, large | T. The price is also included in nominal investment (equipment)
41 Electric boiler, large | V. The heat pumps produce heating at a higher temperature compared to Name plate several months of the year therefore the Name plate COP is higher than the yearly COP.
41 Electric boiler, large | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
41 Electric boiler, large | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
41 Electric boiler, large | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
41 Electric boiler, large | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
41 Electric boiler, large | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
41 Electric boiler, large | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
41 Electric boiler, large | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
41 Electric boiler, large | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
41 Electric boiler, large | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
41 Electric boiler, large | T. The added tracker cost is based on interviews with Danish manufacturers.
41 Electric boiler, large | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
41 Electric boiler, large | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
41 Electric boiler, large | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
41 Electric boiler, large | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
41 Electric boiler, large | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
41 Electric boiler, large | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
44 Natural Gas DH Only | A. The cost presented provides an estimate for what capital cost and operating costs of wave power converters might be in the future assuming all R&D challenges have been overcome, that economics of scale have been realized and that efficiencies in production and operation due to the learning cur...
44 Natural Gas DH Only | B. Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
44 Natural Gas DH Only | C. Much dependent on plant size and location.
44 Natural Gas DH Only | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
44 Natural Gas DH Only | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
44 Natural Gas DH Only | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
44 Natural Gas DH Only | A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present m...
44 Natural Gas DH Only | A. Includes a condensing economizer, without economizer the efficiency will be up to some 93-97 %, LHV reference
44 Natural Gas DH Only | B. Includes a condensing economizer, without economizer the efficiency will be up to some 92-95 %, LHV reference
44 Natural Gas DH Only | C. Not Relevant for heat-only technologies
44 Natural Gas DH Only | D. Boilers with low water content (e.g. watertube instaed of shell tube 3-5 pass boilers) are used start up time from cold is shorter
44 Natural Gas DH Only | E. Boilers in the low power range approx. 0.010 and boilersin the higher power range 0.003
44 Natural Gas DH Only | F. DGC Estimate
44 Natural Gas DH Only | G. Ultra Low NOx burners can reach a level of 5 g/GJ
44 Natural Gas DH Only | H. Fuel dependent , not tecchnology dependent
44 Natural Gas DH Only | I. No data available
44 Natural Gas DH Only | J. The average numbers are for a 2- 3 MW boiler installation
44 Natural Gas DH Only | K. Technical lifetime often exceeds 25 years
44 Natural Gas DH Only | L. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
44 Natural Gas DH Only | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
44 Natural Gas DH Only | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
44 Natural Gas DH Only | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
44 Natural Gas DH Only | L. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
44 Natural Gas DH Only | M. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
44 Natural Gas DH Only | N. 1/4 MWh-heat per MW is lost during startup
44 Natural Gas DH Only | O. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 5 % as compontents must be rated for higher pressure levels
44 Natural Gas DH Only | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
44 Natural Gas DH Only | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
44 Natural Gas DH Only | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
44 Natural Gas DH Only | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
44 Natural Gas DH Only | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
44 Natural Gas DH Only | F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflecte...
44 Natural Gas DH Only | G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
44 Natural Gas DH Only | H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added ...
44 Natural Gas DH Only | I. Not relevant for small and medium size plants.
44 Natural Gas DH Only | K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
44 Natural Gas DH Only | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
44 Natural Gas DH Only | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
44 Natural Gas DH Only | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
44 Natural Gas DH Only | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
44 Natural Gas DH Only | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
44 Natural Gas DH Only | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
44 Natural Gas DH Only | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
44 Natural Gas DH Only | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
44 Natural Gas DH Only | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
44 Natural Gas DH Only | T. The added tracker cost is based on interviews with Danish manufacturers.
44 Natural Gas DH Only | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
44 Natural Gas DH Only | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
44 Natural Gas DH Only | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
44 Natural Gas DH Only | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
44 Natural Gas DH Only | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
44 Natural Gas DH Only | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.1.a Geothermal DH, 1200m, E | A. The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
45.1.a Geothermal DH, 1200m, E | B. The maintenance normally consists of 1 -2 annual service visits.
45.1.a Geothermal DH, 1200m, E | C. An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
45.1.a Geothermal DH, 1200m, E | D. Not considered relevant for small domestic turbines.
45.1.a Geothermal DH, 1200m, E | E. Based on information from manufacturers and resellers. The
45.1.a Geothermal DH, 1200m, E | F. The prices depends significantly on turbine size (5 kW - 6 MEUR/MW; 10 kW - 4 MEUR/MW ; 25 kW - 3 MEUR/MW)
45.1.a Geothermal DH, 1200m, E | G. The service cost is assumed fixed to 100EUR/kW/y.
45.1.a Geothermal DH, 1200m, E | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
45.1.a Geothermal DH, 1200m, E | A. The investment and O&M costs are assessed in relation to an approx. operation in 500 hours/year.
45.1.a Geothermal DH, 1200m, E | B. The installation at low voltage necessitates a transformer substation & expansion of the distribution board. Costs for these are included in the stated equipment costs.
45.1.a Geothermal DH, 1200m, E | C. Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
45.1.a Geothermal DH, 1200m, E | D. The installation costs include costs for electrical integration & grid connection fees.
45.1.a Geothermal DH, 1200m, E | E. The forced outage of electric boilers is very limited and typically well below 1 %. The planned outage is typically limited to 1 day/year.
45.1.a Geothermal DH, 1200m, E | A. No part of the geothermal heat is transferred directly to DH water, all is used as source for the heat pump\nHeat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as per Ch. 40.
45.1.a Geothermal DH, 1200m, E | B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. \nLower / upper case considers variations.
45.1.a Geothermal DH, 1200m, E | C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, \nand geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 1800 EUR/m is assumed.
45.1.a Geothermal DH, 1200m, E | D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection \nwells a horizontal offset in the range of 1-2 km for the injection wells is necessary
45.1.a Geothermal DH, 1200m, E | E. Replacement of submersible pump(s), approx. once every five years, operation staff. \nHeat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
45.1.a Geothermal DH, 1200m, E | F. Include maintenance of filters and wells (chemical treatment)
45.1.a Geothermal DH, 1200m, E | G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity \nto pumps etc.
45.1.a Geothermal DH, 1200m, E | H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in \nconnection with a heat storage.
45.1.a Geothermal DH, 1200m, E | I. Uncertainty does not consider the risk of not finding a suitable reservoir.
45.1.a Geothermal DH, 1200m, E | J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
45.1.a Geothermal DH, 1200m, E | K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
45.1.a Geothermal DH, 1200m, E | L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
45.1.a Geothermal DH, 1200m, E | M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
45.1.a Geothermal DH, 1200m, E | N. Temperature of geothermal heat is 44/17 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
45.1.a Geothermal DH, 1200m, E | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.1.a Geothermal DH, 1200m, E | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.1.a Geothermal DH, 1200m, E | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.1.a Geothermal DH, 1200m, E | P. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M. DH distribution system is not included.
45.1.a Geothermal DH, 1200m, E | Q. 1/4 MWh-heat per MW is lost during startup
45.1.a Geothermal DH, 1200m, E | R. The forecast for future prices is an estimate since this is the first CO2 heat pump plant in this size.
45.1.a Geothermal DH, 1200m, E | S. The CO2 heat pumps are made with magnetic barrings and are oilfree, therefore the O&M are lower compared to traditional heat pumps
45.1.a Geothermal DH, 1200m, E | T. The price is also included in nominal investment (equipment)
45.1.a Geothermal DH, 1200m, E | V. The heat pumps produce heating at a higher temperature compared to Name plate several months of the year therefore the Name plate COP is higher than the yearly COP.
45.1.a Geothermal DH, 1200m, E | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.1.a Geothermal DH, 1200m, E | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.1.a Geothermal DH, 1200m, E | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.1.a Geothermal DH, 1200m, E | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
45.1.a Geothermal DH, 1200m, E | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
45.1.a Geothermal DH, 1200m, E | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
45.1.a Geothermal DH, 1200m, E | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
45.1.a Geothermal DH, 1200m, E | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
45.1.a Geothermal DH, 1200m, E | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
45.1.a Geothermal DH, 1200m, E | T. The added tracker cost is based on interviews with Danish manufacturers.
45.1.a Geothermal DH, 1200m, E | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
45.1.a Geothermal DH, 1200m, E | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
45.1.a Geothermal DH, 1200m, E | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
45.1.a Geothermal DH, 1200m, E | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.1.a Geothermal DH, 1200m, E | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.1.a Geothermal DH, 1200m, E | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.1.b Geothermal DH, 2000m, E | A. The cost presented provides an estimate for what capital cost and operating costs of wave power converters might be in the future assuming all R&D challenges have been overcome, that economics of scale have been realized and that efficiencies in production and operation due to the learning cur...
45.1.b Geothermal DH, 2000m, E | B. Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
45.1.b Geothermal DH, 2000m, E | C. Much dependent on plant size and location.
45.1.b Geothermal DH, 2000m, E | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.1.b Geothermal DH, 2000m, E | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.1.b Geothermal DH, 2000m, E | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.1.b Geothermal DH, 2000m, E | A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present m...
45.1.b Geothermal DH, 2000m, E | A. Includes a condensing economizer, without economizer the efficiency will be up to some 93-97 %, LHV reference
45.1.b Geothermal DH, 2000m, E | B. Includes a condensing economizer, without economizer the efficiency will be up to some 92-95 %, LHV reference
45.1.b Geothermal DH, 2000m, E | C. Not Relevant for heat-only technologies
45.1.b Geothermal DH, 2000m, E | D. Boilers with low water content (e.g. watertube instaed of shell tube 3-5 pass boilers) are used start up time from cold is shorter
45.1.b Geothermal DH, 2000m, E | E. Boilers in the low power range approx. 0.010 and boilersin the higher power range 0.003
45.1.b Geothermal DH, 2000m, E | F. DGC Estimate
45.1.b Geothermal DH, 2000m, E | G. Ultra Low NOx burners can reach a level of 5 g/GJ
45.1.b Geothermal DH, 2000m, E | A. Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 68% of geothermal heat can be exchanged directly, leaving 32 as heat source for the heat pump. \nHeat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as p...
45.1.b Geothermal DH, 2000m, E | B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. \nLower / upper case considers variations.
45.1.b Geothermal DH, 2000m, E | C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, \nand geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 2000 EUR/m is assumed.
45.1.b Geothermal DH, 2000m, E | D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection \nwells a horizontal offset in the range of 1-2 km for the injection wells is necessary
45.1.b Geothermal DH, 2000m, E | E. Replacement of submersible pump(s), approx. once every five years, operation staff. \nHeat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
45.1.b Geothermal DH, 2000m, E | F. Include maintenance of filters and wells (chemical treatment)
45.1.b Geothermal DH, 2000m, E | G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity \nto pumps etc.
45.1.b Geothermal DH, 2000m, E | H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in \nconnection with a heat storage.
45.1.b Geothermal DH, 2000m, E | I. Uncertainty does not consider the risk of not finding a suitable reservoir.
45.1.b Geothermal DH, 2000m, E | J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
45.1.b Geothermal DH, 2000m, E | K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
45.1.b Geothermal DH, 2000m, E | L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
45.1.b Geothermal DH, 2000m, E | M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
45.1.b Geothermal DH, 2000m, E | N. Temperature of geothermal heat is 68/33 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
45.1.b Geothermal DH, 2000m, E | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.1.b Geothermal DH, 2000m, E | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.1.b Geothermal DH, 2000m, E | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.1.b Geothermal DH, 2000m, E | G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
45.1.b Geothermal DH, 2000m, E | H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added ...
45.1.b Geothermal DH, 2000m, E | I. Not relevant for small and medium size plants.
45.1.b Geothermal DH, 2000m, E | K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
45.1.b Geothermal DH, 2000m, E | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
45.1.b Geothermal DH, 2000m, E | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
45.1.b Geothermal DH, 2000m, E | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
45.1.b Geothermal DH, 2000m, E | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
45.1.b Geothermal DH, 2000m, E | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
45.1.b Geothermal DH, 2000m, E | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
45.1.b Geothermal DH, 2000m, E | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
45.1.b Geothermal DH, 2000m, E | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
45.1.b Geothermal DH, 2000m, E | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
45.1.b Geothermal DH, 2000m, E | T. The added tracker cost is based on interviews with Danish manufacturers.
45.1.b Geothermal DH, 2000m, E | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
45.1.b Geothermal DH, 2000m, E | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
45.1.b Geothermal DH, 2000m, E | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
45.1.b Geothermal DH, 2000m, E | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.1.b Geothermal DH, 2000m, E | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.1.b Geothermal DH, 2000m, E | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.2.a Geothermal DH, 1200m, A | A. The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
45.2.a Geothermal DH, 1200m, A | B. The maintenance normally consists of 1 -2 annual service visits.
45.2.a Geothermal DH, 1200m, A | C. An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
45.2.a Geothermal DH, 1200m, A | D. Not considered relevant for small domestic turbines.
45.2.a Geothermal DH, 1200m, A | E. Based on information from manufacturers and resellers. The
45.2.a Geothermal DH, 1200m, A | F. The prices depends significantly on turbine size (5 kW - 6 MEUR/MW; 10 kW - 4 MEUR/MW ; 25 kW - 3 MEUR/MW)
45.2.a Geothermal DH, 1200m, A | G. The service cost is assumed fixed to 100EUR/kW/y.
45.2.a Geothermal DH, 1200m, A | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
45.2.a Geothermal DH, 1200m, A | A. The investment and O&M costs are assessed in relation to an approx. operation in 500 hours/year.
45.2.a Geothermal DH, 1200m, A | B. The installation at low voltage necessitates a transformer substation & expansion of the distribution board. Costs for these are included in the stated equipment costs.
45.2.a Geothermal DH, 1200m, A | C. Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
45.2.a Geothermal DH, 1200m, A | D. The installation costs include costs for electrical integration & grid connection fees.
45.2.a Geothermal DH, 1200m, A | E. The forced outage of electric boilers is very limited and typically well below 1 %. The planned outage is typically limited to 1 day/year.
45.2.a Geothermal DH, 1200m, A | A. No part of the geothermal heat is transferred directly to DH water. 100% heat source for the heat pump. \nHeat pump according to Ch. 40.
45.2.a Geothermal DH, 1200m, A | B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. \nLower / upper case considers variations.
45.2.a Geothermal DH, 1200m, A | C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, \nand geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 1800 EUR/m is assumed.
45.2.a Geothermal DH, 1200m, A | D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection \nwells a horizontal offset in the range of 1-2 km for the injection wells is necessary
45.2.a Geothermal DH, 1200m, A | E. Replacement of submersible pump(s), approx. once every five years, operation staff. \nHeat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
45.2.a Geothermal DH, 1200m, A | F. Include maintenance of filters and wells (chemical treatment)
45.2.a Geothermal DH, 1200m, A | G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity \nto pumps etc.
45.2.a Geothermal DH, 1200m, A | H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in \nconnection with a heat storage.
45.2.a Geothermal DH, 1200m, A | I. Uncertainty does not consider the risk of not finding a suitable reservoir.
45.2.a Geothermal DH, 1200m, A | J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
45.2.a Geothermal DH, 1200m, A | K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
45.2.a Geothermal DH, 1200m, A | L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
45.2.a Geothermal DH, 1200m, A | M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
45.2.a Geothermal DH, 1200m, A | N. Temperature of geothermal heat is 44/17 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
45.2.a Geothermal DH, 1200m, A | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.2.a Geothermal DH, 1200m, A | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.2.a Geothermal DH, 1200m, A | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.2.a Geothermal DH, 1200m, A | P. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M. DH distribution system is not included.
45.2.a Geothermal DH, 1200m, A | Q. 1/4 MWh-heat per MW is lost during startup
45.2.a Geothermal DH, 1200m, A | R. The forecast for future prices is an estimate since this is the first CO2 heat pump plant in this size.
45.2.a Geothermal DH, 1200m, A | S. The CO2 heat pumps are made with magnetic barrings and are oilfree, therefore the O&M are lower compared to traditional heat pumps
45.2.a Geothermal DH, 1200m, A | T. The price is also included in nominal investment (equipment)
45.2.a Geothermal DH, 1200m, A | V. The heat pumps produce heating at a higher temperature compared to Name plate several months of the year therefore the Name plate COP is higher than the yearly COP.
45.2.a Geothermal DH, 1200m, A | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.2.a Geothermal DH, 1200m, A | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.2.a Geothermal DH, 1200m, A | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.2.a Geothermal DH, 1200m, A | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
45.2.a Geothermal DH, 1200m, A | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
45.2.a Geothermal DH, 1200m, A | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
45.2.a Geothermal DH, 1200m, A | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
45.2.a Geothermal DH, 1200m, A | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
45.2.a Geothermal DH, 1200m, A | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
45.2.a Geothermal DH, 1200m, A | T. The added tracker cost is based on interviews with Danish manufacturers.
45.2.a Geothermal DH, 1200m, A | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
45.2.a Geothermal DH, 1200m, A | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
45.2.a Geothermal DH, 1200m, A | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
45.2.a Geothermal DH, 1200m, A | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.2.a Geothermal DH, 1200m, A | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.2.a Geothermal DH, 1200m, A | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.2.b Geothermal DH, 2000m, A | A. The cost presented provides an estimate for what capital cost and operating costs of wave power converters might be in the future assuming all R&D challenges have been overcome, that economics of scale have been realized and that efficiencies in production and operation due to the learning cur...
45.2.b Geothermal DH, 2000m, A | B. Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
45.2.b Geothermal DH, 2000m, A | C. Much dependent on plant size and location.
45.2.b Geothermal DH, 2000m, A | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.2.b Geothermal DH, 2000m, A | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.2.b Geothermal DH, 2000m, A | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.2.b Geothermal DH, 2000m, A | A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present m...
45.2.b Geothermal DH, 2000m, A | A. Includes a condensing economizer, without economizer the efficiency will be up to some 93-97 %, LHV reference
45.2.b Geothermal DH, 2000m, A | B. Includes a condensing economizer, without economizer the efficiency will be up to some 92-95 %, LHV reference
45.2.b Geothermal DH, 2000m, A | C. Not Relevant for heat-only technologies
45.2.b Geothermal DH, 2000m, A | D. Boilers with low water content (e.g. watertube instaed of shell tube 3-5 pass boilers) are used start up time from cold is shorter
45.2.b Geothermal DH, 2000m, A | E. Boilers in the low power range approx. 0.010 and boilersin the higher power range 0.003
45.2.b Geothermal DH, 2000m, A | F. DGC Estimate
45.2.b Geothermal DH, 2000m, A | G. Ultra Low NOx burners can reach a level of 5 g/GJ
45.2.b Geothermal DH, 2000m, A | A. Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 68% of geothermal heat can be exchanged directly, leaving 32 as heat source for the heat pump. Heat pump according to Ch. 40.
45.2.b Geothermal DH, 2000m, A | B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. \nLower / upper case considers variations.
45.2.b Geothermal DH, 2000m, A | C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, \nand geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 1900 EUR/m is assumed.
45.2.b Geothermal DH, 2000m, A | D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection \nwells a horizontal offset in the range of 1-2 km for the injection wells is necessary
45.2.b Geothermal DH, 2000m, A | E. Replacement of submersible pump(s), approx. once every five years, operation staff. \nHeat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
45.2.b Geothermal DH, 2000m, A | F. Include maintenance of filters and wells (chemical treatment)
45.2.b Geothermal DH, 2000m, A | G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity \nto pumps etc.
45.2.b Geothermal DH, 2000m, A | H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in \nconnection with a heat storage.
45.2.b Geothermal DH, 2000m, A | I. Uncertainty does not consider the risk of not finding a suitable reservoir.
45.2.b Geothermal DH, 2000m, A | J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
45.2.b Geothermal DH, 2000m, A | K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
45.2.b Geothermal DH, 2000m, A | L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
45.2.b Geothermal DH, 2000m, A | M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
45.2.b Geothermal DH, 2000m, A | N. Temperature of geothermal heat is 68/33 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
45.2.b Geothermal DH, 2000m, A | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.2.b Geothermal DH, 2000m, A | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.2.b Geothermal DH, 2000m, A | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.2.b Geothermal DH, 2000m, A | G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
45.2.b Geothermal DH, 2000m, A | H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added ...
45.2.b Geothermal DH, 2000m, A | I. Not relevant for small and medium size plants.
45.2.b Geothermal DH, 2000m, A | K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
45.2.b Geothermal DH, 2000m, A | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
45.2.b Geothermal DH, 2000m, A | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
45.2.b Geothermal DH, 2000m, A | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
45.2.b Geothermal DH, 2000m, A | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
45.2.b Geothermal DH, 2000m, A | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
45.2.b Geothermal DH, 2000m, A | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
45.2.b Geothermal DH, 2000m, A | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
45.2.b Geothermal DH, 2000m, A | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
45.2.b Geothermal DH, 2000m, A | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
45.2.b Geothermal DH, 2000m, A | T. The added tracker cost is based on interviews with Danish manufacturers.
45.2.b Geothermal DH, 2000m, A | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
45.2.b Geothermal DH, 2000m, A | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
45.2.b Geothermal DH, 2000m, A | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
45.2.b Geothermal DH, 2000m, A | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.2.b Geothermal DH, 2000m, A | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.2.b Geothermal DH, 2000m, A | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.3.a Geoth. DH, 1200m, E (LT) | A. The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
45.3.a Geoth. DH, 1200m, E (LT) | B. The maintenance normally consists of 1 -2 annual service visits.
45.3.a Geoth. DH, 1200m, E (LT) | C. An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
45.3.a Geoth. DH, 1200m, E (LT) | D. Not considered relevant for small domestic turbines.
45.3.a Geoth. DH, 1200m, E (LT) | E. Based on information from manufacturers and resellers. The
45.3.a Geoth. DH, 1200m, E (LT) | F. The prices depends significantly on turbine size (5 kW - 6 MEUR/MW; 10 kW - 4 MEUR/MW ; 25 kW - 3 MEUR/MW)
45.3.a Geoth. DH, 1200m, E (LT) | G. The service cost is assumed fixed to 100EUR/kW/y.
45.3.a Geoth. DH, 1200m, E (LT) | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
45.3.a Geoth. DH, 1200m, E (LT) | A. The investment and O&M costs are assessed in relation to an approx. operation in 500 hours/year.
45.3.a Geoth. DH, 1200m, E (LT) | B. The installation at low voltage necessitates a transformer substation & expansion of the distribution board. Costs for these are included in the stated equipment costs.
45.3.a Geoth. DH, 1200m, E (LT) | C. Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
45.3.a Geoth. DH, 1200m, E (LT) | D. The installation costs include costs for electrical integration & grid connection fees.
45.3.a Geoth. DH, 1200m, E (LT) | E. The forced outage of electric boilers is very limited and typically well below 1 %. The planned outage is typically limited to 1 day/year.
45.3.a Geoth. DH, 1200m, E (LT) | A. Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 19% of geothermal heat can be exchanged directly, leaving 79 as heat source for the heat pump. \nHeat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as p...
45.3.a Geoth. DH, 1200m, E (LT) | B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
45.3.a Geoth. DH, 1200m, E (LT) | C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 1900 EUR/m is assumed.
45.3.a Geoth. DH, 1200m, E (LT) | D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
45.3.a Geoth. DH, 1200m, E (LT) | E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
45.3.a Geoth. DH, 1200m, E (LT) | F. Include maintenance of filters and wells (chemical treatment)
45.3.a Geoth. DH, 1200m, E (LT) | G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
45.3.a Geoth. DH, 1200m, E (LT) | H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage
45.3.a Geoth. DH, 1200m, E (LT) | I. Uncertainty does not consider the risk of not finding a suitable reservoir.
45.3.a Geoth. DH, 1200m, E (LT) | J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
45.3.a Geoth. DH, 1200m, E (LT) | K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
45.3.a Geoth. DH, 1200m, E (LT) | L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
45.3.a Geoth. DH, 1200m, E (LT) | M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
45.3.a Geoth. DH, 1200m, E (LT) | N. Temperature of geothermal heat is 44/17 (°C source/return). Temperature of DH water is 70/35 (°C source/return)
45.3.a Geoth. DH, 1200m, E (LT) | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.3.a Geoth. DH, 1200m, E (LT) | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.3.a Geoth. DH, 1200m, E (LT) | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.3.a Geoth. DH, 1200m, E (LT) | P. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M. DH distribution system is not included.
45.3.a Geoth. DH, 1200m, E (LT) | Q. 1/4 MWh-heat per MW is lost during startup
45.3.a Geoth. DH, 1200m, E (LT) | R. The forecast for future prices is an estimate since this is the first CO2 heat pump plant in this size.
45.3.a Geoth. DH, 1200m, E (LT) | S. The CO2 heat pumps are made with magnetic barrings and are oilfree, therefore the O&M are lower compared to traditional heat pumps
45.3.a Geoth. DH, 1200m, E (LT) | T. The price is also included in nominal investment (equipment)
45.3.a Geoth. DH, 1200m, E (LT) | V. The heat pumps produce heating at a higher temperature compared to Name plate several months of the year therefore the Name plate COP is higher than the yearly COP.
45.3.a Geoth. DH, 1200m, E (LT) | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.3.a Geoth. DH, 1200m, E (LT) | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.3.a Geoth. DH, 1200m, E (LT) | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.3.a Geoth. DH, 1200m, E (LT) | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
45.3.a Geoth. DH, 1200m, E (LT) | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
45.3.a Geoth. DH, 1200m, E (LT) | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
45.3.a Geoth. DH, 1200m, E (LT) | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
45.3.a Geoth. DH, 1200m, E (LT) | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
45.3.a Geoth. DH, 1200m, E (LT) | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
45.3.a Geoth. DH, 1200m, E (LT) | T. The added tracker cost is based on interviews with Danish manufacturers.
45.3.a Geoth. DH, 1200m, E (LT) | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
45.3.a Geoth. DH, 1200m, E (LT) | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
45.3.a Geoth. DH, 1200m, E (LT) | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
45.3.a Geoth. DH, 1200m, E (LT) | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.3.a Geoth. DH, 1200m, E (LT) | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.3.a Geoth. DH, 1200m, E (LT) | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.3.b Geoth DH, 2000m, E (LT) | A. The cost presented provides an estimate for what capital cost and operating costs of wave power converters might be in the future assuming all R&D challenges have been overcome, that economics of scale have been realized and that efficiencies in production and operation due to the learning cur...
45.3.b Geoth DH, 2000m, E (LT) | B. Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
45.3.b Geoth DH, 2000m, E (LT) | C. Much dependent on plant size and location.
45.3.b Geoth DH, 2000m, E (LT) | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.3.b Geoth DH, 2000m, E (LT) | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.3.b Geoth DH, 2000m, E (LT) | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.3.b Geoth DH, 2000m, E (LT) | A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present m...
45.3.b Geoth DH, 2000m, E (LT) | A. Includes a condensing economizer, without economizer the efficiency will be up to some 93-97 %, LHV reference
45.3.b Geoth DH, 2000m, E (LT) | B. Includes a condensing economizer, without economizer the efficiency will be up to some 92-95 %, LHV reference
45.3.b Geoth DH, 2000m, E (LT) | C. Not Relevant for heat-only technologies
45.3.b Geoth DH, 2000m, E (LT) | D. Boilers with low water content (e.g. watertube instaed of shell tube 3-5 pass boilers) are used start up time from cold is shorter
45.3.b Geoth DH, 2000m, E (LT) | E. Boilers in the low power range approx. 0.010 and boilersin the higher power range 0.003
45.3.b Geoth DH, 2000m, E (LT) | F. DGC Estimate
45.3.b Geoth DH, 2000m, E (LT) | G. Ultra Low NOx burners can reach a level of 5 g/GJ
45.3.b Geoth DH, 2000m, E (LT) | A. Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 83% of geothermal heat can be exchanged directly, leaving 17 as heat source for the heat pump. \nHeat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as p...
45.3.b Geoth DH, 2000m, E (LT) | B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. \nLower / upper case considers variations.
45.3.b Geoth DH, 2000m, E (LT) | C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and \ngeological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 1900 EUR/m is assumed.
45.3.b Geoth DH, 2000m, E (LT) | D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary.
45.3.b Geoth DH, 2000m, E (LT) | E. Replacement of submersible pump(s), approx. once every five years, operation staff. \nHeat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
45.3.b Geoth DH, 2000m, E (LT) | F. Include maintenance of filters and wells (chemical treatment)
45.3.b Geoth DH, 2000m, E (LT) | G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
45.3.b Geoth DH, 2000m, E (LT) | H. A geothermal plant is intended for continuous operation. \nElectric heat pumps may provide some of regulation though, e.g. in connection with a heat storage
45.3.b Geoth DH, 2000m, E (LT) | I. Uncertainty does not consider the risk of not finding a suitable reservoir.
45.3.b Geoth DH, 2000m, E (LT) | J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
45.3.b Geoth DH, 2000m, E (LT) | K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
45.3.b Geoth DH, 2000m, E (LT) | L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
45.3.b Geoth DH, 2000m, E (LT) | M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
45.3.b Geoth DH, 2000m, E (LT) | N. Temperature of geothermal heat is 80/40 (°C source/return). Temperature of DH water is 70/35 (°C source/return)
45.3.b Geoth DH, 2000m, E (LT) | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.3.b Geoth DH, 2000m, E (LT) | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.3.b Geoth DH, 2000m, E (LT) | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.3.b Geoth DH, 2000m, E (LT) | G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
45.3.b Geoth DH, 2000m, E (LT) | H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added ...
45.3.b Geoth DH, 2000m, E (LT) | I. Not relevant for small and medium size plants.
45.3.b Geoth DH, 2000m, E (LT) | K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
45.3.b Geoth DH, 2000m, E (LT) | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
45.3.b Geoth DH, 2000m, E (LT) | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
45.3.b Geoth DH, 2000m, E (LT) | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
45.3.b Geoth DH, 2000m, E (LT) | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
45.3.b Geoth DH, 2000m, E (LT) | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
45.3.b Geoth DH, 2000m, E (LT) | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
45.3.b Geoth DH, 2000m, E (LT) | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
45.3.b Geoth DH, 2000m, E (LT) | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
45.3.b Geoth DH, 2000m, E (LT) | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
45.3.b Geoth DH, 2000m, E (LT) | T. The added tracker cost is based on interviews with Danish manufacturers.
45.3.b Geoth DH, 2000m, E (LT) | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
45.3.b Geoth DH, 2000m, E (LT) | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
45.3.b Geoth DH, 2000m, E (LT) | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
45.3.b Geoth DH, 2000m, E (LT) | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.3.b Geoth DH, 2000m, E (LT) | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.3.b Geoth DH, 2000m, E (LT) | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.4 Geothermal DH, E lar scale | A. The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
45.4 Geothermal DH, E lar scale | B. The maintenance normally consists of 1 -2 annual service visits.
45.4 Geothermal DH, E lar scale | C. An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
45.4 Geothermal DH, E lar scale | D. Not considered relevant for small domestic turbines.
45.4 Geothermal DH, E lar scale | E. Based on information from manufacturers and resellers. The
45.4 Geothermal DH, E lar scale | F. The prices depends significantly on turbine size (5 kW - 6 MEUR/MW; 10 kW - 4 MEUR/MW ; 25 kW - 3 MEUR/MW)
45.4 Geothermal DH, E lar scale | G. The service cost is assumed fixed to 100EUR/kW/y.
45.4 Geothermal DH, E lar scale | A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
45.4 Geothermal DH, E lar scale | A. The investment and O&M costs are assessed in relation to an approx. operation in 500 hours/year.
45.4 Geothermal DH, E lar scale | B. The installation at low voltage necessitates a transformer substation & expansion of the distribution board. Costs for these are included in the stated equipment costs.
45.4 Geothermal DH, E lar scale | C. Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
45.4 Geothermal DH, E lar scale | D. The installation costs include costs for electrical integration & grid connection fees.
45.4 Geothermal DH, E lar scale | E. The forced outage of electric boilers is very limited and typically well below 1 %. The planned outage is typically limited to 1 day/year.
45.4 Geothermal DH, E lar scale | A. Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 19% of geothermal heat can be exchanged directly, leaving 79 as heat source for the heat pump. \nHeat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as p...
45.4 Geothermal DH, E lar scale | B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
45.4 Geothermal DH, E lar scale | A. Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump. 44% of geothermal heat can be exchanged directly, leaving 56% as heat source for the heat pump. \nHeat pump COP based on specific case according to [2]. Improved COP as per Ch. 40.
45.4 Geothermal DH, E lar scale | B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
45.4 Geothermal DH, E lar scale | C. Based on large scale effects. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey etc.\nand geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 2000 EUR/m is assumed.
45.4 Geothermal DH, E lar scale | D. The requirement is per facility. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection \nwells a horizontal offset in the range of 1-2 km for the injection wells is necessary
45.4 Geothermal DH, E lar scale | E. Replacement of submersible pump(s), approx. once every five years, operation staff. \nHeat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
45.4 Geothermal DH, E lar scale | F. Including maintenance of filters and wells (chemical treatment). Does not include drilling of replacement wells.
45.4 Geothermal DH, E lar scale | G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
45.4 Geothermal DH, E lar scale | H. A geothermal plant is intended for continuous operation. Electrical heat pumps may provide some of the regulation though, e.g. in connection with an energy storage to allow for use of the heating when required.
45.4 Geothermal DH, E lar scale | I. Uncertainty does not consider the risk of not finding a suitable reservoir.
45.4 Geothermal DH, E lar scale | J. Heat pump nominal investment costs including installation and integration with geothermal plant, excl. Building integration, electrical supply and district heating connection
45.4 Geothermal DH, E lar scale | K. The basis of the specific investment is the heat generation capacity for one unit including heat pumps but excluding ABEX.
45.4 Geothermal DH, E lar scale | L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
45.4 Geothermal DH, E lar scale | M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
45.4 Geothermal DH, E lar scale | N. Temperature of geothermal heat is 65/10 (°C source/return). Temperature of DH water is (°C source/return) 90/45 (500 h), 85/40 (1500 h) and 80/40 (rest of estimated hours)
45.4 Geothermal DH, E lar scale | O. Abandonment Cost (ABEX) accounts for approx. 7,5 % of total nominal investment [2]
45.4 Geothermal DH, E lar scale | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.4 Geothermal DH, E lar scale | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.4 Geothermal DH, E lar scale | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.4 Geothermal DH, E lar scale | T. The price is also included in nominal investment (equipment)
45.4 Geothermal DH, E lar scale | V. The heat pumps produce heating at a higher temperature compared to Name plate several months of the year therefore the Name plate COP is higher than the yearly COP.
45.4 Geothermal DH, E lar scale | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.4 Geothermal DH, E lar scale | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.4 Geothermal DH, E lar scale | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.4 Geothermal DH, E lar scale | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
45.4 Geothermal DH, E lar scale | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
45.4 Geothermal DH, E lar scale | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
45.4 Geothermal DH, E lar scale | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
45.4 Geothermal DH, E lar scale | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
45.4 Geothermal DH, E lar scale | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
45.4 Geothermal DH, E lar scale | T. The added tracker cost is based on interviews with Danish manufacturers.
45.4 Geothermal DH, E lar scale | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
45.4 Geothermal DH, E lar scale | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
45.4 Geothermal DH, E lar scale | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
45.4 Geothermal DH, E lar scale | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
45.4 Geothermal DH, E lar scale | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
45.4 Geothermal DH, E lar scale | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
46 Solar District Heating | A. The cost presented provides an estimate for what capital cost and operating costs of wave power converters might be in the future assuming all R&D challenges have been overcome, that economics of scale have been realized and that efficiencies in production and operation due to the learning cur...
46 Solar District Heating | B. Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
46 Solar District Heating | C. Much dependent on plant size and location.
46 Solar District Heating | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
46 Solar District Heating | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
46 Solar District Heating | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
46 Solar District Heating | A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present m...
46 Solar District Heating | A. Includes a condensing economizer, without economizer the efficiency will be up to some 93-97 %, LHV reference
46 Solar District Heating | B. Includes a condensing economizer, without economizer the efficiency will be up to some 92-95 %, LHV reference
46 Solar District Heating | C. Not Relevant for heat-only technologies
46 Solar District Heating | D. Boilers with low water content (e.g. watertube instaed of shell tube 3-5 pass boilers) are used start up time from cold is shorter
46 Solar District Heating | E. Boilers in the low power range approx. 0.010 and boilersin the higher power range 0.003
46 Solar District Heating | F. DGC Estimate
46 Solar District Heating | A. The yield is weather dependent and very site-specific, depending much on the temperatures of the district heating network. The quoted yield the average measured output from 40 Danish solar heating plants for 2015.
46 Solar District Heating | B. Estimate is 0,2 EUR/MWh heat output in 2015, excluding electricity consumption.
46 Solar District Heating | C. Applying the formula 250,000 EUR + 167 EUR/m2 solar panel collector for plants <50.000m2, cf. figures from Note G.
46 Solar District Heating | D. Including a diurnal storage is mandatory, 0.2 m3/m2 being a typical average storage size.\nThis figure can vary, dependent on the local conditions and desired solar fraction.
46 Solar District Heating | E. Can be combined with seasonal storage, cf. corresponding chapter.
46 Solar District Heating | F. Solar thermal plants can be regulated by varying the flow of the heat transfer fluid. The regulation ability is limited by the available heat demand in the heat sink (incl. available storage capacity) and solar radiation.
46 Solar District Heating | G. Prices of different plant sizes (Ref. 1): \n{"5000":{"Price pr. m2 [eur\/m2]":216.0,"Total price [M-eur]":1.08},"10000":{"Price pr. m2 [eur\/m2]":193.33,"Total price [M-eur]":1.93},"20000":{"Price pr. m2 [eur\/m2]":180.0,"Total price [M-eur]":3.6},"50000":{"Price pr. m2 [eur\/m2]":174.67,"Tota...
46 Solar District Heating | H. Prices include leveling of ground, laying of district heating pipelines in the ground inkl. 50 m of transmission pipeline to the district heating plant, heat exchanger connected to solar panel field and installed with collection tank and expansion with flanges to secondary side, control and el...
46 Solar District Heating | I. The lifetime is minimum 25-30 years, proven in actual plants still in operation. Critical component is the teflon foil, not the material itself, but the application method. The pipes have been improved, designed for the relatively large number of temperature variations, compared to normal dist...
46 Solar District Heating | J. Space requirement is approximately 3 m2 for each m2 gross collector area. No development of this parameter is expected, since the main reason is to avoid the shadow effect. Minor optimization of the sides of the panels may be obtained, increasing the ratio of aperture/gross area. Other types o...
46 Solar District Heating | K. The forced outage is very small, therefore in practice close to 0 %. The modular construction makes it possible to maintain sections of the panels. Outage of critical components such as the heat exchanger is very limited.
46 Solar District Heating | L. The average plant size increases, but with large variations since both small plants and increasingly larger plants are installed. A 5 % annual increase of the average size is assumed. The plant size is rather dependent on the heat demand in the district heating grid, it is connected to. The co...
46 Solar District Heating | M. Estimate of cost of tank storage (diurnal storage) is 135 EUR/m3. The required size of the storage differs, but a typical size is 0.1-0.3 m3 storage for each m2 of solar panels, hence a 10,000 m2 solar thermal plant requires 1-3,000 m3 of diurnal storage.
46 Solar District Heating | N. Considering a reduction in prices for 2020 / 2020-2030 / 2030-2050 of 0.6 / 0.4 / 0.3 % p.a.
46 Solar District Heating | O. The division of cost elements is site- and plant specific. An indicative distribution of costs are; Solar collectors and piping (48%), heat exchanger, pumps etc. (8%), accumulation tank (11%), transmission pipeline (13%), building (2%), control, operation and startup (5%), land purchase, groun...
46 Solar District Heating | P. Please refer to www.solvarmedata.dk for display of efficiencies of Danish solar district heating plants. Chose a plant, select "Production and efficiency" and a chart will display the efficiency - typically varying between 20 and 50%.
46 Solar District Heating | Q. The solar radiation on the horizontal surface.
46 Solar District Heating | R. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
46 Solar District Heating | S. The cost per output power is converted from cost per collector area via formula: Power/Area = 0.7 kWth/m2. Note this is an approximation, original figures are stated per area or MWh
46 Solar District Heating | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
46 Solar District Heating | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
46 Solar District Heating | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
46 Solar District Heating | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
46 Solar District Heating | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
46 Solar District Heating | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
46 Solar District Heating | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
46 Solar District Heating | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
46 Solar District Heating | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
46 Solar District Heating | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
46 Solar District Heating | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
46 Solar District Heating | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
46 Solar District Heating | T. The added tracker cost is based on interviews with Danish manufacturers.
46 Solar District Heating | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
46 Solar District Heating | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
46 Solar District Heating | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
46 Solar District Heating | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
46 Solar District Heating | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
46 Solar District Heating | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
50 Diesel engine farm | A. The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
50 Diesel engine farm | B. The maintenance normally consists of 1 -2 annual service visits.
50 Diesel engine farm | C. An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
50 Diesel engine farm | D. Not considered relevant for small domestic turbines.
50 Diesel engine farm | E. Based on information from manufacturers and resellers. The
50 Diesel engine farm | F. The prices depends significantly on turbine size (5 kW - 6 MEUR/MW; 10 kW - 4 MEUR/MW ; 25 kW - 3 MEUR/MW)
50 Diesel engine farm | G. The service cost is assumed fixed to 100EUR/kW/y.
50 Diesel engine farm | A. The range of generating capacity for a plant based on this technology is tipically 10-300 MW. Most of UK projects are in the range 18.5-20 MW. Emission requirements for plants with 18.5 MW and above are regulated by the Danish EPA and it is as of yet undetermined whether and exemption due to l...
50 Diesel engine farm | B. Engine size is normally in the range 400 kW - 2 MW. Here considered 10 engines of 1.8 MW.
50 Diesel engine farm | C. Assuming the same efficiency reduction from nameplate to annual average compared to Gas Engines in the main technology catalogue.
50 Diesel engine farm | D. The routine checks and oil change varies depending on the size. Smaller engines (400 kW) needs it every 250 h, while larger engines (2 MW) needs it every 1000h. Here assumed larger engines. Fixed O&M costs can increase for smaller sizes.
50 Diesel engine farm | E. 1.5h monthly maintenance for general checks, 4h semiannual, 2h annually, 2h biannually, 6h every 6 years.
50 Diesel engine farm | F. 50% of the output capacity can be reach within 15 seconds and after 20 seconds the total power output can be provided.
50 Diesel engine farm | G. Minimum load of the single engine is 30%. In a modular solution, some engines can be switched off to reduce the minimum load of the total plant. This way the performance is maintained at the optimal level.
50 Diesel engine farm | H. The startup time of the single engine is around 30 seconds. The syncronization of all the machines and the connection to the grid might increase the startup time to 3-10 minutes.
50 Diesel engine farm | I. Values related to the use of gas oil.
50 Diesel engine farm | L. Split based on the Engine technology in the main technology catalogue
50 Diesel engine farm | M. Development of cost follows the assumptions explained in the introduction. 10% learning rate and capacity development based on IEA ETP 2016.
50 Diesel engine farm | N. The specific investment cost can vary depending on a number of parameters, like size of engines, electrical equipment and other engines characteristics. The specific investment in 2015 from several projects and sources is in the range 0.282-0.456 MEUR/MW.
50 Diesel engine farm | O. The uncertainty is estimated based on the cost span of a number of similar observed projects. It is assumed equal to ±20% in 2020 and it increases to ±30% in 2050.
50 Diesel engine farm | P. Assumed a reduction of 4% in 2030 and 8% in 2050, due to automation of the power plant control and improvement in the operation
50 Diesel engine farm | Q. Assumed two times the reported value for service agreement excluding consumables, to take into account other fixed O&M components.
50 Diesel engine farm | R. The maintenance schedule is not affected by frequent starts and stops, fuel, or trips as modern combustion engines have the capability to stop and start without limitations or maintenance impact.
50 Diesel engine farm | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
50 Diesel engine farm | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
50 Diesel engine farm | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
50 Diesel engine farm | I. Uncertainty does not consider the risk of not finding a suitable reservoir.
50 Diesel engine farm | J. Heat pump nominal investment costs including installation and integration with geothermal plant, excl. Building integration, electrical supply and district heating connection
50 Diesel engine farm | K. The basis of the specific investment is the heat generation capacity for one unit including heat pumps but excluding ABEX.
50 Diesel engine farm | L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
50 Diesel engine farm | M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
50 Diesel engine farm | N. Temperature of geothermal heat is 65/10 (°C source/return). Temperature of DH water is (°C source/return) 90/45 (500 h), 85/40 (1500 h) and 80/40 (rest of estimated hours)
50 Diesel engine farm | O. Abandonment Cost (ABEX) accounts for approx. 7,5 % of total nominal investment [2]
50 Diesel engine farm | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
50 Diesel engine farm | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
50 Diesel engine farm | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
50 Diesel engine farm | T. The price is also included in nominal investment (equipment)
50 Diesel engine farm | V. The heat pumps produce heating at a higher temperature compared to Name plate several months of the year therefore the Name plate COP is higher than the yearly COP.
50 Diesel engine farm | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
50 Diesel engine farm | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
50 Diesel engine farm | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
50 Diesel engine farm | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
50 Diesel engine farm | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
50 Diesel engine farm | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
50 Diesel engine farm | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
50 Diesel engine farm | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
50 Diesel engine farm | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
50 Diesel engine farm | T. The added tracker cost is based on interviews with Danish manufacturers.
50 Diesel engine farm | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
50 Diesel engine farm | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
50 Diesel engine farm | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
50 Diesel engine farm | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
50 Diesel engine farm | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
50 Diesel engine farm | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
51 Natural gas engine plant | A. The cost presented provides an estimate for what capital cost and operating costs of wave power converters might be in the future assuming all R&D challenges have been overcome, that economics of scale have been realized and that efficiencies in production and operation due to the learning cur...
51 Natural gas engine plant | B. Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
51 Natural gas engine plant | C. Much dependent on plant size and location.
51 Natural gas engine plant | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
51 Natural gas engine plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
51 Natural gas engine plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
51 Natural gas engine plant | A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present m...
51 Natural gas engine plant | A. The technology is modular, normally composed by a certain amount of 2-10 MW engines. Here 20 engines of 10 MW are considered.
51 Natural gas engine plant | B. Typical capacity for ultra peakers and emergency plants is in the range 20-300 MW
51 Natural gas engine plant | C. Based on large gas motor (Wartsila 34SG)
51 Natural gas engine plant | D. Assuming the same efficiency reduction from nameplate to annual average compared to main technology catalogue.
51 Natural gas engine plant | E. Based on maintenance schedule of gas engines, considering the reduced number of operating hours and the fact that a typical scheduled maintenance services occurs after 2000, 4000 and 6000 hours, with 1 or 2 days of downtime each. No major maintenance window (16,000 h) is reached.
51 Natural gas engine plant | F. Based on the Gas Engine in the main technology catalogue
51 Natural gas engine plant | G. The values refers to the engine at nominal operating temperature.
51 Natural gas engine plant | H. Minimum load of the single engine is 30%. In a modular solution, some engines can be switched off to reduce the minimum load of the total plant. This way the performance is maintained at the optimal level. Calculation done assuming 20x10MW engines.
51 Natural gas engine plant | I. The engines can startup from warm in 2 minutes. The plant cold startup time is affected by the need to warm up the transformers, which brings it up to 10 minutes. If engines and transformers are hot, the startup time is lower. In case of smaller plants connected to distribution grid, the time ...
51 Natural gas engine plant | L. Dual fuel operation can be considered. Impacting 3-4% of the total plant cost and 7% of engine cost
51 Natural gas engine plant | M. Development of cost follows the assumptions explained in the introduction. 10% learning rate and capacity development based on IEA ETP 2016.
51 Natural gas engine plant | N. The specific investment cost can vary depending on a number of parameters, like size of engines, electrical equipment and other engines characteristics. The specific investment in 2015 from several projects and sources is in the range 0.443-0.616 MEUR/MW. The lower bound refers to smaller plan...
51 Natural gas engine plant | O. The fixed O&M cost is lower than a typical value for plants operating >4000 h a year. A typical large maintenance window including reinvestment is carried after 10,000 running hours. Due to the low utilization, this type of plants might never need it in its lifetime, reducing the fixed O&M cos...
51 Natural gas engine plant | P. Assumed a reduction of 4% in 2030 and 8% in 2050, due to automation of the power plant control and improvement in the operation
51 Natural gas engine plant | Q. The maintenance schedule is not affected by frequent starts and stops, fuel, or trips as modern combustion engines have the capability to stop and start without limitations or maintenance impact. Modern technology can sustain up to 1000 cycles/years with no significant wear.
51 Natural gas engine plant | R. The uncertainty is estimated based on the cost span of a number of similar observed projects. It is assumed equal to ±20% in 2020 and it increases to ±30% in 2050.
51 Natural gas engine plant | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
51 Natural gas engine plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
51 Natural gas engine plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
51 Natural gas engine plant | M. Estimate of cost of tank storage (diurnal storage) is 135 EUR/m3. The required size of the storage differs, but a typical size is 0.1-0.3 m3 storage for each m2 of solar panels, hence a 10,000 m2 solar thermal plant requires 1-3,000 m3 of diurnal storage.
51 Natural gas engine plant | N. Considering a reduction in prices for 2020 / 2020-2030 / 2030-2050 of 0.6 / 0.4 / 0.3 % p.a.
51 Natural gas engine plant | O. The division of cost elements is site- and plant specific. An indicative distribution of costs are; Solar collectors and piping (48%), heat exchanger, pumps etc. (8%), accumulation tank (11%), transmission pipeline (13%), building (2%), control, operation and startup (5%), land purchase, groun...
51 Natural gas engine plant | P. Please refer to www.solvarmedata.dk for display of efficiencies of Danish solar district heating plants. Chose a plant, select "Production and efficiency" and a chart will display the efficiency - typically varying between 20 and 50%.
51 Natural gas engine plant | Q. The solar radiation on the horizontal surface.
51 Natural gas engine plant | R. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
51 Natural gas engine plant | S. The cost per output power is converted from cost per collector area via formula: Power/Area = 0.7 kWth/m2. Note this is an approximation, original figures are stated per area or MWh
51 Natural gas engine plant | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
51 Natural gas engine plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
51 Natural gas engine plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
51 Natural gas engine plant | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
51 Natural gas engine plant | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
51 Natural gas engine plant | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
51 Natural gas engine plant | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
51 Natural gas engine plant | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
51 Natural gas engine plant | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
51 Natural gas engine plant | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
51 Natural gas engine plant | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
51 Natural gas engine plant | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
51 Natural gas engine plant | T. The added tracker cost is based on interviews with Danish manufacturers.
51 Natural gas engine plant | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
51 Natural gas engine plant | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
51 Natural gas engine plant | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
51 Natural gas engine plant | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
51 Natural gas engine plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
51 Natural gas engine plant | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Natural gas | A. The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
52 OCGT - Natural gas | B. The maintenance normally consists of 1 -2 annual service visits.
52 OCGT - Natural gas | C. An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
52 OCGT - Natural gas | D. Not considered relevant for small domestic turbines.
52 OCGT - Natural gas | E. Based on information from manufacturers and resellers. The
52 OCGT - Natural gas | F. The prices depends significantly on turbine size (5 kW - 6 MEUR/MW; 10 kW - 4 MEUR/MW ; 25 kW - 3 MEUR/MW)
52 OCGT - Natural gas | G. The service cost is assumed fixed to 100EUR/kW/y.
52 OCGT - Natural gas | A. The range of generating capacity for a power plant based on this technology is tipically 50-200 MW. Large aeroderivative gas turbines have a rating of 20-100 MW.
52 OCGT - Natural gas | B. The efficiency is drastically reduced at part-load. The difference between efficiency at full load and part load is on average 15%.
52 OCGT - Natural gas | C. Based on the Simple Cycle Turbine in the main technology catalogue. No improvement assumed in the future
52 OCGT - Natural gas | D. Considering one service per year for borescope inspection (18h). No major maintenance intervals reached, due to low utilization.
52 OCGT - Natural gas | E. Lifetime most likely >25years, given low utilization
52 OCGT - Natural gas | F. Some manufacturers offers pre-assembled mobile packages with installation in 30 days.
52 OCGT - Natural gas | G. Based on a droop control of 0.65 MW/s of a Industrial Trent 60 (66MW) turbine at self-sustained speed.
52 OCGT - Natural gas | H. Based on a gas turbine at self-sustained speed. Ramp rates of 15 MW/min to 50 MW/min.
52 OCGT - Natural gas | I. The minimum emissions-compliant load is around 50%, but in case emission regulations do not apply, this can be lower. The efficiency is reduced at part-load (roughly 15%)
52 OCGT - Natural gas | L. The lower bound of 7 minutes might be increased to 10 minutes if the plant is connected to high voltage and transformer needs to warm up before starting operations, similarly to Natural gas engine plants.
52 OCGT - Natural gas | M. Development of cost follows the assumptions explained in the introduction. 10% learning rate and capacity development based on IEA ETP 2016.
52 OCGT - Natural gas | N. The specific investment cost can vary depending on a number of parameters, like size of turbine, electrical equipment and other characteristics. The specific investment in 2015 from several projects is in the range 0.400-0.570.
52 OCGT - Natural gas | O. The uncertainty is estimated based on the cost span of a number of similar observed projects. It is assumed equal to ±20% in 2020 and it increases to ±30% in 2050.
52 OCGT - Natural gas | P. Assumed a reduction of 4% in 2030 and 8% in 2050, due to automation of the power plant control and improvement in the operation
52 OCGT - Natural gas | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
52 OCGT - Natural gas | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Natural gas | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Natural gas | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Natural gas | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Natural gas | I. Uncertainty does not consider the risk of not finding a suitable reservoir.
52 OCGT - Natural gas | J. Heat pump nominal investment costs including installation and integration with geothermal plant, excl. Building integration, electrical supply and district heating connection
52 OCGT - Natural gas | K. The basis of the specific investment is the heat generation capacity for one unit including heat pumps but excluding ABEX.
52 OCGT - Natural gas | L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
52 OCGT - Natural gas | M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
52 OCGT - Natural gas | N. Temperature of geothermal heat is 65/10 (°C source/return). Temperature of DH water is (°C source/return) 90/45 (500 h), 85/40 (1500 h) and 80/40 (rest of estimated hours)
52 OCGT - Natural gas | O. Abandonment Cost (ABEX) accounts for approx. 7,5 % of total nominal investment [2]
52 OCGT - Natural gas | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
52 OCGT - Natural gas | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Natural gas | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Natural gas | T. The price is also included in nominal investment (equipment)
52 OCGT - Natural gas | V. The heat pumps produce heating at a higher temperature compared to Name plate several months of the year therefore the Name plate COP is higher than the yearly COP.
52 OCGT - Natural gas | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
52 OCGT - Natural gas | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Natural gas | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Natural gas | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
52 OCGT - Natural gas | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
52 OCGT - Natural gas | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
52 OCGT - Natural gas | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
52 OCGT - Natural gas | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
52 OCGT - Natural gas | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
52 OCGT - Natural gas | T. The added tracker cost is based on interviews with Danish manufacturers.
52 OCGT - Natural gas | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
52 OCGT - Natural gas | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
52 OCGT - Natural gas | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
52 OCGT - Natural gas | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
52 OCGT - Natural gas | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Natural gas | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Light fuel oil | A. The cost presented provides an estimate for what capital cost and operating costs of wave power converters might be in the future assuming all R&D challenges have been overcome, that economics of scale have been realized and that efficiencies in production and operation due to the learning cur...
52 OCGT - Light fuel oil | B. Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
52 OCGT - Light fuel oil | C. Much dependent on plant size and location.
52 OCGT - Light fuel oil | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
52 OCGT - Light fuel oil | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Light fuel oil | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Light fuel oil | A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present m...
52 OCGT - Light fuel oil | A. Value indicate the estimated change from the correspondent value of natural gas fuelled plant (unit is the same as the paramter).
52 OCGT - Light fuel oil | B. Emission values for Gas Oil. If Residual Oil used, SO2 emissions increased to 100g, NOx reduced to 138g and Particles to 3g.
52 OCGT - Light fuel oil | C. Development of cost follows the assumptions explained in the introduction. 10% learning rate and capacity development based on IEA ETP 2016. Same development as natural gas fuelled plant, since the technology is the same.
52 OCGT - Light fuel oil | D. The uncertainty is estimated based on the cost span of a number of similar observed projects. It is assumed equal to ±20% in 2020 and it increases to ±30% in 2050.
52 OCGT - Light fuel oil | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
52 OCGT - Light fuel oil | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Light fuel oil | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Light fuel oil | H. Minimum load of the single engine is 30%. In a modular solution, some engines can be switched off to reduce the minimum load of the total plant. This way the performance is maintained at the optimal level. Calculation done assuming 20x10MW engines.
52 OCGT - Light fuel oil | I. The engines can startup from warm in 2 minutes. The plant cold startup time is affected by the need to warm up the transformers, which brings it up to 10 minutes. If engines and transformers are hot, the startup time is lower. In case of smaller plants connected to distribution grid, the time ...
52 OCGT - Light fuel oil | L. Dual fuel operation can be considered. Impacting 3-4% of the total plant cost and 7% of engine cost
52 OCGT - Light fuel oil | M. Development of cost follows the assumptions explained in the introduction. 10% learning rate and capacity development based on IEA ETP 2016.
52 OCGT - Light fuel oil | N. The specific investment cost can vary depending on a number of parameters, like size of engines, electrical equipment and other engines characteristics. The specific investment in 2015 from several projects and sources is in the range 0.443-0.616 MEUR/MW. The lower bound refers to smaller plan...
52 OCGT - Light fuel oil | O. The fixed O&M cost is lower than a typical value for plants operating >4000 h a year. A typical large maintenance window including reinvestment is carried after 10,000 running hours. Due to the low utilization, this type of plants might never need it in its lifetime, reducing the fixed O&M cos...
52 OCGT - Light fuel oil | P. Assumed a reduction of 4% in 2030 and 8% in 2050, due to automation of the power plant control and improvement in the operation
52 OCGT - Light fuel oil | Q. The maintenance schedule is not affected by frequent starts and stops, fuel, or trips as modern combustion engines have the capability to stop and start without limitations or maintenance impact. Modern technology can sustain up to 1000 cycles/years with no significant wear.
52 OCGT - Light fuel oil | R. The uncertainty is estimated based on the cost span of a number of similar observed projects. It is assumed equal to ±20% in 2020 and it increases to ±30% in 2050.
52 OCGT - Light fuel oil | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
52 OCGT - Light fuel oil | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Light fuel oil | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Light fuel oil | M. Estimate of cost of tank storage (diurnal storage) is 135 EUR/m3. The required size of the storage differs, but a typical size is 0.1-0.3 m3 storage for each m2 of solar panels, hence a 10,000 m2 solar thermal plant requires 1-3,000 m3 of diurnal storage.
52 OCGT - Light fuel oil | N. Considering a reduction in prices for 2020 / 2020-2030 / 2030-2050 of 0.6 / 0.4 / 0.3 % p.a.
52 OCGT - Light fuel oil | O. The division of cost elements is site- and plant specific. An indicative distribution of costs are; Solar collectors and piping (48%), heat exchanger, pumps etc. (8%), accumulation tank (11%), transmission pipeline (13%), building (2%), control, operation and startup (5%), land purchase, groun...
52 OCGT - Light fuel oil | P. Please refer to www.solvarmedata.dk for display of efficiencies of Danish solar district heating plants. Chose a plant, select "Production and efficiency" and a chart will display the efficiency - typically varying between 20 and 50%.
52 OCGT - Light fuel oil | Q. The solar radiation on the horizontal surface.
52 OCGT - Light fuel oil | R. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
52 OCGT - Light fuel oil | S. The cost per output power is converted from cost per collector area via formula: Power/Area = 0.7 kWth/m2. Note this is an approximation, original figures are stated per area or MWh
52 OCGT - Light fuel oil | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
52 OCGT - Light fuel oil | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Light fuel oil | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Light fuel oil | L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
52 OCGT - Light fuel oil | M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
52 OCGT - Light fuel oil | N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
52 OCGT - Light fuel oil | O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. \nA more moderate learnin...
52 OCGT - Light fuel oil | P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
52 OCGT - Light fuel oil | P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M...
52 OCGT - Light fuel oil | Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from ...
52 OCGT - Light fuel oil | R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
52 OCGT - Light fuel oil | S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used ...
52 OCGT - Light fuel oil | T. The added tracker cost is based on interviews with Danish manufacturers.
52 OCGT - Light fuel oil | U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-t...
52 OCGT - Light fuel oil | V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
52 OCGT - Light fuel oil | W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
52 OCGT - Light fuel oil | *. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
52 OCGT - Light fuel oil | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
52 OCGT - Light fuel oil | **. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.

## Ref
ws | description
01 Coal CHP | 1. Elsam, November 2003
01 Coal CHP | 2. Elsam's and Elkraft's update of the Danish Energy Agency's 'Teknologidata for el- og varmeproduktionsanlæg', December 1997
01 Coal CHP | 3. Eltra, September 2003
01 Coal CHP | 5. Danish Energy Agency, 2009.
01 Coal CHP | 6. "Projected costs of generating electricity", International Energy Agency (IEA), 2005.
01 Coal CHP | 7. "Energy technology perspectives 2008", International Energy Agency, 2008.
01 Coal CHP | 8. Danish Energy Agency, 2008. Measured data (1994-2006) from newest power plants in Denmark.
01 Coal CHP | 9. Own estimate by Danish Energy Agency and Energinet.dk, 2011.
01 Coal CHP | 10. Energinet.dk, 2009
01 Coal CHP | 11. www.ad700.dk
01 Coal CHP | 12. "En opdateret analyse af Danmarks muligheder for at reducere emissionerne af NOx" (Updated analysis of Denmark's options to reduce NOx emissions; in Danish), Danish Environmental Protection Agency, 2009.
01 Coal CHP | 13. National Environmental Research Institute, Denmark, 2009 (data from 2007).
01 Coal CHP | 14. DONG Energy, 2009.
01 Coal CHP | 15. "UK Electricity Generation Costs Update", Mott MacDonald, June 2010.
01 Coal CHP | 16. "The Costs of CO2 Capture, Transport and Storage", Zero Emissions Platform (ZEP), July 2011
01 Coal CHP | 17. The IEA World Energy Outlook 2014 coal fired Ultra-supercritical power plants in Europe. Values used are the projection for 2020.
01 Coal CHP | 18. The IEA Projected Cost of Generating Electricity 2015 for coal fired power plants. Here both the 'world median' is used, and data from recently commissioned plants in the Netherlands. The three units in the Netherlands are chosen because of the proximity to Denmark, because the socio-economic...
01 Coal CHP | 19. EIA Updated Capital Cost Estimates for Utility Scale Electricity Generating Plants 2013 for pulverizes coal fired advanced single units.[1]
01 Coal CHP | 20. Aggregated data from different projects on existing units that Ea Energy Analyses have been working on since 2010. Data is used for estimating O&M costs.
01 Coal CHP | 21. IEA( 2016),Energy Technology Perspectives
01 Coal CHP | 22. E.S. Rubin et al. / Energy Policy 86 (2015) page 198-218, A review of learning rates for electricity supply technologies
03a Coal to wood pellets exi bo | 10. Ea Energy Analysis, based on experience from various commercial projects.
03a Coal to wood pellets exi bo | 11. Government response to the consultation on proposals for the levels of banded support under the Renewables Obligation for the period 2013-17 and the Renewables Obligation Order 2012, UK Department of Energy and Climate Change, July 2012.
03a Coal to wood pellets exi bo | 12. A strategy for converting coal fueled power plants to biomass, Future Metrics, September 2014
03b Coal to wood chips n. boile | 10. Ea Energy Analysis. based on experience from various commercial projects.
03b Coal to wood chips n. boile | 12. A strategy for converting coal fueled power plants to biomass. Future Metrics. September 2014
03c coal to wood chips exi. boi | 10. Ea Energy Analysis, based on experience from various commercial projects.
03d coal to wood chips exi. boi | 13. Ramboll, internal assessment
04 Gas turb. simple cycle, L | 5. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
04 Gas turb. simple cycle, L | 6. Wärtsila Technical Journal "in detail" 02-2014
04 Gas turb. simple cycle, L | 7. Data specs from maufacturers (Web) 2015
04 Gas turb. simple cycle, L | 8. Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
04 Gas turb. simple cycle, L | 9. Danish Gas Technology Centre, environmental survey 2012
04 Gas turb. simple cycle, L | 10. Smart Power Generation - The future of electricity production, J. Klimstra & M. Hotakainen 2011
04 Gas turb. simple cycle, L | 11. IEA: Projected cost of generating electricity, 2010
04 Gas turb. simple cycle, L | 12. COWI 2015 input
04 Gas turb. simple cycle, L | 13. The Omes Project results (2005)
04 Gas turb. simple cycle, L | 14. WBDG-Publication, B. L. Capehart, Microtubines, 2014
04 Gas turb. simple cycle Sm-Me | 5. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
04 Gas turb. simple cycle Sm-Me | 6. Wärtsila Technical Journal "in detail" 02-2014
04 Gas turb. simple cycle Sm-Me | 7. Data specs from maufacturers (Web) 2015
04 Gas turb. simple cycle Sm-Me | 8. Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
04 Gas turb. simple cycle Sm-Me | 9. Danish Gas Technology Centre, environmental survey 2012
04 Gas turb. simple cycle Sm-Me | 10. Smart Power Generation - The future of electricity production, J. Klimstra & M. Hotakainen 2011
04 Gas turb. simple cycle Sm-Me | 11. IEA: Projected cost of generating electricity, 2010
04 Gas turb. simple cycle Sm-Me | 12. COWI 2015 input
04 Gas turb. simple cycle Sm-Me | 13. The Omes Project results (2005)
04 Gas turb. simple cycle Sm-Me | 14. WBDG-Publication, B. L. Capehart, Microtubines, 2014
04 Gas turb. simple cycle Micro | 5. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
04 Gas turb. simple cycle Micro | 6. Wärtsila Technical Journal "in detail" 02-2014
04 Gas turb. simple cycle Micro | 7. Data specs from maufacturers (Web) 2015
04 Gas turb. simple cycle Micro | 8. Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
04 Gas turb. simple cycle Micro | 9. Danish Gas Technology Centre, environmental survey 2012
04 Gas turb. simple cycle Micro | 10. Smart Power Generation - The future of electricity production, J. Klimstra & M. Hotakainen 2011
04 Gas turb. simple cycle Micro | 11. IEA: Projected cost of generating electricity, 2010
04 Gas turb. simple cycle Micro | 12. COWI 2015 input
04 Gas turb. simple cycle Micro | 13. The Omes Project results (2005)
04 Gas turb. simple cycle Micro | 14. WBDG-Publication, B. L. Capehart, Microtubines, 2014
05 Gas turb. CC, steam extract. | 1. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
05 Gas turb. CC, steam extract. | 3. Data specs from maufacturers (Web) 2015
05 Gas turb. CC, steam extract. | 5. Wärtsila Technical Journal "in detail" 02-2014
05 Gas turb. CC, steam extract. | 6. Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
05 Gas turb. CC, steam extract. | 7. Danish Gas Technology Centre, environmental survey 2012
05 Gas turb. CC, steam extract. | 8. Smart Power Generation; the future of electricity production, J. Klimstra & M. Hotakainen 2011
05 Gas turb. CC, steam extract. | 9. IEA: Projected cost of generating electricity, 2010
05 Gas turb. CC, steam extract. | 10. UK Electricity Generation Costs Update, M.M. Donald, June 2010
05 Gas turb. CC, steam extract. | 11. Siemens : Data on GT-CC (2010)
05 Gas turb. CC, Back-pressure | 1. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
05 Gas turb. CC, Back-pressure | 3. Data specs from maufacturers (Web) 2015
05 Gas turb. CC, Back-pressure | 5. Wärtsila Technical Journal "in detail" 02-2014
05 Gas turb. CC, Back-pressure | 6. Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
05 Gas turb. CC, Back-pressure | 7. Danish Gas Technology Centre, environmental survey 2012
05 Gas turb. CC, Back-pressure | 8. Smart Power Generation; the future of electricity production, J. Klimstra & M. Hotakainen 2011
05 Gas turb. CC, Back-pressure | 9. IEA: Projected cost of generating electricity, 2010
05 Gas turb. CC, Back-pressure | 10. UK Electricity Generation Costs Update, M.M. Donald, June 2010
05 Gas turb. CC, Back-pressure | 11. Siemens : Data on GT-CC (2010)
06 Gas engines, natural gas | 3. ASUE BHKW Kenndata 2014/2015
06 Gas engines, natural gas | 4. DGC Efficiency and emission test reports
06 Gas engines, natural gas | 5. DGC analysis, The gas fired cogneration sector, Bilagsrapport 9, Energiforligs analyse 2013
06 Gas engines, natural gas | 6. Features and parameters of various power plant technologies, Wartsila "In Detail", 02-2014 etc.
06 Gas engines, natural gas | 7. Dansk Fjernvarme and FDKV reportings from CHP installations, the Dansk Fjernvarme information is from a 2012 suvey for an earlier version of the report
06 Gas engines, natural gas | 8. Ongoing Sulpur research project at DGC (MUDP)
06 Gas engines, natural gas | 10. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
06 Gas engines, natural gas | 11. Blockheizkraftwerke 2013, M.Buller et al, GWF Gas Erdgas, Juni 2014
06 Gas engines, natural gas | 12. Suppliers association information etc.
06 Gas engines, natural gas | 13. MAN Turbo Presentation of Gas Engine with fuel switch, 2012
06 Gas engines, biogas | 3. ASUE BHKW Kenndata 2014/2015
06 Gas engines, biogas | 4. DGC Efficiency and emission test reports
06 Gas engines, biogas | 5. DGC analysis, The gas fired cogneration sector, Bilagsrapport 9, Energiforligs analyse 2013
06 Gas engines, biogas | 6. Features and parameters of various power plant technologies, Wartsila "In Detail", 02-2014 etc.
06 Gas engines, biogas | 7. Dansk Fjernvarme and FDKV reportings from CHP installations, the Dansk Fjernvarme information is from a 2012 suvey for an earlier version of the report
06 Gas engines, biogas | 8. Ongoing Sulpur research project at DGC (MUDP)
06 Gas engines, biogas | 10. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
06 Gas engines, biogas | 11. Blockheizkraftwerke 2013, M.Buller et al, GWF Gas Erdgas, Juni 2014
06 Gas engines, biogas | 12. Suppliers association information etc.
06 Gas engines, biogas | 13. MAN Turbo Presentation of Gas Engine with fuel switch, 2012
08 WtE CHP, Large, 40 degree | 1. Rambøll present work, range of WtE-projects
08 WtE CHP, Large, 40 degree | 2. Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf.\n Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants\n 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and\n emis...
08 WtE CHP, Large, 40 degree | 3. Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013," \n http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkend...
08 WtE CHP, Large, 40 degree | 4. Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
08 WtE CHP, Large, 40 degree | 5. Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook,\nSerge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019\n https:/...
08 WtE CHP, Large, 50 degree | 1. Rambøll present work, range of WtE-projects
08 WtE CHP, Large, 50 degree | 2. Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf.\n Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants\n 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and\n emis...
08 WtE CHP, Large, 50 degree | 3. Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013," \n http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkend...
08 WtE CHP, Large, 50 degree | 4. Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
08 WtE CHP, Large, 50 degree | 5. Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook,\nSerge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019\n https:/...
08 WtE CHP, Medium | 1. Rambøll present work, range of WtE-projects
08 WtE CHP, Medium | 2. Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf.\n Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants\n 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and\n emis...
08 WtE CHP, Medium | 3. Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013," \n http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkend...
08 WtE CHP, Medium | 4. Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
08 WtE CHP, Medium | 5. Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook,\nSerge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019\n https:/...
08 WtE CHP, Small | 1. Rambøll present work, range of WtE-projects
08 WtE CHP, Small | 2. Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf.\n Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants\n 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and\n emis...
08 WtE CHP, Small | 3. Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013," \n http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkend...
08 WtE CHP, Small | 4. Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
08 WtE CHP, Small | 5. Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook,\nSerge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019\n https:/...
08 WtE HOP | 1. Rambøll present work, range of WtE-projects
08 WtE HOP | 2. Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf.\n Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants\n 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and\n emis...
08 WtE HOP | 3. Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013," \n http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkend...
08 WtE HOP | 4. Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
08 WtE HOP | 5. Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook,\nSerge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019\n https:/...
09a Wood Chips, Large 40 degree | 1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
09a Wood Chips, Large 40 degree | 2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN;...
09a Wood Chips, Large 40 degree | 3. Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 ...
09a Wood Chips, Large 50 degree | 1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
09a Wood Chips, Large 50 degree | 2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN;...
09a Wood Chips, Large 50 degree | 3. Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 ...
09a Wood Chips, Medium | 1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
09a Wood Chips, Medium | 2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN;...
09a Wood Chips, Medium | 3. Emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission fact...
09a Wood Chips, Small | 1. Rambøll Danmark, internal model and evaluation based on either existing projects, supplier offers, or pre-project studies.
09a Wood Chips, Small | 2. Emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission fact...
09b Wood Pellets, Large 40 degr | 1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
09b Wood Pellets, Large 40 degr | 2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN;...
09b Wood Pellets, Large 50 degr | 1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
09b Wood Pellets, Large 50 degr | 2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN;...
09b Wood Pellets, Medium | 1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
09b Wood Pellets, Medium | 2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN;...
09b Wood Pellets, Small | 1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
09c Straw, Large, 40 degree | 1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
09c Straw, Large, 40 degree | 2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN;...
09c Straw, Large, 50 degree | 1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
09c Straw, Large, 50 degree | 2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN;...
09c Straw, Medium | 1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
09c Straw, Medium | 2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN;...
09c Straw, Small | 1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies. NOTICE: There are to our knowledge no references on ORC plants running on straw.
09a Wood Chips HOP, small | 1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
09a Wood Chips HOP, small | 2. Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 ...
09a Wood Chips HOP, medium | 1. Rambøll Danmark, internal evaluation based on either existing projects, supplierand operator information, or pre-project studies.
09a Wood Chips HOP, medium | 2. Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 ...
09a Wood Chips HOP, large | 1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
09a Wood Chips HOP, large | 2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN;...
09a Wood Chips HOP, large | 3. Emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission fact...
09b Wood Pellets HOP | 1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
09c Straw HOP | 1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
09a Wood Chips extract. plant | 1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
09a Wood Chips extract. plant | 2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN;...
09a Wood Chips extract. plant | 3. Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 ...
09b Wood Pellets extract. plant | 1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
09b Wood Pellets extract. plant | 2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN;...
10 Stirling | 1. Stirling DK, December 2009
11 SOFC-CHP | 1. BloomEnergy, www.bloomenergy.com, 2014-11-11
11 SOFC-CHP | 2. https://www.mhps.com/en/technology/index.html, 2014-11-14
11 SOFC-CHP | 3. BloomEnergy, Product datasheet: ES-5710 Energy Saver, November 2014: http://c0688662.cdn.cloudfiles.rackspacecloud.com/downloads_pdf_Bloomenergy_DataSheet_ES-5710.pdf
11 SOFC-CHP | 4. BloomEnergy, Product datasheet: ES-5700 Energy Saver, November 2014: http://c0688662.cdn.cloudfiles.rackspacecloud.com/downloads_pdf_Bloomenergy_DataSheet_ES-5700.pdf
11 SOFC-CHP | 5. Iskov H., Rasmussen N.B., "Update of technology data for energy plants: Fuel cells, electrolysis and technologies for bio-SNG", Danish gas Technology centre, 2013.
11 SOFC-CHP | 6. Fuel Cell and Hydrogen Joint Undertaking: "Multi - Annual Work Plan 2014-2020", adopted 2014-06-30
11 SOFC-CHP | 7. http://www.asue.de, 2014-11-17
11 SOFC-CHP | 8. BloomEnergy Server, http://en.wikipedia.org/wiki/Bloom_Energy_Server, 02-02
11 SOFC-CHP | 13. Chick, LA; Gotthold, DW; Weimar, MR; Whyatt, GA, Cost Study for Manufacturing of Solid Oxide Fuel Cell Power Systems, 2013, Pacific Northwest National Laboratory prepared for the U.S. Department of Energy.
12 LT-PEMFC CHP | 3. International Energy Agency, 2015, Technology Roadmap - Hydrogen and Fuel Cells.
12 LT-PEMFC CHP | 4. Ea Energy Analyses et al. 2016, Technology Data for Hydrogen Technologies.
12 LT-PEMFC CHP | 5. Practical data and expert opinion from Dantherm Power
20 Onshore turbines | 2. DTU International Energy Report - Wind Energy, DTU, 2014
20 Onshore turbines | 3. Master data register of wind turbines at end of December 2014, Danish Energy Agency, 2015
20 Onshore turbines | 4. Nielsen, P. et. al., Vindmøllers økonomi EUDP projekt 33033-0196, 2010
20 Onshore turbines | 14. Information from Energinet.dk based on analyses of installed projects (2013-14), published under "Købsretsordningen", 2015
20 Onshore turbines | 15. Når all-inclusive service alligevel ikke dækker alt, Naturlig Energi, nov. 2014
20 Onshore turbines | 16. Schwabe, P., Lensink, S. & Hand, M., IEA Wind Task 26: Multi-national case study of the financial cost of wind energy, 2011
20 Onshore turbines | 18. Hvor længe holder en mølle, Naturlig Energi, januar 2012
20 Onshore turbines | 25. Analysis of "køberets" projects 2017-18
20 Onshore turbines | 26. Interviews with project developers and suppliers dec.18-jan.19
21 Offshore turbines | 1. Stiesdal, Offshore wind turbine size prediction tool.xlsx, with changes by Danish Energy Agency.
21 Offshore turbines | 2. DTU Wind Energy: Pushing the physics of the large turbines of the future. 2021. Published in DTU International Energy Report 2021: Perspectives on Wind Energy. https://doi.org/10.11581/DTU.00000208
21 Offshore turbines | 3. EMD cost and AEP Excel calculation tool
21 Offshore turbines | 4. EA Energy Analyse/Cowi April 20 slide 25: https://www.ea-energianalyse.dk/wp-content/uploads/2020/05/1949_Offshore-wind-and-infrastructure.pdf
21 Offshore turbines | 5. From ENS 2021: FT - omkostninger Anholt, HR3, KF.xlsx
21 Offshore turbines | 6. Interview with Per Stenholt, Vattenfall, November 21
21 Near shore turbines | 1. Stiesdal, Offshore wind turbine size prediction tool.xlsx, with changes by Danish Energy Agency.
21 Near shore turbines | 2. DTU Wind Energy: Pushing the physics of the large turbines of the future. 2021. Published in DTU International Energy Report 2021: Perspectives on Wind Energy. https://doi.org/10.11581/DTU.00000208
21 Near shore turbines | 3. EMD cost and AEP Excel calculation tool
21 Near shore turbines | 4. EA Energy Analyse/Cowi April 20 slide 25: https://www.ea-energianalyse.dk/wp-content/uploads/2020/05/1949_Offshore-wind-and-infrastructure.pdf
21 Near shore turbines | 5. From ENS 2021: FT - omkostninger Anholt, HR3, KF.xlsx
21 Near shore turbines | 6. Interview with Per Stenholt, Vattenfall, November 21
22 Rooftop PV residential | 1. Peter Riddersholm Wang, DMI Teknisk Rapport 13-08, Referenceværdier: Måneds- og årsværdier for stationer 2001 - 2010, Danmark for temperatur, relativ luftfugtighed, vindhastighed, globalstråling og nedbør.
22 Rooftop PV residential | 2. "World Energy Outlook". IEA. 2021.
22 Rooftop PV residential | 3. " Photovoltaics report". Fraunhofer. 27 July 2021.
22 Rooftop PV residential | 4. "Global Market Outlook For Solar Power 2021 - 2025". SolarPower Europe. July 2021.
22 Rooftop PV residential | 5. PV Tech. (4. Juli 2017). Hentet fra https://www.pv-tech.org/products/helioslites-disruptive-1.5-axis-pv-tracker
22 Rooftop PV residential | 6. Interviews with Danish developers and suppliers in the summer 2021.
22 Rooftop PV comm.&industrial | 1. Peter Riddersholm Wang, DMI Teknisk Rapport 13-08, Referenceværdier: Måneds- og årsværdier for stationer 2001 - 2010, Danmark for temperatur, relativ luftfugtighed, vindhastighed, globalstråling og nedbør.
22 Rooftop PV comm.&industrial | 2. "World Energy Outlook". IEA. 2021.
22 Rooftop PV comm.&industrial | 3. " Photovoltaics report". Fraunhofer. 27 July 2021.
22 Rooftop PV comm.&industrial | 4. "Global Market Outlook For Solar Power 2021 - 2025". SolarPower Europe. July 2021.
22 Rooftop PV comm.&industrial | 5. PV Tech. (4. Juli 2017). Hentet fra https://www.pv-tech.org/products/helioslites-disruptive-1.5-axis-pv-tracker
22 Rooftop PV comm.&industrial | 6. Interviews with Danish developers and suppliers in the summer 2021.
22 Utility-scale PV | 1. Peter Riddersholm Wang, DMI Teknisk Rapport 13-08, Referenceværdier: Måneds- og årsværdier for stationer 2001 - 2010, Danmark for temperatur, relativ luftfugtighed, vindhastighed, globalstråling og nedbør.
22 Utility-scale PV | 2. "World Energy Outlook". IEA. 2021.
22 Utility-scale PV | 3. " Photovoltaics report". Fraunhofer. 27 July 2021.
22 Utility-scale PV | 4. "Global Market Outlook For Solar Power 2021 - 2025". SolarPower Europe. July 2021.
22 Utility-scale PV | 5. PV Tech. (4. Juli 2017). Hentet fra https://www.pv-tech.org/products/helioslites-disruptive-1.5-axis-pv-tracker
22 Utility-scale PV | 6. Interviews with Danish developers and suppliers in the summer 2021.
22 Utility-scale PV tracker | 1. Peter Riddersholm Wang, DMI Teknisk Rapport 13-08, Referenceværdier: Måneds- og årsværdier for stationer 2001 - 2010, Danmark for temperatur, relativ luftfugtighed, vindhastighed, globalstråling og nedbør.
22 Utility-scale PV tracker | 2. "World Energy Outlook". IEA. 2021.
22 Utility-scale PV tracker | 3. " Photovoltaics report". Fraunhofer. 27 July 2021.
22 Utility-scale PV tracker | 4. "Global Market Outlook For Solar Power 2021 - 2025". SolarPower Europe. July 2021.
22 Utility-scale PV tracker | 5. PV Tech. (4. Juli 2017). Hentet fra https://www.pv-tech.org/products/helioslites-disruptive-1.5-axis-pv-tracker
22 Utility-scale PV tracker | 6. Interviews with Danish developers and suppliers in the summer 2021.
23 Wave Energy | 1. Wave Net final report, Project no. ERK5 - CT -1999-20001 (2000 - 2003)
23 Wave Energy | 2. "Energy Technology Perspectives 2008", International Energy Agency, 2008.
23 Wave Energy | 3. "Energy Technology Perspectives 2010", International Energy Agency, 2010.
23 Wave Energy | 4. Danish Wave Energy Association, 2012
40 Comp. hp, airsource 1 MW | 1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
40 Comp. hp, airsource 1 MW | 2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
40 Comp. hp, airsource 1 MW | 3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
40 Comp. hp, airsource 1 MW | 4. Scandinavian Energy Group, 2015, Conversation
40 Comp. hp, airsource 1 MW | 5. Advansor, 2015, Conversation
40 Comp. hp, airsource 1 MW | 6. Hybrid Energi, 2015, Conversation
40 Comp. hp, airsource 1 MW | 7. Innoterm, 2015, Conversation
40 Comp. hp, airsource 1 MW | 8. Cronborg, 2015, Conversation
40 Comp. hp, airsource 1 MW | 9. Johnson Controls, 2019, Conversation
40 Comp. hp, airsource 1 MW | 10. Teknologisk Institut, 2015, 2019, Conversation
40 Comp. hp, airsource 1 MW | 11. Energinet.dk, 2015, Conversation
40 Comp. hp, airsource 1 MW | 12. IEA 2012, Energy Technology Perspectives, 2012
40 Comp. hp, airsource 1 MW | 13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
40 Comp. hp, airsource 1 MW | 14. IES/Victor DST, 2019, Conversation
40 Comp. hp, airsource 1 MW | 15. PlanEnergi, 2019, practical experience from installed plants
40 Comp. hp, airsource 1 MW | 16. DMI, 2019
40 Comp. hp, airsource 1 MW | 17. Danfoss, 2019, Conversation
40 Comp. hp, airsource 1 MW | 18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmev...
40 Comp. hp, airsource 3 MW | 1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
40 Comp. hp, airsource 3 MW | 2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
40 Comp. hp, airsource 3 MW | 3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
40 Comp. hp, airsource 3 MW | 4. Scandinavian Energy Group, 2015, Conversation
40 Comp. hp, airsource 3 MW | 5. Advansor, 2015, Conversation
40 Comp. hp, airsource 3 MW | 6. Hybrid Energi, 2015, Conversation
40 Comp. hp, airsource 3 MW | 7. Innoterm, 2015, Conversation
40 Comp. hp, airsource 3 MW | 8. Cronborg, 2015, Conversation
40 Comp. hp, airsource 3 MW | 9. Johnson Controls, 2019, Conversation
40 Comp. hp, airsource 3 MW | 10. Teknologisk Institut, 2015, 2019, Conversation
40 Comp. hp, airsource 3 MW | 11. Energinet.dk, 2015, Conversation
40 Comp. hp, airsource 3 MW | 12. IEA 2012, Energy Technology Perspectives, 2012
40 Comp. hp, airsource 3 MW | 13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
40 Comp. hp, airsource 3 MW | 14. IES/Victor DST, 2019, Conversation
40 Comp. hp, airsource 3 MW | 15. PlanEnergi, 2019, practical experience from installed plants
40 Comp. hp, airsource 3 MW | 16. DMI, 2019
40 Comp. hp, airsource 3 MW | 17. Danfoss, 2019, Conversation
40 Comp. hp, airsource 3 MW | 18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmev...
40 Comp. hp, airsource 10 MW | 1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
40 Comp. hp, airsource 10 MW | 2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
40 Comp. hp, airsource 10 MW | 3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
40 Comp. hp, airsource 10 MW | 4. Scandinavian Energy Group, 2015, Conversation
40 Comp. hp, airsource 10 MW | 5. Advansor, 2015, Conversation
40 Comp. hp, airsource 10 MW | 6. Hybrid Energi, 2015, Conversation
40 Comp. hp, airsource 10 MW | 7. Innoterm, 2015, Conversation
40 Comp. hp, airsource 10 MW | 8. Cronborg, 2015, Conversation
40 Comp. hp, airsource 10 MW | 9. Johnson Controls, 2019, Conversation
40 Comp. hp, airsource 10 MW | 10. Teknologisk Institut, 2015, 2019, Conversation
40 Comp. hp, airsource 10 MW | 11. Energinet.dk, 2015, Conversation
40 Comp. hp, airsource 10 MW | 12. IEA 2012, Energy Technology Perspectives, 2012
40 Comp. hp, airsource 10 MW | 13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
40 Comp. hp, airsource 10 MW | 14. IES/Victor DST, 2019, Conversation
40 Comp. hp, airsource 10 MW | 15. PlanEnergi, 2019, practical experience from installed plants
40 Comp. hp, airsource 10 MW | 16. DMI, 2019
40 Comp. hp, airsource 10 MW | 17. Danfoss, 2019, Conversation
40 Comp. hp, airsource 10 MW | 18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmev...
40 Comp. hp, excess heat 1 MW | 1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
40 Comp. hp, excess heat 1 MW | 2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
40 Comp. hp, excess heat 1 MW | 3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
40 Comp. hp, excess heat 1 MW | 4. Scandinavian Energy Group, 2015, Conversation
40 Comp. hp, excess heat 1 MW | 5. Advansor, 2015, Conversation
40 Comp. hp, excess heat 1 MW | 6. Hybrid Energi, 2015, Conversation
40 Comp. hp, excess heat 1 MW | 7. Innoterm, 2015, Conversation
40 Comp. hp, excess heat 1 MW | 8. Cronborg, 2015, Conversation
40 Comp. hp, excess heat 1 MW | 9. Johnson Controls, 2019, Conversation
40 Comp. hp, excess heat 1 MW | 10. Teknologisk Institut, 2015, 2019, Conversation
40 Comp. hp, excess heat 1 MW | 11. Energinet.dk, 2015, Conversation
40 Comp. hp, excess heat 1 MW | 12. IEA 2012, Energy Technology Perspectives, 2012
40 Comp. hp, excess heat 1 MW | 13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
40 Comp. hp, excess heat 1 MW | 14. IES/Victor DST, 2019, Conversation
40 Comp. hp, excess heat 1 MW | 15. PlanEnergi, 2019, practical experience from installed plants
40 Comp. hp, excess heat 1 MW | 16. DMI, 2019
40 Comp. hp, excess heat 1 MW | 17. Danfoss, 2019, Conversation
40 Comp. hp, excess heat 1 MW | 18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmev...
40 Comp. hp, excess heat 3 MW | 1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
40 Comp. hp, excess heat 3 MW | 2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
40 Comp. hp, excess heat 3 MW | 3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
40 Comp. hp, excess heat 3 MW | 4. Scandinavian Energy Group, 2015, Conversation
40 Comp. hp, excess heat 3 MW | 5. Advansor, 2015, Conversation
40 Comp. hp, excess heat 3 MW | 6. Hybrid Energi, 2015, Conversation
40 Comp. hp, excess heat 3 MW | 7. Innoterm, 2015, Conversation
40 Comp. hp, excess heat 3 MW | 8. Cronborg, 2015, Conversation
40 Comp. hp, excess heat 3 MW | 9. Johnson Controls, 2019, Conversation
40 Comp. hp, excess heat 3 MW | 10. Teknologisk Institut, 2015, 2019, Conversation
40 Comp. hp, excess heat 3 MW | 11. Energinet.dk, 2015, Conversation
40 Comp. hp, excess heat 3 MW | 12. IEA 2012, Energy Technology Perspectives, 2012
40 Comp. hp, excess heat 3 MW | 13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
40 Comp. hp, excess heat 3 MW | 14. IES/Victor DST, 2019, Conversation
40 Comp. hp, excess heat 3 MW | 15. PlanEnergi, 2019, practical experience from installed plants
40 Comp. hp, excess heat 3 MW | 16. DMI, 2019
40 Comp. hp, excess heat 3 MW | 17. Danfoss, 2019, Conversation
40 Comp. hp, excess heat 3 MW | 18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmev...
40 Comp. hp, excess heat 10 MW | 1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
40 Comp. hp, excess heat 10 MW | 2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
40 Comp. hp, excess heat 10 MW | 3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
40 Comp. hp, excess heat 10 MW | 4. Scandinavian Energy Group, 2015, Conversation
40 Comp. hp, excess heat 10 MW | 5. Advansor, 2015, Conversation
40 Comp. hp, excess heat 10 MW | 6. Hybrid Energi, 2015, Conversation
40 Comp. hp, excess heat 10 MW | 7. Innoterm, 2015, Conversation
40 Comp. hp, excess heat 10 MW | 8. Cronborg, 2015, Conversation
40 Comp. hp, excess heat 10 MW | 9. Johnson Controls, 2019, Conversation
40 Comp. hp, excess heat 10 MW | 10. Teknologisk Institut, 2015, 2019, Conversation
40 Comp. hp, excess heat 10 MW | 11. Energinet.dk, 2015, Conversation
40 Comp. hp, excess heat 10 MW | 12. IEA 2012, Energy Technology Perspectives, 2012
40 Comp. hp, excess heat 10 MW | 13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
40 Comp. hp, excess heat 10 MW | 14. IES/Victor DST, 2019, Conversation
40 Comp. hp, excess heat 10 MW | 15. PlanEnergi, 2019, practical experience from installed plants
40 Comp. hp, excess heat 10 MW | 16. DMI, 2019
40 Comp. hp, excess heat 10 MW | 17. Danfoss, 2019, Conversation
40 Comp. hp, excess heat 10 MW | 18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmev...
40 Comp. hp, seawater 20 MW | 1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
40 Comp. hp, seawater 20 MW | 2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
40 Comp. hp, seawater 20 MW | 3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
40 Comp. hp, seawater 20 MW | 4. Scandinavian Energy Group, 2015, Conversation
40 Comp. hp, seawater 20 MW | 5. Advansor, 2015, Conversation
40 Comp. hp, seawater 20 MW | 6. Hybrid Energi, 2015, Conversation
40 Comp. hp, seawater 20 MW | 7. Innoterm, 2015, Conversation
40 Comp. hp, seawater 20 MW | 8. Cronborg, 2015, Conversation
40 Comp. hp, seawater 20 MW | 9. Johnson Controls, 2019, Conversation
40 Comp. hp, seawater 20 MW | 10. Teknologisk Institut, 2015, 2019, Conversation
40 Comp. hp, seawater 20 MW | 11. Energinet.dk, 2015, Conversation
40 Comp. hp, seawater 20 MW | 12. IEA 2012, Energy Technology Perspectives, 2012
40 Comp. hp, seawater 20 MW | 13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
40 Comp. hp, seawater 20 MW | 14. IES/Victor DST, 2019, Conversation
40 Comp. hp, seawater 20 MW | 15. PlanEnergi, 2019, practical experience from installed plants
40 Comp. hp, seawater 20 MW | 16. DMI, 2019
40 Comp. hp, seawater 20 MW | 17. Danfoss, 2019, Conversation
40 Comp. hp, seawater 20 MW | 18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmev...
40 Absorption heat pump, DH | 3. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, 2014, see http://www.planenergi.dk/varmepumper/
40 Absorption heat pump, DH | 4. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, 2013
40 Absorption heat pump, DH | 13. Scandinavian Energy Group, 2015
40 co2. hp, seawater 50-100 MW | 1. Interview with DIN Forsyning
41 Electric boiler, small | 1. Tjæreborg Industri, 2016
41 Electric boiler, small | 2. Parat, unknown date, Brochure High Voltage Electrode Boiler, available at http://parat.no/media/201154/Electrode-Boiler-web.pdf
41 Electric boiler, large | 1. Tjæreborg Industri, 2016
41 Electric boiler, large | 2. Parat, unknown date, Brochure High Voltage Electrode Boiler, available at http://parat.no/media/201154/Electrode-Boiler-web.pdf
44 Natural Gas DH Only | 1. DGC efficiency and emission test reports from district heating boilers, 2014
44 Natural Gas DH Only | 2. Burner and boiler manufacturer informations, 2015
44 Natural Gas DH Only | 3. Danish District Heating Association, data from a 2012 survey for the report
44 Natural Gas DH Only | 7. National Environmental Research Institute, Denmark 2009
44 Natural Gas DH Only | 8. Elsam/Elkraft update "Teknologidata for el- og varmeproduktionsanlæg", 1997
44 Natural Gas DH Only | 9. DGC calculations, estimates
45.1.a Geothermal DH, 1200m, E | 1. PlanEnergi, GEUS, 2019
45.1.a Geothermal DH, 1200m, E | 2. Data collected from European energy projects
45.1.a Geothermal DH, 1200m, E | 3. Thisted District Heating, Personal Communication
45.1.a Geothermal DH, 1200m, E | 4. Energy Technology Data Catalogue, June 2019
45.1.a Geothermal DH, 1200m, E | 5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
45.1.a Geothermal DH, 1200m, E | 6. Technology Catalogue, Ch. 40 (2020)
45.1.a Geothermal DH, 1200m, E | 7. Input from APMH March 2020 (drilling costs variations with depth)
45.1.b Geothermal DH, 2000m, E | 1. PlanEnergi, GEUS, 2019
45.1.b Geothermal DH, 2000m, E | 2. Data collected from European energy projects
45.1.b Geothermal DH, 2000m, E | 3. Thisted District Heating, Personal Communication
45.1.b Geothermal DH, 2000m, E | 4. Energy Technology Data Catalogue, June 2019
45.1.b Geothermal DH, 2000m, E | 5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
45.1.b Geothermal DH, 2000m, E | 6. Technology Catalogue, Ch. 40 (2020)
45.1.b Geothermal DH, 2000m, E | 7. Input from APMH March 2020 (drilling costs variations with depth)
45.2.a Geothermal DH, 1200m, A | 1. PlanEnergi, GEUS, 2019
45.2.a Geothermal DH, 1200m, A | 2. Data collected from European energy projects
45.2.a Geothermal DH, 1200m, A | 3. Thisted District Heating, Personal Communication
45.2.a Geothermal DH, 1200m, A | 4. Energy Technology Data Catalogue, June 2019
45.2.a Geothermal DH, 1200m, A | 5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
45.2.a Geothermal DH, 1200m, A | 6. Technology Catalogue, Ch. 40 (2020)
45.2.a Geothermal DH, 1200m, A | 7. Input from APMH March 2020 (drilling costs variations with depth)
45.2.b Geothermal DH, 2000m, A | 1. PlanEnergi, GEUS, 2019
45.2.b Geothermal DH, 2000m, A | 2. Data collected from European energy projects
45.2.b Geothermal DH, 2000m, A | 3. Thisted District Heating, Personal Communication
45.2.b Geothermal DH, 2000m, A | 4. Energy Technology Data Catalogue, June 2019
45.2.b Geothermal DH, 2000m, A | 5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
45.2.b Geothermal DH, 2000m, A | 6. Technology Catalogue, Ch. 40 (2020)
45.2.b Geothermal DH, 2000m, A | 7. Input from APMH March 2020 (drilling costs variations with depth)
45.3.a Geoth. DH, 1200m, E (LT) | 1. PlanEnergi, GEUS, 2019
45.3.a Geoth. DH, 1200m, E (LT) | 2. Data collected from European energy projects
45.3.a Geoth. DH, 1200m, E (LT) | 3. Thisted District Heating, Personal Communication
45.3.a Geoth. DH, 1200m, E (LT) | 4. Energy Technology Data Catalogue, June 2019
45.3.a Geoth. DH, 1200m, E (LT) | 5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
45.3.a Geoth. DH, 1200m, E (LT) | 6. Technology Catalogue, Ch. 40 (2020)
45.3.a Geoth. DH, 1200m, E (LT) | 7. Input from APMH March 2020 (drilling costs variations with depth)
45.3.b Geoth DH, 2000m, E (LT) | 1. PlanEnergi, GEUS, 2019
45.3.b Geoth DH, 2000m, E (LT) | 2. Data collected from European energy projects
45.3.b Geoth DH, 2000m, E (LT) | 3. Thisted District Heating, Personal Communication
45.3.b Geoth DH, 2000m, E (LT) | 4. Energy Technology Data Catalogue, June 2019
45.3.b Geoth DH, 2000m, E (LT) | 5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
45.3.b Geoth DH, 2000m, E (LT) | 6. Technology Catalogue, Ch. 40 (2020)
45.3.b Geoth DH, 2000m, E (LT) | 7. Input from APMH March 2020 (drilling costs variations with depth)
45.4 Geothermal DH, E lar scale | 1. PlanEnergi, GEUS, 2019
45.4 Geothermal DH, E lar scale | 2. Input from Innargi Nov 2021 - One case scenario
45.4 Geothermal DH, E lar scale | 3. Thisted District Heating, Personal Communication
45.4 Geothermal DH, E lar scale | 4. Energy Technology Data Catalogue, June 2019
45.4 Geothermal DH, E lar scale | 5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
45.4 Geothermal DH, E lar scale | 6. Technology Catalogue, Ch. 40 (2020)
45.4 Geothermal DH, E lar scale | 7. Input from APMH March 2020 (drilling costs variations with depth)
46 Solar District Heating | 4. Solar Heating plants in Denmark, Simon Furbo, Bengt Perers and Federico Bava, Department of Civil Engineering, Technical University of Denmark. The projected outputs for 2020, 2030 and 2050 are not from this reference.
46 Solar District Heating | 16. Arcon-Sunmark, personal communication. The projected costs are not from this reference, but estimated based on two components; the lower specific costs of larger plants in 2015 and increased competition among suppliers and more efficient production of solar panels.
46 Solar District Heating | 17. "Life expectancy of solar collectors in solar district heating systems", Department of Civil Engineering, Technical University of Denmark, 2009.
46 Solar District Heating | 18. "Recommendation1: Converting solar thermal collector area into installed capacity (m2 to kWth) ", Solar Heaing and Cooling programme, IEA , 2004.
50 Diesel engine farm | 1. Interview with Rolls Royce Power Systems
50 Diesel engine farm | 2. C. Breyer. Fuel-Parity: New very large and sustainable market segments for PV systems. 2010
50 Diesel engine farm | 3. National Grid. Short Term Operating Reserve - Carbon intensity report. 2016
50 Diesel engine farm | 4. EEA. Distributed Generation Operational Reliability and Availability Database. 2004
50 Diesel engine farm | 5. Maintenance schedule Caterpillar Emergency generator. Available at: https://ae.usembassy.gov/wp-content/uploads/sites/254/2017/06/stc12017q0002_post-provided-generator-checklist.pdf
50 Diesel engine farm | 6. Interview with UK manufacturer: Edina Power UK
50 Diesel engine farm | 7. Warstsila. White paper - Combustion engine power plants. 2011
50 Diesel engine farm | 8. Institut for Miljøvidenskab. Emission factors. Available at: http://envs.au.dk/videnudveksling/luft/emissioner/emission-factors/
50 Diesel engine farm | 9. Timera Energy. Investment in UK peaking assets. Available at: www.timera-energy.com/investment-in-uk-peaking-assets
50 Diesel engine farm | 10. UK Department for Business, Energy and Industrial Strategy. Electricity Generation Cost. November 2016
50 Diesel engine farm | 11. EUGINE (European Engine Power Plants Association) questionnaire to their members. Data presented in "Flexibility Needs and Options for Europe's Future Electricity System", Energy Brainpool, September 2017.
50 Diesel engine farm | 12. BEIS. Electricity Generation cost. November 2016
50 Diesel engine farm | 13. LAZARD. Levelized cost of energy analysis v11. November 2017
51 Natural gas engine plant | 1. Wartsila. Power Plant solutions 2016
51 Natural gas engine plant | 2. Main technology catalogue: Technology Data for Energy Plants - August 2016
51 Natural gas engine plant | 3. EEA. Distributed Generation Operational Reliability and Availability Database. 2004
51 Natural gas engine plant | 4. Kiisa Power plant project for Elering
51 Natural gas engine plant | 5. Warstsila. White paper - Combustion engine power plants. 2011
51 Natural gas engine plant | 6. D. Santoianni. Defining true flexibility - a comparison of gas-fired power generating technologies. 2015
51 Natural gas engine plant | 7. Phone interview with Wartsila
51 Natural gas engine plant | 8. Institut for Miljøvidenskab. Emission factors. Available at: http://envs.au.dk/videnudveksling/luft/emissioner/emission-factors/
51 Natural gas engine plant | 9. UK Department for Business, Energy and Industrial Strategy. Electricity Generation Cost. November 2016
51 Natural gas engine plant | 10. EUGINE (European Engine Power Plants Association) questionnaire to their members. Data presented in "Flexibility Needs and Options for Europe's Future Electricity System", Energy Brainpool, September 2017.
51 Natural gas engine plant | 11. BEIS. Electricity Generation cost. November 2016
51 Natural gas engine plant | 12. LAZARD. Levelized cost of energy analysis v11. November 2017
52 OCGT - Natural gas | 1. GE - Aeroderivative turbines product brochures.
52 OCGT - Natural gas | 2. Siemens - Aeroderivative turbine brochures
52 OCGT - Natural gas | 3. Main technology catalogue: Technology Data for Energy Plants - August 2016
52 OCGT - Natural gas | 4. EEA. Distributed Generation Operational Reliability and Availability Database. 2004
52 OCGT - Natural gas | 5. M. Welch, T.Krol. Flexible Power Generation for Grid Support utilizing Aero-derivative Gas Turbine Technology. 2016
52 OCGT - Natural gas | 6. EU Turbines. Gas and Steam Turbines Solutions for a sustainable energy mix (brochure). 2017
52 OCGT - Natural gas | 7. Forrsa Power plant for Fingrid. Available at: www.fingrid.fi/en/pages/news/news/2013/fingrids-new-reserve-power-plant-inaugurated-in-forssa/
52 OCGT - Natural gas | 8. Agora Energiwende. Flexibility in thermal power plants. 2017
52 OCGT - Natural gas | 9. Energy Brainpool. Flexibility Needs and Options for Europe's Future Electricity System. September 2017.
52 OCGT - Natural gas | 10. Phone interview with Siemens Turbomachinery UK
52 OCGT - Natural gas | 11. Institut for Miljøvidenskab. Emission factors. Available at: http://envs.au.dk/videnudveksling/luft/emissioner/emission-factors/
52 OCGT - Natural gas | 12. ESMAP. Technical paper: Study of Equipment Prices in the Power Sector. 2009
52 OCGT - Light fuel oil | 11. Institut for Miljøvidenskab. Emission factors. Available at: http://envs.au.dk/videnudveksling/luft/emissioner/emission-factors/
52 OCGT - Light fuel oil | 18. Phone interview with Siemens Turbomachinery UK
52 OCGT - Light fuel oil | 19. Forrsa Power plant for Fingrid. Available at: www.fingrid.fi/en/pages/news/news/2013/fingrids-new-reserve-power-plant-inaugurated-in-forssa/
52 OCGT - Light fuel oil | 20. ESMAP. Technical paper: Study of Equipment Prices in the Power Sector. 2009

## 01 Coal CHP
Technology |  | Coal power plant, supercritical - extraction - coal - medium
year |  | 2015 | 2020 | 2030 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 500 | 500 | 500 | 500
| Electrical efficiency (net, name plate) [] | 46% | 48.5% | 52% | 53.5% | C | [8, 7, 9, 11]
| Cb coefficient (50°C/100°C) | 0.75 | 0.84 | 1.01 |  | A
| Cv coefficient (50°C/100°C) | 0.15 | 0.15 | 0.15 |  |  | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 |  | 6
| Construction time [years] | 4.5 | 4.5 | 4.5 |  |  | [2, 3, 3]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 5% | 5% | 5% | D | 14
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | D | 14
| Minimum load (of full load) [] | 18% | 15% | 15% | 10% |  | [10, 14]
Environment
| SO2 (degree of desulphuring) [] | 97% | 97% | 97% | 97% | B | 5
| NOX [g/GJ_i] | 38 | 35 | 35 | 35 | B | [12, 5, 5, 5]
| CH4 [g/GJ_i] | 1.5 | 1.5 | 1.5 | 1.5 |  | [13, 5, 5, 5]
| N2O [g/GJ_i] | 0.8 | 0.8 | 0.8 | 0.8 |  | [13, 5, 5, 5]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 2.1824 | 2.1484 | 2.1032 | 2.0128 | J | [17, 18, 19, 20, 21, 22]
| Variable O&M (*total) [EUR/MWh_e] | 3.3357 | 3.2792 | 3.2114 | 3.0757 | J | [17, 18, 19, 20, 21, 22]
| Fixed O&M (*total) [EUR/MW_e/y] | 35618.9884 | 35053.6077 | 34324.4022 | 32911.1764 | J | [17, 18, 19, 20, 21, 22]
Technology-specific data
| Availability [] | 95% | 95% | 95% |  | E | 7
Notes:
A. The Cb values have been calculated from the electricity efficiencies in condensation mode, the Cv values and a total efficiency (electricity plus heat) in full back-pressure mode of 90%. Cf. Annex 1.
B. The data for SO2 and NOx emissions assume flue gas desulphurisation (wet gypsum) and DeNOx equipment of the "high dust" SCR type.
C. Supercritical in 2010 and ultra-supercritical from 2020.
D. Please refer to section 'Regulation ability' in the above qualitative description.
E. Outage rates are generally about 5% for plants that are 10-20 years old. Unless the plant is refurbished, the rate increases to 20% for plants that are 40 years old (ref. 7)
F. It is assumed that the cost is falling by 0.2 % p.a. Defaltor 2011-2015: 1.059
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Elsam, November 2003
2. Elsam's and Elkraft's update of the Danish Energy Agency's 'Teknologidata for el- og varmeproduktionsanlæg', December 1997
3. Eltra, September 2003
5. Danish Energy Agency, 2009.
6. "Projected costs of generating electricity", International Energy Agency (IEA), 2005.
7. "Energy technology perspectives 2008", International Energy Agency, 2008.
8. Danish Energy Agency, 2008. Measured data (1994-2006) from newest power plants in Denmark.
9. Own estimate by Danish Energy Agency and Energinet.dk, 2011.
10. Energinet.dk, 2009
11. www.ad700.dk
12. "En opdateret analyse af Danmarks muligheder for at reducere emissionerne af NOx" (Updated analysis of Denmark's options to reduce NOx emissions; in Danish), Danish Environmental Protection Agency, 2009.
13. National Environmental Research Institute, Denmark, 2009 (data from 2007).
14. DONG Energy, 2009.
15. "UK Electricity Generation Costs Update", Mott MacDonald, June 2010.
16. "The Costs of CO2 Capture, Transport and Storage", Zero Emissions Platform (ZEP), July 2011
17. The IEA World Energy Outlook 2014 coal fired Ultra-supercritical power plants in Europe. Values used are the projection for 2020.
18. The IEA Projected Cost of Generating Electricity 2015 for coal fired power plants. Here both the 'world median' is used, and data from recently commissioned plants in the Netherlands. The three units in the Netherlands are chosen because of the proximity to Denmark, because the socio-economic parameters (labour cost etc) are assumed to be similar and because the units are new (all from 2015).
19. EIA Updated Capital Cost Estimates for Utility Scale Electricity Generating Plants 2013 for pulverizes coal fired advanced single units.[1]
20. Aggregated data from different projects on existing units that Ea Energy Analyses have been working on since 2010. Data is used for estimating O&M costs.
21. IEA( 2016),Energy Technology Perspectives
22. E.S. Rubin et al. / Energy Policy 86 (2015) page 198-218, A review of learning rates for electricity supply technologies

## 02 LTE existing plant
Technology |  | Life time extension of coal extraction plant - refurbish - coal - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 300 | 300 | 300 |  | 200 | 400 | 200 | 400
| Electrical efficiency (net, annual average, additional to existing plant) [] | 0% | 0% | 0% |  | -1% | 1% |  |  | [E, F] | 7
| Electrical efficiency (net, name plate, additional to existing plant) [] | 0% | 0% | 0% |  | -1% | 1% |  |  | [E, F] | 7
| Cb coefficient (50°C/100°C, additional to existing plant) | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, F] | 7
| Cv coefficient (50°C/100°C, additional to existing plant) | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, F] | 7
| Forced outage (additional to existing plant) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | [A, F] | 7
| Planned outage (additional to existing plant) [weeks per year] | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, F] | 7
| Technical lifetime [years] | ctrl: 15; ctrl: 15; ctrl: 15; -: [4, 5, 6, 7]
| Construction time [years] | ctrl: 0.5; ctrl: 0.5; ctrl: 0.5; -: 7
| Space requirement (additional to existing plant) [1000 m2/MW_e] | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, F]
Regulation ability
| Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | [A, F] | 7
| Secondary regulation (of full load, additional to existing plant, per minute) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | [A, F] | 7
| Minimum load (of full load, additional to existing plant) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | [A, F] | 7
| Warm start-up time (additional to existing plant) [hours] | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, F] | 7
| Cold start-up time (additional to existing plant) [hours] | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, F] | 7
Environment
| SO2 (degree of desulphuring, additional to existing plant) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | [A, F, G] | 8
| NOX (additional to existing plant) [g/GJ_i] | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, F, G] | 8
| CH4 (additional to existing plant) [g/GJ_i] | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, F, G] | 8
| N2O (additional to existing plant) [g/GJ_i] | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, F, G] | 8
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 0.25521 | 0.25521 | 0.25521 | 0 | 0.15951 | 0.36155 | 0 | 0 | [C, F] | [4, 5, 6, 7]
| Nominal investment (equipment) [MEUR/MW_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nominal investment (installation) [MEUR/MW_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [A, D, F] | 7
| Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | 0 | 0 | 0 | 0 | 0 | 8506.9817 | 0 | 0 | [A, B, F] | 7
Technology-specific data
Notes:
A. Values will generally be similar to those of the plant prior to Life Time Extention (LTE).
B. Values will depend on those of the plant prior to LTE, however the average fixed O&M cost may increase slightly for the extension period compared with the original life time to accomodate the necessary reinvestments during the extended life time.
C. Investment costs will vary largely, depending on the necessary scope of work. The indicated range represents typical cases where 20-25 years Danish coal power CHP plants have been life time extended to obtain additional 15 years life time (based mainly on budgetted values).
D. Variable O&M costs will in general be similar or a bit smaller to those of the plant prior to LTE. The reason for the small improvement is when you compare it to just before the LTE. When compared to the average over the lifetime the O&M costs will be similar.
E. Values will generally be similar to those of the plant prior to LTE. Average efficiencies over the lifetime will be similar to the plant prior to LTE, but the efficiencies just after the LTE will be better than that of the plant just before the LTE.
F. Values for year 2050 are not considered relevant since new coal fired power plants are not expected to be built
G. It is assumed that plants emissions prior to the LTE is within the legal limits.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
4. Projected Costs of Generating electricity edition 2015, IEA, NEA and OECD 2015
5. Baggrundsnotat omhandlende metode for Energinet.dk's forventninger til kraftværksudviklingen i Danmark, Energinet.dk, 27. august 2014 (Background note concerning method for Energinet.dk's expectations for power plant development in Denmark , Energinet.dk , August 27, 2014)
6. Studstrupværket kører videre på kul frem til 2015, Ingeniøren, 10. maj 2012,( Studstrupværket continues to run on coal until 2015, Engineer , May 10, 2012, )
7. Ea Energy Analysis, based on experience from various commercial projects.
8. It is assumed by Ea Energy Analyses that plants emissions prior to the LTE is within the legal limits.

## 03a Coal to wood pellets exi bo
Technology |  | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 300; ctrl: 300; ctrl: 300; lower: 200; upper: 400
| Electrical efficiency (net, annual average, additional to existing plant) [] | -1% | -1% | -1% |  | 0% | -2% |  |  | [A, B, C, I] | 10
| Electrical efficiency (net, name plate, additional to existing plant) [] | -1% | -1% | -1% |  | 0% | -2% |  |  | [A, B, C, I] | 10
| Cb coefficient (50°C/100°C, additional to existing plant) | -0.02 | -0.02 | -0.02 |  | 0 | -0.05 |  |  | [A, B, C, I] | 10
| Cv coefficient (50°C/100°C, additional to existing plant) | 0 | 0 | 0 |  | -0.01 | 0.01 |  |  | [A, C] | 10
| Forced outage (additional to existing plant) [] | 0% | 0% | 0% |  | -1% | 1% |  |  | A | 10
| Planned outage (additional to existing plant) [weeks per year] | 0 | 0 | 0 |  | 0 | 0 |  |  | A | 10
| Technical lifetime [years] | ctrl: 15; ctrl: 15; ctrl: 15; -: C; -: 10
| Construction time [years] | 2 | 2 | 2 |  | 1.5 | 2.5 |  |  | C | 10
| Space requirement (additional to existing plant) [1000 m2/MW_e] | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, D]
Regulation ability
| Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | A | 10
| Secondary regulation (of full load, additional to existing plant, per minute) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | A | 10
| Minimum load (of full load, additional to existing plant) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | A | 10
| Warm start-up time (additional to existing plant) [hours] | 0 | 0 | 0 |  | 0 | 0 |  |  | A | 10
| Cold start-up time (additional to existing plant) [hours] | 0 | 0 | 0 |  | 0 | 0 |  |  | A | 10
Environment
SO2 (degree of desulphuring) [] | bar: -
| NOX [g/GJ_i] | 20 | 21 | 18 |  | 19 | 53 |  |  | G
| CH4 [g/GJ_i] | 0 | 0 | 0 |  | 3.1 | 3.1 |  |  | G
| N2O [g/GJ_i] | 1 | 1 | 1 |  | 0.8 | 0.8 |  |  | G
| Particles [g/GJ_i] | ctrl: 0.3; ctrl: 0.3; ctrl: 0.3
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 0.53169 | 0.53169 | 0.53169 | 0 | 0.37218 | 0.8507 | 0 | 0 | [C, E, K] | [10, 11, 12]
| Nominal investment (equipment) [MEUR/MW_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nominal investment (installation) [MEUR/MW_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | 0.95704 | 0.95704 | 0.95704 | 0 | 0.42535 | 1.4887 | 0 | 0 | [A, F, K] | 10
| Fixed O&M [EUR/MWe/year] | 3562.2986 | 3562.2986 | 3562.2986 | 0 | 1435.5532 | 5689.044 | 0 | 0 | [A, F, K] | 10
Technology-specific data
| Variable O&M (*total, additional to existing plantl) [EUR/MWh_i] | 0.36 | 0.36 | 0.36 |  | 0.16 | 0.56 |  |  | [A, F, K] | 10
| Fixed O&M (*total, additional to existing plant) [EUR/MW_i/y] | 1350 | 1350 | 1350 |  | 550 | 2150 |  |  | [A, F, K] | 10
Notes:
A. Value depend on the original plant. Value indicate the estimated change from the original value (unit is the same as the paramter).
B. Typically the electricity efficiency will be 1-2 % point lower than that of the plant prior to conversion. The thermal efficiency is typically unchanged, thus the Cb value decreases, meaning more heat is produced compared to electricity.
C. Values for year 2050 are not considered relevant since it is assumed that all coal fired plants in Denmark have been rebuilt or decommissioned.
D. Some additional under roof space (or silos) will be required for storage of pellets compared to coal (estimated 50%-100% extra m3 storage). But not more floor space (m2).
E. The nominal investment assumes that the original plant is aged and therefore include investment for a general life time extension campaign
F. The variable O&M costs will be similar to those of the original plant, however fixed O&M costs are likely to increase by 10-20%
G. Assumed the same emission values from the datasheet of new biomass plants (wood chips). See references and notes in the datasheet '09 Biomass CHP, Steam Turbine - Large steam turbine, Woodchips'.
I. It is assumed that plants that are refurbished in 2015 have an electric efficiency of 41% and a CB coefficient of 0.556. Plants refurbished in 2020 have an electric efficiency of 42% and a CB coefficient of 0.64. Plants refurbished in 2030 have an electric efficiency of 44% and a CB coefficient of 0.77. The estimates are made based on Danish CHP plants that are commissioned in 1990, 1995 and 2005.
J. It is assumed that that Flue Gas Desulphurization plant is bypassed (stopped) due to low Sulphur content in wood pellet fuel
K. O&M cost and CAPEX has been estimated by Ramboll in April 2019 based on input from DE/Ørsted and data from UK Department for Business, Energy & Industry strategy (BEIS) in their Electricity Generation Cost report from 2016.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
10. Ea Energy Analysis, based on experience from various commercial projects.
11. Government response to the consultation on proposals for the levels of banded support under the Renewables Obligation for the period 2013-17 and the Renewables Obligation Order 2012, UK Department of Energy and Climate Change, July 2012.
12. A strategy for converting coal fueled power plants to biomass, Future Metrics, September 2014

## 03b Coal to wood chips n. boile
Technology |  | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 300; ctrl: 300; ctrl: 300; lower: 200; upper: 400
| Electrical efficiency (net, annual average, additional to existing plant) [] | -1% | -1% | -1% |  | 0% | -2% |  |  | [A, B, J] | 10
| Electrical efficiency (net, name plate, additional to existing plant) [] | -1% | -1% | -1% |  | 0% | -2% |  |  | [A, B, J] | 10
| Cb coefficient (50°C/100°C, additional to existing plant) | -0.07 | -0.07 | -0.07 |  | -0.02 | -0.1 |  |  | [A, B, J] | 10
| Cv coefficient (50°C/100°C, additional to existing plant) | 0 | 0 | 0 |  | -0.01 | 0.01 |  |  | A | 10
| Forced outage (additional to existing plant) [] | 0% | 0% | 0% |  | -1% | 1% |  |  | A | 10
| Planned outage (additional to existing plant) [weeks per year] | 0 | 0 | 0 |  | 0 | 0 |  |  | A | 10
| Technical lifetime [years] | ctrl: 15; ctrl: 15; ctrl: 15; -: C; -: 10
| Construction time [years] | 2.5 | 2.5 | 2.5 |  | 2 | 3 |  |  | C | 10
| Space requirement (additional to existing plant) [1000 m2/MW_e] | 0.03 | 0.03 | 0.03 |  | 0.02 | 0.05 |  |  | [A, D] | 10
Regulation ability
| Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | -2% | 0% | 0% |  | 0% | -5% |  |  | [A, I] | 10
| Secondary regulation (of full load, additional to existing plant, per minute) [] | -2% | 0% | 0% |  | 0% | -5% |  |  | [A, I] | 10
| Minimum load (of full load, additional to existing plant) [] | 0.05% | 0.05% | 0% |  | 0% | 0.1% |  |  | A | 10
| Warm start-up time (additional to existing plant) [hours] | 0.5 | 0.5 | 0 |  | 0 | 2 |  |  | [A, I] | 10
| Cold start-up time (additional to existing plant) [hours] | 1 | 1 | 1 |  | 0 | 2 |  |  | [A, I] | 10
Environment
| SO2 (degree of desulphuring) [] | ctrl: 98%; ctrl: 98%; ctrl: 98%
| NOX [g/GJ_i] | 30 | 24 | 20 |  | 19 | 53 |  |  | G
| CH4 [g/GJ_i] | 3 | 2 | 2 |  | 0 | 0.5 |  |  | G
| N2O [g/GJ_i] | 10 | 8 | 6 |  | 2 | 20 |  |  | G
| Particles [g/GJ_i] | ctrl: 0.3; ctrl: 0.3; ctrl: 0.3
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 1.712 | 1.712 | 1.712 | 0 | 1.4249 | 2.2863 | 0 | 0 | [C, E] | [10, 12]
| Nominal investment (equipment) [MEUR/MW_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nominal investment (installation) [MEUR/MW_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [EUR/MWh_e] | 2.9243 | 2.9243 | 2.9243 | 0 | 1.8609 | 3.9876 | 0 | 0 | [F, K] | 10
| Fixed O&M (*total) [EUR/MW_e/y] | 78423.738 | 78423.738 | 78423.738 | 0 | 65131.579 | 91715.8969 | 0 | 0 | [F, K] | 10
Technology-specific data
| Variable O&M (*total) [EUR/MWh_i] | 1.1 | 1.1 | 1.1 |  | 0.7 | 1.5 |  |  | [F, K] | 10
| Fixed O&M (*total) [EUR/MW_i/y] | 29500 | 29500 | 29500 |  | 24500 | 34500 |  |  | [F, K] | 10
Notes:
A. Value depend on the original plant.
B. Typically the electricity efficiency will be 1-2 % point lower than that of the plant prior to conversion. The thermal efficiency will typically increase to around 105%. thus the Cb value decreases. meaning more heat is produced compared to electricity. This is mainly due to implementation of exhaust gas condenser.
C. Values for year 2050 are not considered relevant since it is assumed that all coal fired plants in Denmark have been rebuilt or decommissioned.
D. Some additional space will be required for storage of chips (estimated 50%-100% extra).
E. The nominal investment assumes that the original plant is aged and therefore include investment for a general life time extension campaign
F. The fixed O&M costs are likely to increase by 10-20%. whereas the variable O&M costs are likely to increase approx. 50%.
G. Emission values from the datasheet of new CFB biomass plants. See references and notes in the datasheet 'Large Biomass Circulating Fluidized Bed Combustion Systems (CFBC) for wood'.
I. The regulation time of the boiler will often increase due to slower burning of chips compared to pulverized fuel. Depending of the other thermal limitations in the cycle (e.g. in the turbines) this will have no change or an increase in the regulation time.
J. It is assumed that plants that are refurbished in 2015 have an electric efficiency of 41% and a CB coefficient of 0.56. Plants refurbished in 2020 have an electric efficiency of 42% and a CB coefficient of 0.64. Plants refurbished in 2030 have an electric efficiency of 44% and a CB coefficient of 0.77. The estimates are made based on Danish CHP plants that are commissioned in 1990, 1995 and 2005.
K. O&M cost are copied from 09 Large Wood Chip CHP corrected with efficiency. Note that all financial data are absolute values and not relative to coal.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
10. Ea Energy Analysis. based on experience from various commercial projects.
12. A strategy for converting coal fueled power plants to biomass. Future Metrics. September 2014

## 03c coal to wood chips exi. boi
Technology |  | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 300; ctrl: 300; ctrl: 300; lower: 200; upper: 400
| Electrical efficiency (net, annual average, additional to existing plant) [] | -3% | -3% | -3% |  | -2% | -4% |  |  | [A, B, I] | 10
| Electrical efficiency (net, name plate, additional to existing plant) [] | -3% | -3% | -3% |  | -2% | -4% |  |  | [A, B, I] | 10
| Cb coefficient (50°C/100°C, additional to existing plant) | -0.07 | -0.07 | -0.07 |  | -0.02 | -0.1 |  |  | [A, B, I] | 10
| Cv coefficient (50°C/100°C, additional to existing plant) | 0 | 0 | 0 |  | -0.01 | 0.01 |  |  | A | 10
| Forced outage (additional to existing plant) [] | 0% | 0% | 0% |  | -1% | 1% |  |  | A | 10
| Planned outage (additional to existing plant) [weeks per year] | 0 | 0 | 0 |  | 0 | 0 |  |  | A | 10
| Technical lifetime [years] | ctrl: 15; ctrl: 15; ctrl: 15; -: C; -: 10
| Construction time [years] | 2 | 2 | 2 |  | 1.5 | 2.5 |  |  | C | 10
| Space requirement (additional to existing plant) [1000 m2/MW_e] | 0.04 | 0.04 | 0.04 |  | 0.03 | 0.06 |  |  | [A, D] | 10
Regulation ability
| Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | A | 10
| Secondary regulation (of full load, additional to existing plant, per minute) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | A | 10
| Minimum load (of full load, additional to existing plant) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | A | 10
| Warm start-up time (additional to existing plant) [hours] | 0 | 0 | 0 |  | 0 | 0 |  |  | A | 10
| Cold start-up time (additional to existing plant) [hours] | 0 | 0 | 0 |  | 0 | 0 |  |  | A | 10
Environment
| SO2 (degree of desulphuring) [] | ctrl: 98%; ctrl: 98%; ctrl: 98%; -: G
| NOX [g/GJ_i] | 30 | 24 | 20 |  | 19 | 53 |  |  | G
| CH4 [g/GJ_i] | 3 | 2 | 2 |  | 3.1 | 3.1 |  |  | G
| N2O [g/GJ_i] | 10 | 8 | 6 |  | 0.8 | 0.8 |  |  | G
| Particles [g/GJ_i] | ctrl: 0.3; ctrl: 0.3; ctrl: 0.3; -: G
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 1.712 | 1.712 | 1.712 | 0 | 1.4249 | 2.2863 | 0 | 0 | [C, E] | 10
| Nominal investment (equipment) [MEUR/MW_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nominal investment (installation) [MEUR/MW_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total, additional to existing plant) [EUR/MWh_e] | 1.5951 | 1.5951 | 1.5951 | 0 | 1.0634 | 2.1267 | 0 | 0 | F | 10
| Fixed O&M (*total, additional to existing plant) [EUR/MW_e/y] | 15073.3083 | 15073.3083 | 15073.3083 | 0 | 13398.4962 | 16748.1203 | 0 | 0 | F | 10
Technology-specific data
Notes:
A. Value depend on the original plant.
B. Typically the electricity efficiency will be 3-4 % point lower than that of the plant prior to conversion. The thermal efficiency is increased to approximately 100% because of flue gas condensation in drying process, thus the Cb value decreases, meaning more heat is produced compared to electricity.
C. Values for year 2050 are not considered relevant since it is assumed that all coal fired plants in Denmark have been rebuilt or decommissioned.
D. Some additional space will be required for storage of chips (estimated 50%-100% extra) and for the drying plant.
E. The nominal investment assumes that the original plant is aged and therefore include investment for a general life time extension campaign
F. Both variable and fixed O&M costs are likely to increase by 40-50% from the original plant.
G. Assumed the same emission values from the datasheet of new biomass plants (wood chips). See references and notes in the datasheet '09 Biomass CHP, Steam Turbine - Large steam turbine, Woodchips'.
I. It is assumed that plants that are refurbished in 2015 have an electric efficiency of 41% and a CB coefficient of 0.57. Plants refurbished in 2020 have an electric efficiency of 42% and a CB coefficient of 0.64. Plants refurbished in 2030 have an electric efficiency of 44% and a CB coefficient of 0.77. The estimates are made based on Danish CHP plants that are commissioned in 1990, 1995 and 2005.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
10. Ea Energy Analysis, based on experience from various commercial projects.

## 03d coal to wood chips exi. boi
Technology |  | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 70; lower: 50; upper: 90; -: [A, E]; -: 13
| Electrical efficiency (net, annual average) [] | ctrl: 0.27%; -: B; -: 13
| Electrical efficiency (net, name plate) [] | -: 13
| Cb coefficient (50°C/100°C) | ctrl: 0.35; -: B; -: 13
| Cv coefficient (50°C/100°C) | -: 13
| Forced outage [] | ctrl: 3%; -: C; -: 13
| Planned outage [weeks per year] | ctrl: 1.56; -: C; -: 13
| Technical lifetime [years] | ctrl: 15
Construction time [years]
Space requirement [1000 m2/MW_e]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | ctrl: 2%; -: C; -: 13
| Secondary regulation (of full load, per minute) [] | ctrl: 3%; -: C; -: 13
| Minimum load (of full load) [] | ctrl: 45%; -: C; -: 13
| Warm start-up time [hours] | ctrl: 2; -: C; -: 13
| Cold start-up time [hours] | ctrl: 12; -: C; -: 13
Environment
SO2 (degree of desulphuring) []
| NOX [g/GJ_i] | ctrl: 30; -: C; -: 13
| CH4 [g/GJ_i] | ctrl: 3; -: C; -: 13
| N2O [g/GJ_i] | ctrl: 10; -: C; -: 13
| Particles [g/GJ_i] | ctrl: 0.3; -: C; -: 13
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nominal investment (equipment) [MEUR/MW_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nominal investment (installation) [MEUR/MW_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M (*total) [EUR/MWh_e] | 4.3279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D
| Fixed O&M (*total) [EUR/MW_e/y] | 116183.3163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D
Technology-specific data
| Variable O&M (*total) [EUR/MWh_i] | ctrl: 1.1; -: D
| Fixed O&M (*total) [EUR/MW_i/y] | ctrl: 29500; -: D
Notes:
A. Based on existing converted coal plant 50-90 MW capacity
B. The estimated electrcial efficiency is 27 %. It is assumed that plants are equipped with Flue Gas Condensation having total efficiency of 105 %
C. Values are based on Data sheet for Wood Chips CHP, Large
D. O&M data are based data sheet 09 Wood chips CHP, Large, the specific values based on electricity has been corrected base on efficiency
E. Uncertainty estimate applies for 2015 value
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
13. Ramboll, internal assessment

## 04 Gas turb. simple cycle, L
Technology |  | Gas turbine, simple cycle - back pressure - natural gas - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | lower: 40; upper: 125; lower: 40; upper: 125; -: F
| Electrical efficiency (net, name plate) [] | 41% | 42% | 43% | 45% | 38% | 42% | 40% | 44% |  | [6, 12]
| Electrical efficiency (net, annual average) [] | 39% | 40% | 41% | 43% | 36% | 40% | 38% | 42% |  | [6, 11]
| Cb coefficient (50°C/100°C) | 0.95 | 0.96 | 1 | 1 | 0.8 | 1.2 | 0.8 | 1.2 |  | [6, 12]
Cv coefficient (50°C/100°C) | bar: -
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 3% | 2% | 3% |  | 6
| Planned outage [weeks per year] | 3 | 3 | 2.5 | 2.5 | 2 | 3.5 | 1.5 | 3 |  | 6
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 |  | 25 |  | E | [6, 7]
| Construction time [years] | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 2 | 1 | 2 |  | 6
| Space requirement [1000 m2/MW_e] | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.03 | 0.01 | 0.03 | G | 7
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to -
| Secondary regulation (of full load, per minute) [] | 20% | 20% | 20% | 20% | 20% | 50% | 20% | 50% | C | 6
| Minimum load (of full load) [] | 25% | 23% | 20% | 20% | 20% | 25% | 20% | 25% | A | 6
| Warm start-up time [hours] | 0.25 | 0.23 | 0.2 | 0.2 | 0.1 | 0.5 | 0.1 | 0.4 |  | [5, 6, 8]
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 1 | 0.4 | 1 |  | [5, 6, 8]
Environment
SO2 (degree of desulphuring) [] | bar: ctrl to upper
| NOX [g/GJ_i] | 20 | 15 | 10 | 10 | 10 | 30 | 7.5 | 20 | D | [7, 9]
| CH4 [g/GJ_i] | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 8 | 1 | 8 | G | 9
| N2O [g/GJ_i] | 1 | 1 | 1 | 1 | 0.7 | 1.2 | 0.7 | 1.2 | G | 9
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 0.63802 | 0.62739 | 0.59549 | 0.55295 | 0.42535 | 0.95704 | 0.37218 | 0.90387 | 0 | [6, 10]
| Nominal investment (equipment) [MEUR/MW_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | K
| Nominal investment (installation) [MEUR/MW_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | K
| Variable O&M (*total) [EUR/MWh_e] | 4.7852 | 4.6788 | 4.4662 | 4.2535 | 4.2535 | 6.3802 | 3.1901 | 5.3169 | 0 | 6
| Fixed O&M (*total) [EUR/MW_e/y] | 21267.4544 | 20735.768 | 19778.7326 | 19140.7089 | 0 | 0 | 0 | 0 | B | 6
Technology-specific data
Notes:
A. Very low efficiency at low loads and often increased Nox emisison
B. Insurance excluded, unknown. Daily start assumed
C. Power related
D. Based on Dry Low NOx (DLN) techniques
E. Technical- and design life most often > 25 years
F. Electrical output
G. Combined with DGC assumptions, CHP configuration
H. GT's (5 MWe) are available including internal recuperator; the electrical nominal efficiency is then 37 % (LCV basis)
I. No data available, no known use
J. Not relevant for this CHP configuration
K. No data available
L. DGC Estimate
M. Air preheating by internal recuperation included
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
5. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
6. Wärtsila Technical Journal "in detail" 02-2014
7. Data specs from maufacturers (Web) 2015
8. Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
9. Danish Gas Technology Centre, environmental survey 2012
10. Smart Power Generation - The future of electricity production, J. Klimstra & M. Hotakainen 2011
11. IEA: Projected cost of generating electricity, 2010
12. COWI 2015 input
13. The Omes Project results (2005)
14. WBDG-Publication, B. L. Capehart, Microtubines, 2014

## 04 Gas turb. simple cycle Sm-Me
Technology |  | Gas turbine, simple cycle - back pressure - natural gas - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | lower: 5; upper: 40; lower: 5; upper: 40; -: F
| Electrical efficiency (net, name plate) [] | 36% | 37% | 39% | 40% | 32% | 40% | 34% | 42% | [G, H] | [6, 12]
| Electrical efficiency (net, annual average) [] | 34% | 35% | 37% | 38% | 30% | 38% | 32% | 40% |  | [6, 11]
| Cb coefficient (50°C/100°C) | 0.71 | 0.73 | 0.8 | 0.8 | 0.61 | 0.8 | 0.7 | 0.9 |  | [6, 12]
Cv coefficient (50°C/100°C) | bar: -
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 3% | 2% | 3% |  | 6
| Planned outage [weeks per year] | 3 | 2.8 | 2.5 | 2.5 | 2 | 3.5 | 1.5 | 3 |  | 6
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 |  | 25 |  | E | [6, 7]
| Construction time [years] | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 1.5 | 1 | 1.5 |  | 6
| Space requirement [1000 m2/MW_e] | 0.04 | 0.04 | 0.04 | 0.04 | 0.03 | 0.07 | 0.03 | 0.07 | G | 7
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to -
| Secondary regulation (of full load, per minute) [] | 20% | 20% | 20% | 20% | 20% | 50% | 20% | 50% | C | 6
| Minimum load (of full load) [] | 25% | 23% | 20% | 20% | 20% | 25% | 20% | 25% | A | 6
| Warm start-up time [hours] | 0.25 | 0.23 | 0.2 | 0.2 | 0.1 | 0.5 | 0.1 | 0.4 |  | [5, 6, 8]
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 1 | 0.4 | 1 |  | [5, 6, 8]
Environment
SO2 (degree of desulphuring) [] | bar: ctrl to upper
| NOX [g/GJ_i] | 20 | 15 | 10 | 10 | 10 | 30 | 8 | 20 | D | [7, 9]
| CH4 [g/GJ_i] | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 8 | 1 | 8 |  | 9
| N2O [g/GJ_i] | 1 | 1 | 1 | 1 | 0.7 | 1.2 | 0.7 | 1.2 |  | 9
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 0.79753 | 0.77626 | 0.74436 | 0.72309 | 0.63802 | 1.0634 | 0.58485 | 1.0102 | 0 | [6, 10]
| Nominal investment (equipment) [MEUR/MW_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | K
| Nominal investment (installation) [MEUR/MW_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | K
| Variable O&M (*total) [EUR/MWh_e] | 5.8485 | 5.7422 | 5.4232 | 4.8915 | 5.3169 | 7.4436 | 4.2535 | 6.3802 | 0 | 6
| Fixed O&M (*total) [EUR/MW_e/y] | 21267.4544 | 20735.768 | 19778.7326 | 19140.7089 | 0 | 0 | 0 | 0 | B | 6
Technology-specific data
Notes:
A. Very low efficiency at low loads and often increased Nox emisison
B. Insurance excluded, unknown. Daily start assumed
C. Power related
D. Based on Dry Low NOx (DLN) techniques
E. Technical- and design life most often > 25 years
F. Electrical output
G. Combined with DGC assumptions, CHP configuration
H. GT's (5 MWe) are available including internal recuperator; the electrical nominal efficiency is then 37 % (LCV basis)
I. No data available, no known use
J. Not relevant for this CHP configuration
K. No data available
L. DGC Estimate
M. Air preheating by internal recuperation included
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
5. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
6. Wärtsila Technical Journal "in detail" 02-2014
7. Data specs from maufacturers (Web) 2015
8. Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
9. Danish Gas Technology Centre, environmental survey 2012
10. Smart Power Generation - The future of electricity production, J. Klimstra & M. Hotakainen 2011
11. IEA: Projected cost of generating electricity, 2010
12. COWI 2015 input
13. The Omes Project results (2005)
14. WBDG-Publication, B. L. Capehart, Microtubines, 2014

## 04 Gas turb. simple cycle Micro
Technology |  | Gas turbine, simple cycle - back pressure - natural gas - micro
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | lower: 0.01; upper: 0.2; lower: 0.01; upper: 0.2
| Electrical efficiency (net, name plate) [] | 30% | 30% | 30% | 30% | 23% | 32% | 25% | 35% | M | 7
| Electrical efficiency (net, annual average) [] | 28% | 28% | 28% | 28% | 21% | 29% | 23% | 33%
| Cb coefficient (50°C/100°C) | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.85 | 0.4 | 0.85 |  | [7, 13]
Cv coefficient (50°C/100°C) | bar: -
Forced outage [] | bar: ctrl to ctrl
Planned outage [weeks per year]
| Technical lifetime [years] | 15 | 15 | 15 | 15 | 10 | 20 | 10 | 20 | L
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.8 | 0.2 | 0.7 | L | 13
| Space requirement [1000 m2/MW_e] | 0.06 | 0.06 | 0.06 | 0.06 | 0.05 | 0.15 | 0.05 | 0.15 |  | 7
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to upper
Secondary regulation (of full load, per minute) [] | bar: ctrl to upper
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 30% | 50% | 25% | 50% | L | [7, 13]
| Warm start-up time [hours] | ctrl: 0.25; ctrl: 0.25; ctrl: 0.25; ctrl: 0.25
| Cold start-up time [hours] | ctrl: 0.5; ctrl: 0.5; ctrl: 0.5; ctrl: 0.5
Environment
| SO2 (degree of desulphuring) [] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | 13
| NOX [g/GJ_i] | 10 | 10 | 10 | 10 | 6 | 15 | 6 | 15 |  | [7, 13]
| CH4 [g/GJ_i] | ctrl: 6; ctrl: 6; ctrl: 6; ctrl: 6; -: 13
| N2O [g/GJ_i] | -: 13
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 1.276 | 1.276 | 1.1697 | 1.0634 | 0 | 0 | 0 | 0 | 0 | [13, 14]
| Nominal investment (equipment) [MEUR/MW_e] | 0.90387 | 0.90387 | 0.8507 | 0.74436 | 0 | 0 | 0 | 0 | 0 | [13, 14]
| Nominal investment (installation) [MEUR/MW_e] | 0.37218 | 0.37218 | 0.31901 | 0.31901 | 0 | 0 | 0 | 0 | 0 | [13, 14]
| Variable O&M (*total) [EUR/MWh_e] | 15.9506 | 15.9506 | 14.8872 | 13.8238 | 10.6337 | 15.9506 | 8.507 | 15.9506 | 0 | 13
| Fixed O&M (*total) [EUR/MW_e/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology-specific data
Notes:
A. Very low efficiency at low loads and often increased Nox emisison
B. Insurance excluded, unknown. Daily start assumed
C. Power related
D. Based on Dry Low NOx (DLN) techniques
E. Technical- and design life most often > 25 years
F. Electrical output
G. Combined with DGC assumptions, CHP configuration
H. GT's (5 MWe) are available including internal recuperator; the electrical nominal efficiency is then 37 % (LCV basis)
I. No data available, no known use
J. Not relevant for this CHP configuration
K. No data available
L. DGC Estimate
M. Air preheating by internal recuperation included
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
5. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
6. Wärtsila Technical Journal "in detail" 02-2014
7. Data specs from maufacturers (Web) 2015
8. Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
9. Danish Gas Technology Centre, environmental survey 2012
10. Smart Power Generation - The future of electricity production, J. Klimstra & M. Hotakainen 2011
11. IEA: Projected cost of generating electricity, 2010
12. COWI 2015 input
13. The Omes Project results (2005)
14. WBDG-Publication, B. L. Capehart, Microtubines, 2014

## 05 Gas turb. CC, steam extract.
Technology |  | Gas turbine, combined cycle - extraction - natural gas - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | lower: 100; upper: 500; lower: 100; upper: 500; -: F
| Electrical efficiency (net, name plate) [] | 58% | 59% | 61% | 63% | 55% | 61% | 58% | 65% |  | 5
| Electrical efficiency (net, annual average) [] | 55% | 56% | 58% | 60% | 52% | 58% | 55% | 62% |  | [5, 9]
| Cb coefficient (50°C/100°C) | 1.7 | 1.8 | 2 | 2.2 | 1.5 | 2.2 | 1.5 | 2.4
| Cv coefficient (50°C/100°C) | ctrl: 0.15; ctrl: 0.15; ctrl: 0.15; ctrl: 0.15; -: J
| Forced outage [] | 3% | 3% | 3% | 3% | 2% | 4% | 2% | 4% |  | 5
| Planned outage [weeks per year] | 2.5 | 2.3 | 2 | 2 | 2 | 4 | 2 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 |  | 25 |  | E | [5, 3]
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 |  | 5
| Space requirement [1000 m2/MW_e] | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.03 | 0.01 | 0.03 | G | 3
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: -
| Secondary regulation (of full load, per minute) [] | 15% | 15% | 15% | 15% | 5% | 15% | 5% | 15% |  | [5, 3, 11]
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 30% | 50% | 30% | 50% | A | [5, 3, 11]
| Warm start-up time [hours] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 | H | [5, 6, 1, 11]
| Cold start-up time [hours] | 2.5 | 2.5 | 2.5 | 2 | 2 | 5 | 1.5 | 5 |  | [5, 6, 1, 11]
Environment
SO2 (degree of desulphuring) [] | bar: ctrl to upper
| NOX [g/GJ_i] | 20 | 15 | 10 | 8 | 10 | 30 | 5 | 15 | D | [3, 7]
| CH4 [g/GJ_i] | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 8 | 1 | 8 | G | 7
| N2O [g/GJ_i] | 1 | 1 | 1 | 1 | 0.7 | 1.2 | 0.7 | 1.2 | G | 7
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 0.95704 | 0.93577 | 0.8826 | 0.8507 | 0.8507 | 1.276 | 0.74436 | 1.1697 | 0 | [5, 8]
| Nominal investment (equipment) [MEUR/MW_e] | 0.74436 | 0.72309 | 0.68056 | 0.64866 | 0.69119 | 1.0846 | 0.63802 | 1.0102 | 0 | 10
| Nominal investment (installation) [MEUR/MW_e] | 0.21267 | 0.21267 | 0.20204 | 0.20204 | 0.15951 | 0.19141 | 0.10634 | 0.15951 | 0 | 10
| Variable O&M (*total) [EUR/MWh_e] | 4.7852 | 4.6788 | 4.4662 | 4.2535 | 3.1901 | 7.4436 | 3.1901 | 7.4436 | 0 | 5
| Fixed O&M (*total) [EUR/MW_e/y] | 31901.1815 | 31156.8206 | 29561.7616 | 27647.6907 | 26584.318 | 37218.0451 | 21267.4544 | 31901.1815 | B | 5
Technology-specific data
Notes:
A. Low efficiency at low loads and often increased NOx emission
B. Limited availability of data
C. Power related
D. Based on Dry Low NOx (DLN) techniques
E. Technical- and design life most often > 25 years
F. Electrical output
G. CHP configuration, Including DGC assumptions
H. Manufacturers says down to 30 minute
I. No data available
J. Data on Cv from the 2012 version roughly adjusted for higher electricity efficiency
K. No known use
L. No Relevance for Back Pressure Lay Out
M. Upward regulation is typically 10 - 15 %/min, while downward regulation is > 30 % /min
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
3. Data specs from maufacturers (Web) 2015
5. Wärtsila Technical Journal "in detail" 02-2014
6. Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
7. Danish Gas Technology Centre, environmental survey 2012
8. Smart Power Generation; the future of electricity production, J. Klimstra & M. Hotakainen 2011
9. IEA: Projected cost of generating electricity, 2010
10. UK Electricity Generation Costs Update, M.M. Donald, June 2010
11. Siemens : Data on GT-CC (2010)

## 05 Gas turb. CC, Back-pressure
Technology |  | Gas turbine, combined cycle - back pressure - natural gas - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | lower: 10; upper: 100; lower: 10; upper: 100; -: F
| Electrical efficiency (net, name plate) [] | 50% | 51% | 53% | 55% | 42% | 55% | 45% | 58% |  | 5
| Electrical efficiency (net, annual average) [] | 47% | 48% | 50% | 52% | 39% | 52% | 42% | 55% |  | [5, 9]
| Cb coefficient (50°C/100°C) | 1.2 | 1.3 | 1.4 | 1.55 | 0.9 | 1.6 | 1.1 | 1.7
Cv coefficient (50°C/100°C) | bar: -
| Forced outage [] | 3% | 3% | 3% | 3% | 2% | 4% | 2% | 4% |  | 5
| Planned outage [weeks per year] | 2.5 | 2.3 | 2 | 2 | 2 | 4 | 1.5 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 |  | 25 |  | E | [5, 3]
| Construction time [years] | 2.5 | 2 | 2 | 2 | 2 | 3 | 2 | 3 |  | 5
| Space requirement [1000 m2/MW_e] | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.04 | 0.02 | 0.04 | G | 3
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: -
| Secondary regulation (of full load, per minute) [] | 15% | 15% | 15% | 15% | 5% | 15% | 5% | 15% | [C, M] | [5, 3, 11]
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 30% | 50% | 30% | 50% | A | [5, 3, 11]
| Warm start-up time [hours] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 | H | [5, 6, 1, 11]
| Cold start-up time [hours] | 2.5 | 2.5 | 2.5 | 2 | 2 | 5 | 1.5 | 5 |  | [5, 6, 1, 11]
Environment
SO2 (degree of desulphuring) [] | bar: ctrl to upper
| NOX [g/GJ_i] | 20 | 15 | 10 | 8 | 10 | 30 | 5 | 15 | D | [3, 7]
| CH4 [g/GJ_i] | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 8 | 1 | 8 | G | 7
| N2O [g/GJ_i] | 1 | 1 | 1 | 1 | 0.7 | 1.2 | 0.7 | 1.2 | G | 7
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 1.3824 | 1.3824 | 1.276 | 1.1697 | 1.1697 | 1.9141 | 0.95704 | 1.7014 | 0 | [5, 9]
| Nominal investment (equipment) [MEUR/MW_e] | 1.0634 | 1.0634 | 0.95704 | 0.8507 | 0.8507 | 1.4887 | 0.69119 | 1.3292 | 0 | 10
| Nominal investment (installation) [MEUR/MW_e] | 0.31901 | 0.31901 | 0.31901 | 0.31901 | 0.31901 | 0.42535 | 0.26584 | 0.37218 | 0 | 10
| Variable O&M (*total) [EUR/MWh_e] | 4.7852 | 4.6788 | 4.4662 | 4.2535 | 3.1901 | 7.4436 | 3.1901 | 7.4436 | 0 | 5
| Fixed O&M (*total) [EUR/MW_e/y] | 31901.1815 | 31156.8206 | 29561.7616 | 27647.6907 | 26584.318 | 37218.0451 | 21267.4544 | 31901.1815 | B | 5
Technology-specific data
Notes:
A. Low efficiency at low loads and often increased NOx emission
B. Limited availability of data
C. Power related
D. Based on Dry Low NOx (DLN) techniques
E. Technical- and design life most often > 25 years
F. Electrical output
G. CHP configuration, Including DGC assumptions
H. Manufacturers says down to 30 minute
I. No data available
J. Data on Cv from the 2012 version roughly adjusted for higher electricity efficiency
K. No known use
L. No Relevance for Back Pressure Lay Out
M. Upward regulation is typically 10 - 15 %/min, while downward regulation is > 30 % /min
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
3. Data specs from maufacturers (Web) 2015
5. Wärtsila Technical Journal "in detail" 02-2014
6. Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
7. Danish Gas Technology Centre, environmental survey 2012
8. Smart Power Generation; the future of electricity production, J. Klimstra & M. Hotakainen 2011
9. IEA: Projected cost of generating electricity, 2010
10. UK Electricity Generation Costs Update, M.M. Donald, June 2010
11. Siemens : Data on GT-CC (2010)

## 06 Gas engines, natural gas
Technology |  | Engine - back pressure - natural gas - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | lower: 1; upper: 10; lower: 1; upper: 10
| Electrical efficiency (net, name plate) [] | 46% | 47% | 48% | 50% | 40% | 48% | 44% | 52% | A | [3, 4]
| Electrical efficiency (net, annual average) [] | 44% | 45% | 47% | 48% | 38% | 46% | 42% | 50% | A | [3, 4, 7]
| Cb coefficient (50°C/100°C) | 0.9 | 0.95 | 0.99 | 1.04 | 0.65 | 1.02 | 0.65 | 1.15 |  | [3, 4, 7]
Cv coefficient (50°C/100°C) | bar: -
| Forced outage [] | 3% | 3% | 3% | 3% | 2% | 5% | 2% | 5% |  | [5, 6]
| Planned outage [weeks per year] | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  |  | H | [5, 6]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 |  | 25 |  | D | [4, 5, 7]
| Construction time [years] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 | B | [3, 6]
| Space requirement [1000 m2/MW_e] | 0.04 | 0.04 | 0.04 | 0.03 | 0.03 | 0.05 | 0.03 | 0.04
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 25% | 30% | 35% | 50% | 10% | 40% | 25% | 100% |  | 12
| Secondary regulation (of full load, per minute) [] | 25% | 30% | 40% | 50% | 20% | 100% | 25% | 100% | C | [6, 12, 13]
| Minimum load (of full load) [] | 50% | 50% | 50% | 50% | 30% | 50% | 25% | 50% |  | 6
| Warm start-up time [hours] | 0.05 | 0.05 | 0.05 | 0.05 | 0.01 | 0.15 | 0.01 | 0.15 | C | [6, 10]
| Cold start-up time [hours] | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.4 | 0.2 | 0.4 | E | [6, 10]
Environment
| SO2 (degree of desulphuring) [] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | 4
| NOX [g/GJ_i] | 75 | 60 | 60 | 60 | 50 | 100 | 50 | 100 |  | 4
| CH4 [g/GJ_i] | 315 | 315 | 280 | 250 | 300 | 400 | 250 | 350 |  | 4
| N2O [g/GJ_i] | ctrl: 0.6; ctrl: 0.6; ctrl: 0.6; ctrl: 0.6; -: H
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 1.0634 | 1.0102 | 0.95704 | 0.90387 | 0.95704 | 1.1697 | 0.8507 | 1.1697 | 0 | [3, 5, 11]
| Nominal investment (equipment) [MEUR/MW_e] | 0.69119 | 0.63802 | 0.58485 | 0.58485 | 0 | 0 | 0 | 0 | H | [3, 5]
| Nominal investment (installation) [MEUR/MW_e] | 0.37218 | 0.37218 | 0.37218 | 0.31901 | 0 | 0 | 0 | 0 | H | [3, 5]
| Variable O&M (*total) [EUR/MWh_e] | 5.7422 | 5.7422 | 5.4232 | 5.2105 | 4.2535 | 12.7605 | 4.2535 | 10.6337 | F | [3, 5, 11]
| Fixed O&M (*total) [EUR/MW_e/y] | 10633.7272 | 10367.884 | 9889.3663 | 9038.6681 | 7443.609 | 21267.4544 | 6380.2363 | 15950.5908 | F | 5
Technology-specific data
Notes:
A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
D. Technical- and design life most often > 25 years
E. For a medium size engine; small engines with less thermal mass might be faster
F. When operating 4000 hours a year
G. Only relevant for steam based CHP
H. No data available
I. DGC estimate for years 2030, 2050
J. No known use, data from n-gas engines
K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
3. ASUE BHKW Kenndata 2014/2015
4. DGC Efficiency and emission test reports
5. DGC analysis, The gas fired cogneration sector, Bilagsrapport 9, Energiforligs analyse 2013
6. Features and parameters of various power plant technologies, Wartsila "In Detail", 02-2014 etc.
7. Dansk Fjernvarme and FDKV reportings from CHP installations, the Dansk Fjernvarme information is from a 2012 suvey for an earlier version of the report
8. Ongoing Sulpur research project at DGC (MUDP)
10. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
11. Blockheizkraftwerke 2013, M.Buller et al, GWF Gas Erdgas, Juni 2014
12. Suppliers association information etc.
13. MAN Turbo Presentation of Gas Engine with fuel switch, 2012

## 06 Gas engines, biogas
Technology |  | Engine - back pressure - biogas - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | lower: 1; upper: 10; lower: 1; upper: 10
| Electrical efficiency (net, name plate) [] | 42% | 43% | 45% | 47% | 38% | 44% | 42% | 48% | A | [3, 4]
| Electrical efficiency (net, annual average) [] | 40% | 41% | 43% | 45% | 36% | 42% | 40% | 46% | A | [3, 4, 7]
| Cb coefficient (50°C/100°C) | 0.82 | 0.86 | 0.92 | 1 | 0.59 | 0.96 | 0.75 | 1.1 |  | [3, 4, 7]
Cv coefficient (50°C/100°C) | bar: -
| Forced outage [] | 3% | 3% | 3% | 3% | 2% | 5% | 2% | 5% |  | [5, 6]
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 |  |  |  |  | H | [5, 6]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 |  | 25 |  | D | [4, 5, 7]
| Construction time [years] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 | B | [3, 6]
| Space requirement [1000 m2/MW_e] | 0.04 | 0.04 | 0.04 | 0.03 | 0.03 | 0.05 | 0.03 | 0.05
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 25% | 30% | 40% | 50% | 10% | 40% | 25% | 100% | J | 8
| Secondary regulation (of full load, per minute) [] | 25% | 30% | 40% | 50% | 20% | 100% | 25% | 100% | C | [6, 8, 13]
| Minimum load (of full load) [] | 50% | 50% | 50% | 50% | 30% | 50% | 25% | 50% |  | 6
| Warm start-up time [hours] | 0.05 | 0.05 | 0.05 | 0.05 | 0.01 | 0.15 | 0.01 | 0.15 | C | [6, 10]
| Cold start-up time [hours] | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.4 | 0.2 | 0.4 | E | [6, 10]
Environment
| SO2 (degree of desulphuring) [] |  |  |  |  | 0% | 99.9% | 0% | 99.9% | K | 8
| NOX [g/GJ_i] | 100 | 100 | 100 | 100 | 90 | 120 | 90 | 120 |  | 4
| CH4 [g/GJ_i] | 300 | 300 | 300 | 300 | 300 | 400 | 300 | 400 |  | 4
N2O [g/GJ_i] | bar: ctrl to ctrl; -
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 1.0634 | 1.0102 | 0.95704 | 0.90387 | 0.8507 | 1.276 | 0.8507 | 1.276 | 0 | [3, 5, 11]
| Nominal investment (equipment) [MEUR/MW_e] | 0.69119 | 0.63802 | 0.58485 | 0.58485 | 0 | 0 | 0 | 0 | 0 | [3, 5]
| Nominal investment (installation) [MEUR/MW_e] | 0.37218 | 0.37218 | 0.37218 | 0.31901 | 0 | 0 | 0 | 0 | 0 | [3, 5]
| Variable O&M (*total) [EUR/MWh_e] | 8.507 | 7.9753 | 7.4436 | 6.3802 | 6.3802 | 13.8238 | 4.2535 | 12.7605 | F | [3, 5, 11]
| Fixed O&M (*total) [EUR/MW_e/y] | 10633.7272 | 10367.884 | 9889.3663 | 9038.6681 | 7443.609 | 21267.4544 | 6380.2363 | 15950.5908 | F | 5
Technology-specific data
Notes:
A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
D. Technical- and design life most often > 25 years
E. For a medium size engine; small engines with less thermal mass might be faster
F. When operating 4000 hours a year
G. Only relevant for steam based CHP
H. No data available
I. DGC estimate for years 2030, 2050
J. No known use, data from n-gas engines
K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
3. ASUE BHKW Kenndata 2014/2015
4. DGC Efficiency and emission test reports
5. DGC analysis, The gas fired cogneration sector, Bilagsrapport 9, Energiforligs analyse 2013
6. Features and parameters of various power plant technologies, Wartsila "In Detail", 02-2014 etc.
7. Dansk Fjernvarme and FDKV reportings from CHP installations, the Dansk Fjernvarme information is from a 2012 suvey for an earlier version of the report
8. Ongoing Sulpur research project at DGC (MUDP)
10. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
11. Blockheizkraftwerke 2013, M.Buller et al, GWF Gas Erdgas, Juni 2014
12. Suppliers association information etc.
13. MAN Turbo Presentation of Gas Engine with fuel switch, 2012

## 08 WtE CHP, Large, 40 degree
Technology |  | Waste CHP, 40/80 degree - back pressure - waste - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 51.77 | 51.77 | 53 | 54.91 | 46.98 | 56.44 | 46.98 | 60.65 | [A, B]
| Electrical efficiency (net, annual average) [] | 22.36% | 22.36% | 22.89% | 23.71% | 19% | 25% | 19% | 27% | [A, B, C]
| Electrical efficiency (net, name plate) [] | 23.53% | 23.53% | 24.09% | 24.96% | 21% | 26% | 21% | 28% | [A, B]
| Cb coefficient (40°C/80°C) | 0.3 | 0.3 | 0.31 | 0.32 | 0.27 | 0.32 | 0.27 | 0.35 | [A, B]
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [A, B]
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.91% | 2.91% | 2.921% | 2.911% | 2.147% | 3.196% | 1.718% | 3.238% | [A, B]
Forced outage [] | bar: ctrl to upper; -
| Planned outage [weeks per year] | 2.5 | 2.38 | 2.15 | 1.76 | 2.02 | 2.73 | 1.32 | 2.2 | E | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 3 | 3 | 3 | 3 | 2.5 | 3.5 | 2 | 3.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.77 | 0.77 | 0.75 | 0.73 | 0.66 | 0.89 | 0.55 | 0.91 |  | 1
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to -
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | [F, G]
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | [F, G]
| Warm start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [F, G]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [F, G]
Environment
| SO2 (degree of desulphuring) [] | 99.79% | 99.79% | 99.79% | 99.79% | 98.96% | 99.9% | 99.48% | 99.9% | H | 1
| NOX [g/GJ_i] | 80 | 60 | 20 | 10 | 10 | 60 | 10 | 60 | I | [2, 3, 5]
| CH4 [g/GJ_i] | 0.3 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.1 |  | 2
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | J | 2
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | J | 2
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 8.4538 | 8.2518 | 7.8477 | 6.8694 | 7.0076 | 9.6661 | 5.0191 | 8.5389 | N | 1
| Nominal investment (equipment) [MEUR/MW_e] | 5.0936 | 4.9766 | 4.7958 | 4.211 | 4.2216 | 5.9017 | 3.02 | 5.2105 | N | 1
| Nominal investment (installation) [MEUR/MW_e] | 3.3603 | 3.2752 | 3.0412 | 2.6584 | 2.786 | 3.7643 | 1.9885 | 3.3177 | M | 1
| Variable O&M (*total) [EUR/MWh_e] | 26.5737 | 26.5737 | 25.9782 | 25.0956 | 22.6073 | 30.6251 | 18.8642 | 31.3589 | K | 1
| Fixed O&M (*total) [EUR/MW_e/y] | 243512.3524 | 197787.3255 | 185026.8529 | 157379.1623 | 168012.8894 | 231815.2525 | 115907.6263 | 195660.5801 | L | 1
Technology-specific data
| Heat efficiency (net, annual average) [] | 80.19% | 80.19% | 79.89% | 79.57% | 76% | 85% | 73% | 87% | [A, B, C]
| Heat efficiency (net, name plate) [] | 79.01% | 79.01% | 78.68% | 78.32% | 74% | 84% | 71% | 86% | [A, B]
| Nominal investment (*total) [MEUR/MW_i] | 1.9885 | 1.946 | 1.8928 | 1.712 | 1.6482 | 2.2756 | 1.2548 | 2.1267 | N | 1
| Nominal investment (*total) [MEUR/t_i] | 733.7272 | 712.4597 | 691.1923 | 627.3899 | 606.1224 | 840.0644 | 457.2503 | 786.8958 | N | 1
| Nominal investment (equipment) [MEUR/MW_i] | 1.2016 | 1.1697 | 1.1591 | 1.0527 | 0.99957 | 1.393 | 0.75499 | 1.2973 | N | 1
| Nominal investment (installation) [MEUR/MW_i] | 0.7869 | 0.76563 | 0.73373 | 0.65929 | 0.65929 | 0.8826 | 0.49979 | 0.82943 | M | 1
| Variable O&M (*total) [EUR/MWh_i] | 6.2526 | 6.2526 | 6.2526 | 6.2633 | 5.3169 | 7.2097 | 4.7107 | 7.8264 | K | 1
| Fixed O&M (*total) [EUR/MW_i/y] | 57422.1267 | 46682.0623 | 44555.3169 | 39344.7905 | 39663.8024 | 54551.0204 | 28817.4006 | 48915.145 | L | 1
| Fixed O&M (*total) [EUR/t_i/y] | 21.1292 | 17.1735 | 16.4078 | 14.4725 | 14.6001 | 20.0658 | 10.6231 | 18.0135 | L | [1, 4]
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | O
| Output of recovered condensate [t/MWh_i] | 0.11697 | 0.11697 | 0.11697 | 0.1276 | 0.10634 | 0.14887 | 0.10634 | 0.15951 | [D, K]
| Output of recovered condensate [EUR/t_i] | 18.4176 | 18.4176 | 18.4282 | 18.4495 | 15.6741 | 21.2356 | 13.8664 | 23.0539 | K | [1, 4]
| Incineration capacity [t_i/h] | 74.69 | 74.69 | 74.69 | 74.69 | 74.69 | 74.69 | 74.69 | 74.69 | [A, B]
| Flue gas condensation | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [D, O]
| Combustion air humidification | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [D, O]
| Additional heat potential with heat pumps (of thermal input) [] | 4.151% | 4.151% | 4.015% | 3.74% | 1% | 6% | 1% | 6% | [A, B, D]
Notes:
A. Assumed lower heating value 10.6 MJ/kg, waste input 74.7 tph = tonnes per hour (incineration capacity) divided in two, equally sized furnace/boiler units , corresponding to thermal input of 2x110 MW. One common turbine/generator set is foreseen. Live steam pressure in base case 50 bara, temperature 425 °C of 2015 and 2020, increasing to 440 °C and 450 °C, in 2030 and 2050, respectively. Efficiencies refer to lower heating value.
B. With flue gas condensation (condensation through heat exchange with DH-water, only) and a back-pressure turbine/condenser system optimised at DH return temperature 40°C and flow 80°C.
C. Annual average heat output is higher than nameplate because the total efficiency is constant, and the annual average electricity generation is lower than nameplate electricity output. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 and 2050.
E. Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
F. Regulation and start-up refer to electricity generation controlled by the turbine operation.The WtE facility would usually be operating at 100% thermal input, and the electricity output is controlled to the desired level by use of turbine by-pass, by which excess steam is used to produce DH-energy. Warm start-up time refers to 2 days down-time of the turbine.
G. The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (in stead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the requirement of min. 2 sec residence time of the flue gas at min. 850 °C after the last air injection. Below this limit it may also be a challenge to ensure sufficient superheating of the steam. Warm start-up of the combustion process is typically 8 hours and cold start-up is 8 hours.
H. Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream the flue gas treatment system. Sulphur content in fuel 270 g/GJ.
I. Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2030 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2050. The SCR-technology entails additional investment.
J. N2O is expected to be related primarily to the use of SNCR using urea injection. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
K. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
L. Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
M. Installation includes civils works (including waste bunker) and project cost.
N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract.
O. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll present work, range of WtE-projects
2. Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.
3. Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013," http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkendelseovn5Juni2013.pdf
4. Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
5. Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook, Serge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019 https://eippcb.jrc.ec.europa.eu/reference/BREF/WI/JRC118637_WI_Bref_2019_published.pdf

## 08 WtE CHP, Large, 50 degree
Technology |  | Waste CHP, 50/100 degree - back pressure - waste - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 46.81 | 46.81 | 48.2 | 50.15 | 42.06 | 51.61 | 42.06 | 55.88 | [A, B]
| Electrical efficiency (net, annual average) [] | 20.21% | 20.21% | 20.81% | 21.65% | 17% | 23% | 17% | 25% | [A, B, C]
| Electrical efficiency (net, name plate) [] | 21.28% | 21.28% | 21.91% | 22.79% | 19% | 24% | 19% | 26% | [A, B]
| Cb coefficient (50°C/100°C) | 0.28 | 0.28 | 0.29 | 0.3 | 0.25 | 0.31 | 0.25 | 0.34 | [A, B]
| Cv coefficient (50°C/100°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [A, B]
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.957% | 2.957% | 2.967% | 2.953% | 2.185% | 3.224% | 1.748% | 3.265% | [A, B]
Forced outage [] | bar: ctrl to upper; -
| Planned outage [weeks per year] | 2.5 | 2.38 | 2.15 | 1.76 | 2.02 | 2.73 | 1.32 | 2.2 | E | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 3 | 3 | 3 | 3 | 2.5 | 3.5 | 2 | 3.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.85 | 0.85 | 0.83 | 0.8 | 0.73 | 0.98 | 0.6 | 1 |  | 1
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to -
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | [F, G]
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | [F, G]
| Warm start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [F, G]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [F, G]
Environment
| SO2 (degree of desulphuring) [] | 99.79% | 99.79% | 99.79% | 99.79% | 98.96% | 99.9% | 99.48% | 99.9% | H | 1
| NOX [g/GJ_i] | 80 | 60 | 20 | 10 | 10 | 60 | 10 | 60 | I | [2, 3, 5]
| CH4 [g/GJ_i] | 0.3 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.1 |  | 2
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | J | 2
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | J | 2
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 9.3577 | 9.1237 | 8.624 | 7.518 | 7.752 | 10.6975 | 5.4976 | 9.347 | N | 1
| Nominal investment (equipment) [MEUR/MW_e] | 5.6359 | 5.4976 | 5.2743 | 4.6044 | 4.6788 | 6.5291 | 3.3071 | 5.7103 | N | 1
| Nominal investment (installation) [MEUR/MW_e] | 3.7112 | 3.6261 | 3.3496 | 2.9136 | 3.0838 | 4.1684 | 2.1799 | 3.6367 | M | 1
| Variable O&M (*total) [EUR/MWh_e] | 29.0088 | 29.0088 | 28.2006 | 27.1585 | 24.5745 | 33.7089 | 20.2466 | 34.1874 | K | 1
| Fixed O&M (*total) [EUR/MW_e/y] | 270096.6704 | 219054.7799 | 203104.1891 | 172266.3803 | 186090.2257 | 256272.825 | 126541.3534 | 214801.289 | L | 1
Technology-specific data
| Heat efficiency (net, annual average) [] | 76.35% | 76.35% | 76.19% | 76.25% | 72% | 85% | 70% | 86% | [A, B, C]
| Heat efficiency (net, name plate) [] | 75.29% | 75.29% | 75.09% | 75.11% | 70% | 84% | 68% | 85% | [A, B]
| Nominal investment (*total) [MEUR/MW_i] | 1.9885 | 1.946 | 1.8928 | 1.712 | 1.6482 | 2.2756 | 1.2548 | 2.1267 | N | 1
| Nominal investment (*total) [MEUR/t_i] | 733.7272 | 712.4597 | 691.1923 | 627.3899 | 606.1224 | 840.0644 | 457.2503 | 786.8958 | N | 1
| Nominal investment (equipment) [MEUR/MW_i] | 1.2016 | 1.1697 | 1.1591 | 1.0527 | 0.99957 | 1.393 | 0.75499 | 1.2973 | N | 1
| Nominal investment (installation) [MEUR/MW_i] | 0.7869 | 0.76563 | 0.73373 | 0.65929 | 0.65929 | 0.8826 | 0.49979 | 0.82943 | M | 1
| Variable O&M (*total) [EUR/MWh_i] | 6.1676 | 6.1676 | 6.1782 | 6.1888 | 5.2318 | 7.1671 | 4.615 | 7.7945 | K | 1
| Fixed O&M (*total) [EUR/MW_i/y] | 57422.1267 | 46682.0623 | 44555.3169 | 39344.7905 | 39663.8024 | 54551.0204 | 28817.4006 | 48915.145 | L | 1
| Fixed O&M (*total) [EUR/t_i/y] | 21.1292 | 17.1735 | 16.4078 | 14.4725 | 14.6001 | 20.0658 | 10.6231 | 18.0135 | L | [1, 4]
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | O
| Output of recovered condensate [t/MWh_i] | 0.03 | 0.03 | 0.04 | 0.05 | 0.01 | 0.11 | 0.01 | 0.11 | [D, K]
| Output of recovered condensate [EUR/t_i] | 18.1837 | 18.1837 | 18.1943 | 18.2368 | 15.4083 | 21.1292 | 13.6005 | 22.9582 | K | [1, 4]
| Incineration capacity [t_i/h] | 74.69 | 74.69 | 74.69 | 74.69 | 74.69 | 74.69 | 74.69 | 74.69 | [A, B]
| Flue gas condensation | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [D, O]
| Combustion air humidification | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [D, O]
| Additional heat potential with heat pumps (of thermal input) [] | 10.04% | 10.04% | 9.709% | 9.042% | 4% | 12% | 4% | 12% | [A, B, D]
Notes:
A. Assumed lower heating value 10.6 MJ/kg, waste input 74.7 tph = tonnes per hour (incineration capacity) divided in two, equally sized furnace/boiler units , corresponding to thermal input of 2x110 MW. One common turbine/generator set is foreseen. Live steam pressure in base case 50 bara, temperature 425 °C of 2015 and 2020, increasing to 440 °C and 450 °C, in 2030 and 2050, respectively. Efficiencies refer to lower heating value.
B. With flue gas condensation (condensation through heat exchange with DH-water, only) and a back-pressure turbine/condenser system optimised at DH return temperature 50°C and flow 100°C.
C. Annual average heat output is higher than nameplate because the total efficiency is constant, and the annual average electricity generation is lower than nameplate electricity output. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 and 2050.
E. Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
F. Regulation and start-up refer to electricity generation controlled by the turbine operation.The WtE facility would usually be operating at 100% thermal input, and the electricity output is controlled to the desired level by use of turbine by-pass, by which excess steam is used to produce DH-energy. Warm start-up time refers to 2 days down-time of the turbine.
G. The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (in stead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the requirement of min. 2 sec residence time of the flue gas at min. 850 °C after the last air injection. Below this limit it may also be a challenge to ensure sufficient superheating of the steam. Warm start-up of the combustion process is typically 8 hours and cold start-up is 8 hours.
H. Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream the flue gas treatment system. Sulphur content in fuel 270 g/GJ.
I. Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2030 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2050. The SCR-technology entails additional investment.
J. N2O is expected to be related primarily to the use of SNCR using urea injection. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
K. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
L. Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
M. Installation includes civils works (including waste bunker) and project cost.
N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract.
O. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll present work, range of WtE-projects
2. Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.
3. Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013," http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkendelseovn5Juni2013.pdf
4. Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
5. Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook, Serge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019 https://eippcb.jrc.ec.europa.eu/reference/BREF/WI/JRC118637_WI_Bref_2019_published.pdf

## 08 WtE CHP, Medium
Technology |  | Waste CHP - back pressure - waste - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 18.61 | 18.61 | 19.03 | 19.69 | 16.91 | 20.24 | 16.91 | 21.66 | [A, B]
| Electrical efficiency (net, annual average) [] | 22.1% | 22.1% | 22.6% | 23.38% | 19% | 25% | 19% | 26% | [A, B, C]
| Electrical efficiency (net, name plate) [] | 23.26% | 23.26% | 23.79% | 24.61% | 21% | 26% | 21% | 28% | [A, B, C]
| Cb coefficient (40°C/80°C) | 0.3 | 0.3 | 0.3 | 0.31 | 0.27 | 0.32 | 0.27 | 0.35 | [A, B]
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [A, B]
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.91% | 2.91% | 2.922% | 2.911% | 2.147% | 3.196% | 1.718% | 3.268% | [A, B]
Forced outage [] | bar: ctrl to upper; -
| Planned outage [weeks per year] | 3 | 2.85 | 2.58 | 2.11 | 2.43 | 3.28 | 1.58 | 2.64 | E | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 1.5 | 3 |  | 1
| Space requirement [1000 m2/MW_e] | 1.61 | 1.61 | 1.58 | 1.52 | 1.37 | 1.85 | 1.14 | 1.9 |  | 1
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to -
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | [F, G]
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | [F, G]
| Warm start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [F, G]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [F, G]
Environment
| SO2 (degree of desulphuring) [] | 99.79% | 99.79% | 99.79% | 99.79% | 98.96% | 99.9% | 99.48% | 99.9% | H | 1
| NOX [g/GJ_i] | 80 | 60 | 40 | 10 | 10 | 60 | 10 | 60 | I | [2, 3, 5]
| CH4 [g/GJ_i] | 0.3 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.1 |  | 2
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | J | 2
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | J | 2
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 9.8362 | 9.5916 | 9.145 | 8.0178 | 8.1561 | 11.2611 | 5.8485 | 9.9638 | N | 1
| Nominal investment (equipment) [MEUR/MW_e] | 5.9762 | 5.8273 | 5.6465 | 4.9553 | 4.9553 | 6.9332 | 3.5517 | 6.1463 | N | 1
| Nominal investment (installation) [MEUR/MW_e] | 3.86 | 3.7643 | 3.4985 | 3.0625 | 3.2008 | 4.3279 | 2.2969 | 3.8281 | M | 1
| Variable O&M (*total) [EUR/MWh_e] | 26.8821 | 26.8821 | 26.3078 | 25.4465 | 22.8731 | 30.9867 | 19.1301 | 31.7842 | K | 1
| Fixed O&M (*total) [EUR/MW_e/y] | 316885.07 | 278603.6521 | 260526.3159 | 222244.8981 | 237132.1161 | 325392.0517 | 163759.3986 | 276476.9067 | L | 1
Technology-specific data
| Heat efficiency (net, annual average) [] | 79.99% | 79.99% | 79.71% | 79.42% | 76% | 85% | 73% | 88% | [A, B, C]
| Heat efficiency (net, name plate) [] | 78.82% | 78.82% | 78.52% | 78.19% | 74% | 84% | 71% | 86% | [A, B]
| Nominal investment (*total) [MEUR/MW_i] | 2.2863 | 2.2331 | 2.1799 | 1.9779 | 1.8928 | 2.6159 | 1.4356 | 2.4564 | N | 1
| Nominal investment (*total) [MEUR/t_i] | 840.0644 | 818.797 | 797.5295 | 723.0934 | 701.826 | 967.6692 | 531.6864 | 903.8668 | N | 1
| Nominal investment (equipment) [MEUR/MW_i] | 1.393 | 1.3611 | 1.3398 | 1.2229 | 1.1484 | 1.6163 | 0.87197 | 1.51 | N | 1
| Nominal investment (installation) [MEUR/MW_i] | 0.89323 | 0.87197 | 0.82943 | 0.75499 | 0.74436 | 1.0102 | 0.56359 | 0.93577 | M | 1
| Variable O&M (*total) [EUR/MWh_i] | 6.2526 | 6.2526 | 6.2526 | 6.2633 | 5.3169 | 7.2097 | 4.7107 | 7.8264 | K | 1
| Fixed O&M (*total) [EUR/MW_i/y] | 73691.7293 | 64865.7358 | 61888.2922 | 54657.3577 | 55189.044 | 75712.1375 | 40195.4887 | 68055.8539 | L | 1
| Fixed O&M (*total) [EUR/t_i/y] | 27.1266 | 23.8834 | 22.7774 | 20.119 | 20.2998 | 27.8604 | 14.7915 | 25.0531 | L | [1, 4]
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | P
| Output of recovered condensate [t/MWh_i] | 0.11 | 0.11 | 0.11 | 0.12 | 0.1 | 0.14 | 0.1 | 0.14 | [D, K]
| Output of recovered condensate [EUR/t_i] | 18.4176 | 18.4176 | 18.4282 | 18.4495 | 15.6741 | 21.2356 | 13.8664 | 23.0433 | K | [1, 4]
| Incineration capacity [t_i/h] | 27.16 | 27.16 | 27.16 | 27.16 | 27.16 | 27.16 | 27.16 | 27.16 | [A, B]
| Flue gas condensation | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [D, P]
| Combustion air humidification | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [D, P]
| Additional heat potential with heat pumps (of thermal input) [] | 4.151% | 4.151% | 4.015% | 3.74% | 1% | 6% | 1% | 6% | [A, B, D]
Notes:
A. Assumed lower heating value 10.6 MJ/kg, waste input 27.2 tph = tonnes per hour (incineration capacity), corresponding to thermal input of 80 MW. Live steam pressure in base case 50 bara, temperature 425 °C of 2015 and 2020, increasing to 440 °C and 450 °C, in 2030 and 2050, restpectively. Efficiencies refer to lower heating value.
B. With flue gas condensation (condensation through heat exchange with DH-water, only) and a back-pressure turbine/condenser system optimised for DH return temperature 40°C and flow 80°C
C. Annual average heat output is higher than nameplate because the total efficiency is constant, and the annual average electricity generation is lower than nameplate electricity output. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 and 2050.
E. Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
F. Regulation and start-up refer to electricity generation controlled by the turbine operation.The WtE facility would usually be operating at 100% thermal input, and the electricity output is controlled to the desired level by use of turbine by-pass, by which excess steam is used to produce DH-energy. Warm start-up time refers to 2 days down-time of the turbine.
G. The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (in stead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the requirement of min. 2 sec residence time of the flue gas at min. 850 °C after the last air injection. Below this limit it may also be a challenge to ensure sufficient superheating of the steam. Warm start-up of the combustion process is typically 8 hours and cold start-up is 8 hours.
H. Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream the flue gas treatment system. Sulphur content in fuel 270 g/GJ.
I. Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2020 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2030. The SCR-technology entails additional investment.
J. N2O is expected to be related primarily to the use of SNCR using urea injection. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
K. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
L. Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
M. Installation includes civils works (including waste bunker) and project cost
N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract.
O. Through a turbine by-pass all the produced steam energy can be used for District Heat production. It can be assumed that all electricity production is converted into heat production in by-pass.
P. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll present work, range of WtE-projects
2. Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.
3. Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013," http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkendelseovn5Juni2013.pdf
4. Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
5. Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook, Serge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019 https://eippcb.jrc.ec.europa.eu/reference/BREF/WI/JRC118637_WI_Bref_2019_published.pdf

## 08 WtE CHP, Small
Technology |  | Waste CHP - back pressure - waste - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 7.96 | 7.96 | 8.12 | 8.34 | 7.25 | 8.62 | 7.25 | 9.19 | [A, B]
| Electrical efficiency (net, annual average) [] | 21.59% | 21.59% | 22.03% | 22.64% | 18% | 24% | 18% | 25% | [A, B, C]
| Electrical efficiency (net, name plate) [] | 22.73% | 22.73% | 23.19% | 23.83% | 20% | 25% | 20% | 27% | [A, B, C]
| Cb coefficient (40°C/80°C) | 0.29 | 0.29 | 0.29 | 0.3 | 0.26 | 0.31 | 0.26 | 0.33 | [A, B]
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [A, B]
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.91% | 2.91% | 2.922% | 2.939% | 2.147% | 3.229% | 1.718% | 3.3% | [A, B]
Forced outage [] | bar: ctrl to upper; -
| Planned outage [weeks per year] | 3.5 | 3.33 | 3.01 | 2.46 | 2.83 | 3.83 | 1.85 | 3.08 | E | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 1.5 | 3 |  | 1
| Space requirement [1000 m2/MW_e] | 2.51 | 2.51 | 2.46 | 2.4 | 2.14 | 2.89 | 1.8 | 3 |  | 1
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: -
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | [F, G]
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | [F, G]
| Warm start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [F, G]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [F, G]
Environment
| SO2 (degree of desulphuring) [] | 99.79% | 99.79% | 99.79% | 99.79% | 98.96% | 99.9% | 99.48% | 99.9% | H | 1
| NOX [g/GJ_i] | 80 | 60 | 40 | 20 | 10 | 60 | 10 | 60 | I | [2, 3, 5]
| CH4 [g/GJ_i] | 0.3 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.1 |  | 2
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | J | 2
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | J | 2
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 11.3249 | 11.0484 | 10.5699 | 9.3258 | 9.3896 | 12.9838 | 6.795 | 11.5908 | N | 1
| Nominal investment (equipment) [MEUR/MW_e] | 7.0502 | 6.8694 | 6.678 | 5.9017 | 5.8379 | 8.1773 | 4.2322 | 7.3054 | N | 1
| Nominal investment (installation) [MEUR/MW_e] | 4.2854 | 4.1791 | 3.8919 | 3.4241 | 3.5517 | 4.8064 | 2.5734 | 4.2854 | M | 1
| Variable O&M (*total) [EUR/MWh_e] | 27.5201 | 27.5201 | 26.9884 | 26.2653 | 23.4155 | 31.6991 | 19.7468 | 32.8157 | K | 1
| Fixed O&M (*total) [EUR/MW_e/y] | 451933.4052 | 437046.1871 | 406208.3783 | 348786.2515 | 371117.0786 | 508292.1592 | 257336.1978 | 433856.0689 | L | 1
Technology-specific data
| Heat efficiency (net, annual average) [] | 80.3% | 80.3% | 80.09% | 80.49% | 77% | 86% | 74% | 88% | [A, B, C]
| Heat efficiency (net, name plate) [] | 79.16% | 79.16% | 78.93% | 79.3% | 75% | 85% | 72% | 86% | [A, B]
| Nominal investment (*total) [MEUR/MW_i] | 3.2539 | 2.5096 | 2.4458 | 2.2224 | 2.1374 | 2.9455 | 1.6163 | 2.7648 | N | 1
| Nominal investment (*total) [MEUR/t_i] | 946.4017 | 925.1343 | 903.8668 | 818.797 | 786.8958 | 1084.6402 | 595.4887 | 1020.8378 | N | 1
| Nominal investment (equipment) [MEUR/MW_i] | 2.0204 | 1.5632 | 1.5525 | 1.4037 | 1.3292 | 1.8609 | 1.0102 | 1.7439 | N | 1
| Nominal investment (installation) [MEUR/MW_i] | 1.2335 | 0.9464 | 0.90387 | 0.8188 | 0.80816 | 1.0953 | 0.61676 | 1.0208 | M | 1
| Variable O&M (*total) [EUR/MWh_i] | 6.2526 | 6.2526 | 6.2526 | 6.2633 | 5.3169 | 7.2097 | 4.7107 | 7.8264 | K | 1
| Fixed O&M (*total) [EUR/MW_i/y] | 102615.4672 | 99319.0118 | 94214.8228 | 83049.4092 | 84431.7938 | 115375.9398 | 61356.6058 | 103466.1654 | L | 1
| Fixed O&M (*total) [EUR/t_i/y] | 37.8029 | 36.5481 | 34.6766 | 30.5613 | 31.0718 | 42.4924 | 22.5754 | 38.09 | L | [1, 4]
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | O
| Output of recovered condensate [t/MWh_i] | 0.11 | 0.11 | 0.11 | 0.12 | 0.1 | 0.14 | 0.1 | 0.14 | [D, K]
| Output of recovered condensate [EUR/t_i] | 18.4176 | 18.4176 | 18.4282 | 18.4389 | 15.6741 | 21.2249 | 13.8664 | 23.0433 | K | [1, 4]
| Incineration capacity [t_i/h] | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | [A, B]
| Flue gas condensation | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [D, O]
| Combustion air humidification | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [D, O]
| Additional heat potential with heat pumps (of thermal input) [] | 4.151% | 4.151% | 4.015% | 3.877% | 1% | 6% | 1% | 6% | [A, B, D]
Notes:
A. Assumed lower heating value 10.6 MJ/kg, waste input 11.9 tph = tonnes per hour (incineration capacity), corresponding to thermal input of 35 MW. Live steam pressure in base case 50 bara, temperature 425 °C of 2015 and 2020, increasing to 440 °C and 450 °C, in 2030 and 2050, respectively. Efficiencies refer to lower heating value.
B. With flue gas condensation (condensation through heat exchange with DH-water, only) and a back-pressure turbine/condenser system optimised for DH return temperature 40°C and flow 80°C
C. Annual average heat output is higher than nameplate because the total efficiency is constant, and the annual average electricity generation is lower than nameplate electricity output. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 and 2050.
E. Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
F. Regulation and start-up refer to electricity generation controlled by the turbine operation.The WtE facility would usually be operating at 100% thermal input, and the electricity output is controlled to the desired level by use of turbine by-pass, by which excess steam is used to produce DH-energy. Warm start-up time refers to 2 days down-time of the turbine.
G. The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (in stead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the requirement of min. 2 sec residence time of the flue gas at min. 850 °C after the last air injection. Below this limit it may also be a challenge to ensure sufficient superheating of the steam. Warm start-up of the combustion process is typically 8 hours and cold start-up is 8 hours.
H. Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream the flue gas treatment system. Sulphur content in fuel 270 g/GJ.
I. Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2020 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2030. The SCR-technology entails additional investment.
J. N2O is expected to be related primarily to the use of SNCR using urea injection. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
K. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
L. Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
M. Installation includes civils works (including waste bunker) and project cost
N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract..
O. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll present work, range of WtE-projects
2. Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf
3. Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013," http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkendelseovn5Juni2013.pdf
4. Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
5. Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook, Serge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019 https://eippcb.jrc.ec.europa.eu/reference/BREF/WI/JRC118637_WI_Bref_2019_published.pdf

## 08 WtE HOP
Technology |  | Waste boiler - boiler - waste - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 36.95 | 36.95 | 37.04 | 37.21 | 36.26 | 37.92 | 36.26 | 38.08 | [A, B]
| Heat efficiency (net, annual average) [] | 105.6% | 105.6% | 105.8% | 106.3% | 103% | 109% | 103% | 109% | [A, B, C]
| Heat efficiency (net, name plate) [] | 105.6% | 105.6% | 105.8% | 106.3% | 103% | 109% | 103% | 109% | [A, B, C]
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.585% | 2.585% | 2.55% | 2.484% | 1.903% | 2.773% | 1.49% | 2.761% | [A, B, C]
Forced outage [] | bar: ctrl to upper; -
| Planned outage [weeks per year] | 3 | 2.85 | 2.58 | 2.11 | 2.43 | 3.28 | 1.58 | 2.64 | E | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 2 | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 |  | 1
| Space requirement [1000 m2/MW_h] | 0.54 | 0.54 | 0.54 | 0.54 | 0.46 | 0.62 | 0.4 | 0.67 |  | 1
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) [] | bar: ctrl to -
| Minimum load (of full load) [] | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | G
| Warm start-up time [hours] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | G
| Cold start-up time [hours] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | G
Environment
| SO2 (degree of desulphuring) [] | 99.79% | 99.79% | 99.79% | 99.79% | 98.96% | 99.9% | 99.48% | 99.9% | H | 1
| NOX [g/GJ_i] | 80 | 60 | 40 | 20 | 10 | 60 | 10 | 60 | I | [2, 3, 5]
| CH4 [g/GJ_i] | 0.3 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.1 |  | 2
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | J | 2
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | J | 2
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 1.8928 | 1.8503 | 1.8184 | 1.6376 | 1.6163 | 2.2437 | 1.3079 | 2.2437 | P
| Nominal investment (equipment) [MEUR/MW_h] | 1.0846 | 1.0634 | 1.0634 | 0.96767 | 0.92513 | 1.3079 | 0.75499 | 1.3079 | P
| Nominal investment (installation) [MEUR/MW_h] | 0.80816 | 0.7869 | 0.74436 | 0.66992 | 0.69119 | 0.92513 | 0.56359 | 0.93577 | P
| Variable O&M (*total) [EUR/MWh_h] | 7.6776 | 7.8477 | 8.6771 | 9.0068 | 6.7205 | 8.9111 | 7.2947 | 10.857 | [K, P]
| Variable O&M (electricity cost) [EUR/MWh_h] | 1.7333 | 1.8928 | 2.7435 | 3.0944 | 1.7758 | 1.9353 | 2.9455 | 3.2752 | [K, P]
| Variable O&M (other O&M) [EUR/MWh_h] | 5.9443 | 5.9443 | 5.9336 | 5.9124 | 4.934 | 6.9864 | 4.3492 | 7.5818 | [K, P]
| Fixed O&M (*total) [EUR/MW_h/y] | 85814.1783 | 82943.072 | 78583.2439 | 68800.2149 | 71033.2976 | 97298.6037 | 52530.6123 | 88791.622 | P
Technology-specific data
| Nominal investment (*total) [MEUR/MW_i] | 1.9991 | 1.9566 | 1.9247 | 1.7439 | 1.7014 | 2.3607 | 1.393 | 2.382 | N | 1
| Nominal investment (*total) [MEUR/t_i] | 733.7272 | 723.0934 | 701.826 | 638.0236 | 627.3899 | 871.9656 | 510.4189 | 882.5994 | N | 1
| Nominal investment (equipment) [MEUR/MW_i] | 1.1484 | 1.1165 | 1.1272 | 1.0315 | 0.9783 | 1.3824 | 0.79753 | 1.393 | N | 1
| Nominal investment (installation) [MEUR/MW_i] | 0.8507 | 0.82943 | 0.7869 | 0.71246 | 0.72309 | 0.9783 | 0.59549 | 0.98894 | M | 1
| Variable O&M (*total) [EUR/MWh_i] | 8.1029 | 8.2837 | 9.1769 | 9.5704 | 7.2735 | 9.2407 | 7.9328 | 11.2505 | K | 1
| Variable O&M (electricity cost) [EUR/t_i] | 5.3807 | 5.9017 | 8.5389 | 9.6767 | 5.6784 | 5.9017 | 9.4321 | 10.0063 | K | [1, 4]
| Variable O&M (other O&M) [EUR/t_i] | 18.4921 | 18.4921 | 18.5027 | 18.524 | 15.7485 | 21.31 | 13.9408 | 23.1284 | K | [1, 4]
| Fixed O&M (*total) [EUR/MW_i/y] | 90599.3555 | 87515.5747 | 83155.7465 | 73160.043 | 74967.7766 | 102721.8045 | 55933.4049 | 94427.4973 | L | 1
| Fixed O&M (*total) [EUR/t_i/y] | 33.3367 | 32.2202 | 30.6039 | 26.9459 | 27.6158 | 37.8242 | 20.5763 | 34.751 | L | [1, 4]
| Output of recovered condensate [t/MWh_i] | 0.13824 | 0.13824 | 0.14887 | 0.14887 | 0.1276 | 0.18077 | 0.1276 | 0.18077 | [D, K]
| Output of recovered condensate [EUR/t_i] | 23.8834 | 24.3938 | 27.0416 | 28.2006 | 21.427 | 27.2117 | 23.3729 | 33.1347 | K | [1, 4]
| Incineration capacity [t_i/h] | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | [A, B]
| Flue gas condensation | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [D, O]
| Combustion air humidification | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [D, O]
| Additional heat potential with heat pumps (of thermal input) [] | 4.151% | 4.151% | 4.015% | 3.74% | 1% | 6% | 1% | 6% | [A, B, D]
Notes:
A. Assumed lower heating value 10.6 MJ/kg, waste input 11.9 tph = tonnes per hour (incineration capacity), corresponding to thermal input of 35 MW. Efficiencies refer to lower heating value.
B. With flue gas condensation (condensation through heat exchange with DH-water, only), DH return temperature 40°C and flow 80°C.
C. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency.
D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 and 2050.
E. Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
G. The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (instead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the requirement of min. 2 sec residence time of the flue gas at min. 850 °C after the last air injection. Below this limit it may also be a challenge to ensure sufficient superheating of the steam. Warm start-up of the combustion process is typically 8 hours and cold start-up is 8 hours.
H. Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream of the flue gas treatment system. Sulphur content in fuel 270 g/GJ
I. Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2020 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2030. The SCR-technology entails additional investment.
J. N2O is expected to be related primarily to the use of SNCR. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
K. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
L. Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
M. Installation includes civils works (including waste bunker) and project cost .
N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract.
O. Binary value where 1 = yes and 0 = no
P. Reference to heat output because of the lack of electricity production.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll present work, range of WtE-projects
2. Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.
3. Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013," http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkendelseovn5Juni2013.pdf
4. Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
5. Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook, Serge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019 https://eippcb.jrc.ec.europa.eu/reference/BREF/WI/JRC118637_WI_Bref_2019_published.pdf

## 09a Wood Chips, Large 40 degree
Technology |  | Biomass CHP, 40/80 degree - back pressure - wood chips - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 182.24 | 182.62 | 183.28 | 180.08 | 166.32 | 242.89 | 174.4 | 251.01 | A
| Electrical efficiency (net, annual average) [] | 28.85% | 28.92% | 29.02% | 28.51% | 24% | 39% | 26% | 40% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 30.37% | 30.44% | 30.55% | 30.01% | 27% | 41% | 29% | 42% | [A, H] | 1
| Cb coefficient (40°C/80°C) | 0.37 | 0.37 | 0.38 | 0.37 | 0.34 | 0.5 | 0.35 | 0.51
Cv coefficient (40°C/80°C) | bar: ctrl to -
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.962% | 2.941% | 2.943% | 2.935% | 2.181% | 3.272% | 1.799% | 3.432% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 5 | 5 | 5 | 5 | 4.5 | 5.5 | 4 | 5.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.08 | 0.08 | 0.08 | 0.08 | 0.07 | 0.09 | 0.06 | 0.1 |  | 1
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to upper
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 45% | 45% | 45% | 45% | 45% | 45% | 45% | 45%
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [E, G] | 1
| Cold start-up time [hours] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.97% | 97.97% | 97.97% | 97.97% | 94.92% | 98.98% | 97.97% | 98.98% | F | [1, 2, 3]
| NOX [g/GJ_i] | 30 | 20 | 20 | 10 | 10 | 30 | 10 | 20 | F | [1, 2, 3]
| CH4 [g/GJ_i] | 3 | 2 | 2 | 1 | 1 | 3 | 0 | 3 | F | [1, 2, 3]
| N2O [g/GJ_i] | 10 | 8 | 6 | 5 | 5 | 10 | 3 | 10 | F | [1, 2, 3]
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | [1, 2, 3]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 3.5942 | 3.4985 | 3.3177 | 3.1263 | 2.9668 | 4.1897 | 2.467 | 4.2854 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 2.3288 | 2.265 | 2.148 | 2.0417 | 1.8928 | 2.7435 | 1.5738 | 2.7967 | K
| Nominal investment (installation) [MEUR/MW_e] | 1.2654 | 1.2335 | 1.1697 | 1.074 | 1.074 | 1.4568 | 0.89323 | 1.4887 | K
| Variable O&M (*total) [EUR/MWh_e] | 4.6682 | 4.6682 | 4.6469 | 4.732 | 3.3071 | 5.2424 | 2.9562 | 5.7103 | L
| Fixed O&M (*total) [EUR/MW_e/y] | 103147.1536 | 101020.4082 | 94640.1719 | 89323.3083 | 85069.8174 | 118034.3717 | 68055.854 | 116970.999 | 0
Technology-specific data
| Heat efficiency (net, annual average) [] | 82.91% | 83.07% | 82.96% | 83.48% | 47% | 87% | 46% | 85% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 81.4% | 81.55% | 81.43% | 81.98% | 44% | 85% | 43% | 83% | [B, H] | 1
| Nominal investment (*total) [MEUR/MW_i] | 1.0953 | 1.0634 | 1.0102 | 0.93577 | 0.90387 | 1.276 | 0.74436 | 1.2867 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.70183 | 0.69119 | 0.65929 | 0.61676 | 0.57422 | 0.82943 | 0.46788 | 0.84006 | K
| Nominal investment (installation) [MEUR/MW_i] | 0.38281 | 0.37218 | 0.36155 | 0.31901 | 0.32965 | 0.44662 | 0.26584 | 0.44662 | K
| Variable O&M (*total) [EUR/MWh_i] | 1.4143 | 1.4249 | 1.4249 | 1.4249 | 1.0102 | 1.5951 | 0.8826 | 1.712 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 31369.4952 | 30625.1343 | 29030.0752 | 26690.6552 | 25839.957 | 36048.3351 | 20310.4189 | 34984.9624
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0.010634 | 0.010634 | 0.010634 | 0.010634 | 0.010634 | 0.010634 | 0.010634 | 0.010634 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | M
| Output of recovered condensate [t/MWh_i] | 0.22 | 0.22 | 0.22 | 0.22 | 0 | 0.22 | 0 | 0.22 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.943% | 1.869% | 1.869% | 1.87% | 1% | 28% | 1% | 28% | C | 1
Notes:
A. The boiler in the plant is a circulating fluid bed boiler (CFB) producing steam to be used in a subsequent back-pressure steam turbine without steam re-heat. The system is optimised at DH return temperature 40°C and flow 80°C. At DH return temperature 40 °C and flow 80 °C, for year 2015, the name plate net electricity efficiency increases by about 2.1%-point, to 30.4% and the net name plate heat efficiency is increased about 0.5%-point, to 81.4%, the Cb coefficient increases about 0.02, and the additional heat potential with heat pumps reduced by around 2.7%-point. Other cases experience similar changes.
B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator). Warm start-up time is particularly low for fluid bed types of plants.
F. It is to be expected that the NOx level is low from the CFB, and that the necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 20 g/GJ, in which case SCR is used. From 2017 NOx (and other emissions) must fulfill the BAT_AEL values of the LCP BREF note. The N2O level is relatively high due to the use of a CFB.
G. Warm start is starting with a glowing bed and a warm deaerator.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
3. Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.

## 09a Wood Chips, Large 50 degree
Technology |  | Biomass CHP, 50/100 degree - back pressure - wood chips - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 169.53 | 169.84 | 170.47 | 167.48 | 153.68 | 230.21 | 162.19 | 238.75 | A
| Electrical efficiency (net, annual average) [] | 26.84% | 26.89% | 26.99% | 26.52% | 23% | 37% | 24% | 38% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 28.25% | 28.31% | 28.41% | 27.91% | 25% | 39% | 27% | 40% | [A, H] | 1
| Cb coefficient (50°C/100°C) | 0.35 | 0.35 | 0.35 | 0.34 | 0.32 | 0.47 | 0.33 | 0.49
Cv coefficient (50°C/100°C) | bar: ctrl to -
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.978% | 2.956% | 2.958% | 2.95% | 2.202% | 3.289% | 1.816% | 3.449% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 5 | 5 | 5 | 5 | 4.5 | 5.5 | 4 | 5.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.09 | 0.09 | 0.09 | 0.09 | 0.08 | 0.1 | 0.07 | 0.11 |  | 1
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to upper
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 45% | 45% | 45% | 45% | 45% | 45% | 45% | 45%
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [E, G] | 1
| Cold start-up time [hours] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.97% | 97.97% | 97.97% | 97.97% | 94.92% | 98.98% | 97.97% | 98.98% | F | [1, 2, 3]
| NOX [g/GJ_i] | 30 | 20 | 20 | 10 | 10 | 30 | 10 | 20 | F | [1, 2, 3]
| CH4 [g/GJ_i] | 3 | 2 | 2 | 1 | 1 | 3 | 0 | 3 | F | [1, 2, 3]
| N2O [g/GJ_i] | 10 | 8 | 6 | 5 | 5 | 10 | 3 | 10 | F | [1, 2, 3]
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | [1, 2, 3]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 3.86 | 3.7537 | 3.5623 | 3.3603 | 3.1901 | 4.5087 | 2.6478 | 4.6044 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 2.4989 | 2.4351 | 2.3075 | 2.2012 | 2.0417 | 2.9455 | 1.6908 | 3.0093 | K
| Nominal investment (installation) [MEUR/MW_e] | 1.3611 | 1.3292 | 1.2548 | 1.1591 | 1.1591 | 1.5632 | 0.95704 | 1.5951 | K
| Variable O&M (*total) [EUR/MWh_e] | 4.8915 | 4.8915 | 4.8702 | 4.966 | 3.5517 | 5.5189 | 3.1795 | 6.0187 | L
| Fixed O&M (*total) [EUR/MW_e/y] | 111654.1354 | 108464.0172 | 102083.7809 | 95703.5446 | 91450.0537 | 127604.7262 | 73372.7175 | 125477.9807 | 0
Technology-specific data
| Heat efficiency (net, annual average) [] | 82.28% | 82.55% | 82.45% | 82.94% | 48% | 86% | 48% | 85% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 80.87% | 81.14% | 81.03% | 81.54% | 46% | 84% | 45% | 83% | [B, H] | 1
| Nominal investment (*total) [MEUR/MW_i] | 1.0953 | 1.0634 | 1.0102 | 0.93577 | 0.90387 | 1.276 | 0.74436 | 1.2867 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.70183 | 0.69119 | 0.65929 | 0.61676 | 0.57422 | 0.82943 | 0.46788 | 0.84006 | K
| Nominal investment (installation) [MEUR/MW_i] | 0.38281 | 0.37218 | 0.36155 | 0.31901 | 0.32965 | 0.44662 | 0.26584 | 0.44662 | K
| Variable O&M (*total) [EUR/MWh_i] | 1.3824 | 1.3824 | 1.3824 | 1.3824 | 1.0102 | 1.5632 | 0.8826 | 1.6801 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 31369.4952 | 30625.1343 | 29030.0752 | 26690.6552 | 25839.957 | 36048.3351 | 20310.4189 | 34984.9624
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0.010634 | 0.010634 | 0.010634 | 0.010634 | 0.010634 | 0.010634 | 0.010634 | 0.010634 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | M
| Output of recovered condensate [t/MWh_i] | 0.19 | 0.19 | 0.19 | 0.19 | 0 | 0.19 | 0 | 0.19 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 4.639% | 4.462% | 4.462% | 4.464% | 4% | 28% | 4% | 28% | C | 1
Notes:
A. The boiler in the plant is a circulating fluid bed boiler (CFB) producing steam to be used in a subsequent back-pressure steam turbine without steam re-heat. The system is optimised at DH return temperature 50°C and flow 100°C. At DH return temperature 40 °C and flow 80 °C, for year 2015, the name plate net electricity efficiency increases by about 2.1%-point, to 30.4% and the net name plate heat efficiency is increased about 0.5%-point, to 81.4%, the Cb coefficient increases about 0.02, and the additional heat potential with heat pumps reduced by around 2.7%-point. Other cases experience similar changes.
B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator). Warm start-up time is particularly low for fluid bed types of plants.
F. It is to be expected that the NOx level is low from the CFB, and that the necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 20 g/GJ, in which case SCR is used. From 2017 NOx (and other emissions) must fulfill the BAT_AEL values of the LCP BREF note. The N2O level is relatively high due to the use of a CFB.
G. Warm start is starting with a glowing bed and a warm deaerator.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
3. Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.

## 09a Wood Chips, Medium
Technology |  | Biomass CHP - back pressure - wood chips - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 23.77 | 23.77 | 23.86 | 23.43 | 22.17 | 31.78 | 22.74 | 32.73 | A
| Electrical efficiency (net, annual average) [] | 28.23% | 28.23% | 28.33% | 27.82% | 24% | 38% | 25% | 39% | [A, H, F] | 1
| Electrical efficiency (net, name plate) [] | 29.71% | 29.71% | 29.83% | 29.29% | 27% | 40% | 28% | 41% | [A, H, F] | 1
| Cb coefficient (40°C/80°C) | 0.37 | 0.37 | 0.37 | 0.36 | 0.34 | 0.49 | 0.35 | 0.5
Cv coefficient (40°C/80°C) | bar: ctrl to -
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.961% | 2.961% | 2.963% | 2.955% | 2.185% | 3.271% | 1.799% | 3.431% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 1.5 | 3 |  | 1
| Space requirement [1000 m2/MW_e] | 0.21 | 0.21 | 0.21 | 0.21 | 0.18 | 0.24 | 0.16 | 0.27
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20%
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [E, G] | 1
| Cold start-up time [hours] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.97% | 97.97% | 97.97% | 97.97% | 94.92% | 98.98% | 97.97% | 98.98% | F | [1, 2, 3]
| NOX [g/GJ_i] | 90 | 60 | 40 | 20 | 40 | 60 | 20 | 40 | F | [1, 2, 3]
| CH4 [g/GJ_i] | 3 | 2 | 2 | 1 | 1 | 3 | 0 | 3 | F | [1, 2, 3]
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | [1, 2, 3]
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | [1, 2, 3]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 3.86 | 3.7643 | 3.5729 | 3.4028 | 3.1582 | 4.4449 | 2.6159 | 4.6576 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 2.584 | 2.5202 | 2.3926 | 2.3075 | 2.0736 | 2.9774 | 1.7227 | 3.1476 | K
| Nominal investment (installation) [MEUR/MW_e] | 1.276 | 1.2441 | 1.1803 | 1.0846 | 1.0846 | 1.4675 | 0.90387 | 1.4994 | K
| Variable O&M (*total) [EUR/MWh_e] | 4.7745 | 4.7745 | 4.7533 | 4.8383 | 3.3815 | 5.3807 | 3.0306 | 5.8592 | L
| Fixed O&M (*total) [EUR/MW_e/y] | 163759.3986 | 158442.535 | 148872.1805 | 137175.0806 | 133984.9625 | 183963.4802 | 103147.1536 | 177583.2439 | 0
Technology-specific data
| Heat efficiency (net, annual average) [] | 82.72% | 82.72% | 82.61% | 83.15% | 49% | 86% | 46% | 85% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 81.24% | 81.24% | 81.12% | 81.68% | 46% | 84% | 43% | 83% | [B, H] | 1
| Nominal investment (*total) [MEUR/MW_i] | 1.1484 | 1.1165 | 1.0634 | 0.99957 | 0.93577 | 1.3186 | 0.76563 | 1.3611 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.76563 | 0.75499 | 0.71246 | 0.68056 | 0.61676 | 0.8826 | 0.49979 | 0.92513 | K
| Nominal investment (installation) [MEUR/MW_i] | 0.38281 | 0.37218 | 0.35091 | 0.31901 | 0.31901 | 0.43598 | 0.26584 | 0.43598 | K
| Variable O&M (*total) [EUR/MWh_i] | 1.4143 | 1.4143 | 1.4143 | 1.4143 | 1.0102 | 1.5951 | 0.8826 | 1.712 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 48702.4705 | 47213.7487 | 44448.9796 | 40195.4887 | 39663.8024 | 54763.695 | 30093.4479 | 51892.5886
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0.010634 | 0.010634 | 0.010634 | 0.010634 | 0.010634 | 0.021267 | 0.010634 | 0.021267 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | M
| Output of recovered condensate [t/MWh_i] | 0.22 | 0.22 | 0.22 | 0.22 | 0 | 0.22 | 0 | 0.22 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.943% | 1.943% | 1.943% | 1.944% | 1% | 26% | 1% | 28% | C | 1
Notes:
A. The boiler in the plant is a grate fired boiler producing steam to be used in a subsequent back pressure steam turbine. Though a grate is reasonable flexible with respect to combusting different fuels the fuel feed system will be dependent on the type of fuel. It is to be expected that it is necessary with a specific DeNOx plant (SNCR might not be sufficient). The system is optimised at DH return temperature 40°C and flow 80°C.
B. Through a turbine by-pass all the produced steam energy is used for District Heat production.
C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. It is to be expected that necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 40 g/GJ in which case SCR is used with slight adverse effect on electricity efficiency. From 2017 NOx (and other emissions) must fulfill the BAT_AEL values of the LCP BREF note.
G. Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
3. Emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.

## 09a Wood Chips, Small
Technology |  | Biomass CHP - back pressure - wood chips - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 2.93 | 2.93 | 2.94 | 2.89 | 2.85 | 2.97 | 2.79 | 2.98 | A
| Electrical efficiency (net, annual average) [] | 13.93% | 13.93% | 13.99% | 13.71% | 12% | 15% | 12% | 15% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 14.66% | 14.66% | 14.72% | 14.43% | 14% | 15% | 13% | 15% | [A, H] | 1
| Cb coefficient (40°C/80°C) | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.14 | 0.15
Cv coefficient (40°C/80°C) | bar: ctrl to -
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.734% | 2.734% | 2.735% | 2.73% | 2.08% | 2.989% | 1.661% | 2.99% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.68 | 0.68 | 0.68 | 0.69 | 0.58 | 0.78 | 0.52 | 0.87
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | D | 1
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | D | 1
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | G | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.97% | 97.97% | 97.97% | 97.97% | 94.92% | 98.98% | 97.97% | 98.98% | F | [1, 2]
| NOX [g/GJ_i] | 90 | 60 | 40 | 30 | 40 | 80 | 20 | 40 | F | [1, 2]
| CH4 [g/GJ_i] | 20 | 10 | 8 | 4 | 4 | 16 | 2 | 16 | F | [1, 2]
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | [1, 2]
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | [1, 2]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 6.8907 | 6.7205 | 6.3696 | 6.1676 | 5.8592 | 7.9221 | 4.8702 | 8.4113 | [E, J, K] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 4.2748 | 4.1684 | 3.9557 | 3.9345 | 3.6367 | 4.9234 | 3.02 | 5.3275 | K
| Nominal investment (installation) [MEUR/MW_e] | 2.6053 | 2.5415 | 2.4139 | 2.2224 | 2.2224 | 2.9987 | 1.8396 | 3.0731 | K
| Variable O&M (*total) [EUR/MWh_e] | 9.8468 | 9.8468 | 9.8043 | 10.0063 | 6.8588 | 11.0697 | 6.1463 | 12.0693 | L
| Fixed O&M (*total) [EUR/MW_e/y] | 303061.2246 | 298807.7338 | 290300.752 | 287110.6339 | 256272.825 | 346659.5061 | 217991.4072 | 368990.3331 | 0
Technology-specific data
| Heat efficiency (net, annual average) [] | 97.32% | 97.32% | 97.26% | 97.55% | 73% | 98% | 70% | 98% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 96.58% | 96.58% | 96.52% | 96.82% | 71% | 98% | 69% | 98% | [B, H] | 1
| Nominal investment (*total) [MEUR/MW_i] | 1.0102 | 0.98894 | 0.93577 | 0.89323 | 0.86133 | 1.1591 | 0.70183 | 1.2122 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.62739 | 0.61676 | 0.58485 | 0.56359 | 0.53169 | 0.72309 | 0.43598 | 0.76563 | K
| Nominal investment (installation) [MEUR/MW_i] | 0.38281 | 0.37218 | 0.35091 | 0.31901 | 0.32965 | 0.43598 | 0.26584 | 0.44662 | K
| Variable O&M (*total) [EUR/MWh_i] | 1.4462 | 1.4462 | 1.4462 | 1.4462 | 1.0102 | 1.627 | 0.8826 | 1.7439 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 44448.9796 | 43810.956 | 42747.5832 | 41471.536 | 37537.0569 | 50829.2159 | 31475.8324 | 53274.9731
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.010634 | 0.021267 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Output of recovered condensate [t/MWh_i] | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0.25 | 0 | 0.25 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.943% | 1.943% | 1.943% | 1.944% | 1% | 26% | 1% | 28% | C | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate. The electric power is produced by an ORC module (Organic Rankine Cycle; Waste Heat Recovery - WHR). Refer for instance to the following link for further information about technology and suppliers: http://www.enova.no/upload_images/36AC689098414B05A7112FA2EE985BDA.pdf . This is low temperature and low efficiency electric power but at an affordable price. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance. Though, the load control of the heat production is important and most units will perform better than the figure shown. Also, minimum load could be substantially lower.
E. Since electricity generation is only a secondary objective for minor heat producers, it may make more sense to relate the total investment only to the heat production capacity.
F. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However to reach NOx-levels below 40 g/GJ SCR is assumed.
G. Warm start is starting with a glowing fuel layer on the grate.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. Cv=1 describes turbine by-pass operation. During operation the turbine can be by-passed fully or partly for direct district heating production, at operator choice.
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal model and evaluation based on either existing projects, supplier offers, or pre-project studies.
2. Emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.

## 09b Wood Pellets, Large 40 degr
Technology |  | Biomass CHP, 40/80 degree - back pressure - wood pellets - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 267.52 | 268.1 | 268.84 | 268.84 | 262.35 | 348.19 | 262.35 | 348.58 | A
| Electrical efficiency (net, annual average) [] | 31.77% | 31.84% | 31.92% | 31.92% | 29% | 42% | 29% | 42% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 33.44% | 33.51% | 33.6% | 33.6% | 32% | 44% | 32% | 44% | [A, H] | 1
| Cb coefficient (40°C/80°C) | 0.51 | 0.51 | 0.52 | 0.52 | 0.5 | 0.67 | 0.5 | 0.67
Cv coefficient (40°C/80°C) | bar: ctrl to -
| Auxiliary Electricity consumption (share of heat gen.) [] | 3.284% | 3.267% | 3.27% | 3.27% | 2.408% | 3.69% | 1.926% | 3.692% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 5 | 5 | 5 | 5 | 4.5 | 5.5 | 4 | 5.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.06 | 0.06 | 0.06 | 0.06 | 0.05 | 0.06 | 0.04 | 0.07
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to upper
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% |  | 1
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | G | 1
| Cold start-up time [hours] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | E | 1
Environment
| SO2 (degree of desulphuring) [] | 98.25% | 98.25% | 98.25% | 98.25% | 95.62% | 99.12% | 98.25% | 99.12% |  | [1, 2]
| NOX [g/GJ_i] | 20 | 20 | 20 | 10 | 10 | 30 | 10 | 20 | [C, F] | [1, 2]
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | [1, 2]
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 |  | [1, 2]
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 |  | [1, 2]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 2.4564 | 2.3926 | 2.2756 | 2.0629 | 2.031 | 2.8073 | 1.6695 | 2.8286 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 1.3718 | 1.3398 | 1.2654 | 1.1591 | 1.1059 | 1.5632 | 0.9145 | 1.5738 | K
| Nominal investment (installation) [MEUR/MW_e] | 1.0846 | 1.0527 | 0.99957 | 0.90387 | 0.9145 | 1.2441 | 0.75499 | 1.2548 | K
| Variable O&M (*total) [EUR/MWh_e] | 1.829 | 1.829 | 1.8184 | 1.8184 | 1.4675 | 2.0842 | 1.2867 | 2.2544 | L
| Fixed O&M (*total) [EUR/MW_e/y] | 68055.854 | 65929.1085 | 62738.9904 | 57422.1268 | 56358.7541 | 76562.8357 | 44661.6542 | 75499.463 | 0
Technology-specific data
| Heat efficiency (net, annual average) [] | 66.82% | 66.94% | 66.85% | 66.85% | 46% | 69% | 46% | 69% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 65.15% | 65.26% | 65.17% | 65.17% | 43% | 67% | 43% | 67% | [B, H] | 1
| Nominal investment (*total) [MEUR/MW_i] | 0.8188 | 0.79753 | 0.76563 | 0.69119 | 0.68056 | 0.9464 | 0.56359 | 0.9464 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.45725 | 0.44662 | 0.42535 | 0.38281 | 0.37218 | 0.52105 | 0.30838 | 0.53169 | K
| Nominal investment (installation) [MEUR/MW_i] | 0.36155 | 0.35091 | 0.34028 | 0.30838 | 0.30838 | 0.41472 | 0.25521 | 0.42535 | K
| Variable O&M (*total) [EUR/MWh_i] | 0.60612 | 0.61676 | 0.61676 | 0.61676 | 0.48915 | 0.70183 | 0.43598 | 0.75499 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 22756.1762 | 22224.4898 | 21267.4544 | 19459.7207 | 18715.3598 | 25839.957 | 14993.5553 | 25414.6079
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | M
| Output of recovered condensate [t/MWh_i] | 0.06 | 0.06 | 0.06 | 0.06 | 0 | 0.06 | 0 | 0.06 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.73% | 1.664% | 1.664% | 1.664% | 1% | 13% | 1% | 13% | C | 1
Notes:
A. The boiler in the plant is a suspension fired boiler producing steam to be used in a subsequent steam turbine. Currently, the steam turbine is expected to be a back-pressure turbine with no re-heat. In some of the future scenarios it is assumed that the prices on electricity will allow for an increased electrical efficiency and subsequently re-heating of steam is introduced. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper ranges of 2020 and 2050.
D. This is given by grid code (Energinet.dk)
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. This plant is equiped with an SCR catalyst for DeNOx and an electrostatic precipitator for catching dust/fly ash
G. Warm start is starting with the steam system being pressurized.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949

## 09b Wood Pellets, Large 50 degr
Technology |  | Biomass CHP, 50/100 degree - back pressure - wood pellets - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 252.95 | 253.44 | 254.15 | 254.15 | 248.11 | 333.42 | 248.11 | 333.79 | A
| Electrical efficiency (net, annual average) [] | 30.04% | 30.1% | 30.18% | 30.18% | 27% | 40% | 27% | 40% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 31.62% | 31.68% | 31.77% | 31.77% | 31% | 42% | 31% | 42% | [A, H] | 1
| Cb coefficient (50°C/100°C) | 0.49 | 0.49 | 0.49 | 0.49 | 0.48 | 0.64 | 0.48 | 0.65
Cv coefficient (50°C/100°C) | bar: ctrl to -
| Auxiliary Electricity consumption (share of heat gen.) [] | 3.298% | 3.28% | 3.283% | 3.283% | 2.426% | 3.705% | 1.94% | 3.707% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 5 | 5 | 5 | 5 | 4.5 | 5.5 | 4 | 5.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.06 | 0.06 | 0.06 | 0.06 | 0.05 | 0.07 | 0.04 | 0.07
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to upper
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% |  | 1
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | G | 1
| Cold start-up time [hours] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | E | 1
Environment
| SO2 (degree of desulphuring) [] | 98.25% | 98.25% | 98.25% | 98.25% | 95.62% | 99.12% | 98.25% | 99.12% |  | [1, 2]
| NOX [g/GJ_i] | 20 | 20 | 20 | 10 | 10 | 30 | 10 | 20 | [C, F] | [1, 2]
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | [1, 2]
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 |  | [1, 2]
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 |  | [1, 2]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 2.5946 | 2.5308 | 2.4032 | 2.1799 | 2.148 | 2.9668 | 1.7652 | 2.9881 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 1.4462 | 1.4143 | 1.3398 | 1.2229 | 1.1697 | 1.6589 | 0.96767 | 1.6589 | K
| Nominal investment (installation) [MEUR/MW_e] | 1.1484 | 1.1165 | 1.0634 | 0.95704 | 0.9783 | 1.3186 | 0.79753 | 1.3186 | K
| Variable O&M (*total) [EUR/MWh_e] | 1.829 | 1.8396 | 1.829 | 1.829 | 1.5525 | 2.1055 | 1.3611 | 2.2863 | L
| Fixed O&M (*total) [EUR/MW_e/y] | 72309.3448 | 70182.5994 | 66992.4812 | 61675.6176 | 59548.8722 | 81879.6993 | 47851.7723 | 79752.9539 | 0
Technology-specific data
| Heat efficiency (net, annual average) [] | 66.14% | 66.37% | 66.28% | 66.28% | 47% | 69% | 47% | 69% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 64.56% | 64.78% | 64.69% | 64.69% | 43% | 67% | 43% | 67% | [B, H] | 1
| Nominal investment (*total) [MEUR/MW_i] | 0.8188 | 0.79753 | 0.76563 | 0.69119 | 0.68056 | 0.9464 | 0.56359 | 0.9464 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.45725 | 0.44662 | 0.42535 | 0.38281 | 0.37218 | 0.52105 | 0.30838 | 0.53169 | K
| Nominal investment (installation) [MEUR/MW_i] | 0.36155 | 0.35091 | 0.34028 | 0.30838 | 0.30838 | 0.41472 | 0.25521 | 0.42535 | K
| Variable O&M (*total) [EUR/MWh_i] | 0.57422 | 0.58485 | 0.58485 | 0.58485 | 0.48915 | 0.66992 | 0.43598 | 0.72309 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 22756.1762 | 22224.4898 | 21267.4544 | 19459.7207 | 18715.3598 | 25839.957 | 14993.5553 | 25414.6079
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | M
| Output of recovered condensate [t/MWh_i] | 0.03 | 0.03 | 0.03 | 0.03 | 0 | 0.03 | 0 | 0.03 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 4.13% | 3.973% | 3.972% | 3.972% | 3% | 13% | 3% | 13% | C | 1
Notes:
A. The boiler in the plant is a suspension fired boiler producing steam to be used in a subsequent steam turbine. Currently, the steam turbine is expected to be a back-pressure turbine with no re-heat. In some of the future scenarios it is assumed that the prices on electricity will allow for an increased electrical efficiency and subsequently re-heating of steam is introduced. The system is optimised at DH return temperature 50°C and flow 100°C.
B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper ranges of 2020 and 2050.
D. This is given by grid code (Energinet.dk)
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. This plant is equiped with an SCR catalyst for DeNOx and an electrostatic precipitator for catching dust/fly ash
G. Warm start is starting with the steam system being pressurized.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949

## 09b Wood Pellets, Medium
Technology |  | Biomass CHP - back pressure - wood pellets - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 24.68 | 24.68 | 24.75 | 24.4 | 23.84 | 33.36 | 23.78 | 34.03 | A
| Electrical efficiency (net, annual average) [] | 29.3% | 29.3% | 29.39% | 28.98% | 26% | 40% | 26% | 41% | [A, H, F] | 1
| Electrical efficiency (net, name plate) [] | 30.85% | 30.85% | 30.94% | 30.51% | 29% | 42% | 29% | 43% | [A, H, F] | 1
| Cb coefficient (40°C/80°C) | 0.46 | 0.46 | 0.46 | 0.45 | 0.44 | 0.62 | 0.44 | 0.63
Cv coefficient (40°C/80°C) | bar: ctrl to -
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.513% | 2.513% | 2.514% | 2.508% | 1.915% | 2.942% | 1.527% | 3.051% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 1.5 | 3 |  | 1
| Space requirement [1000 m2/MW_e] | 0.18 | 0.18 | 0.18 | 0.18 | 0.16 | 0.21 | 0.14 | 0.23
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | D | 1
| Minimum load (of full load) [] | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | E | 1
| Cold start-up time [hours] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 98.25% | 98.25% | 98.25% | 98.25% | 95.62% | 99.12% | 98.25% | 99.12% | F | [1, 2]
| NOX [g/GJ_i] | 80 | 50 | 40 | 20 | 40 | 50 | 10 | 40 | F | [1, 2]
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | [1, 2]
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | [1, 2]
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | [1, 2]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 3.2752 | 3.2008 | 3.0306 | 2.8817 | 2.6584 | 3.775 | 2.2012 | 3.9451 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 2.0948 | 2.0417 | 1.9353 | 1.8822 | 1.6589 | 2.4032 | 1.3718 | 2.5627 | K
| Nominal investment (installation) [MEUR/MW_e] | 1.1803 | 1.1591 | 1.0953 | 0.99957 | 1.0102 | 1.3611 | 0.82943 | 1.393 | K
| Variable O&M (*total) [EUR/MWh_e] | 1.9779 | 1.9779 | 1.9672 | 1.9991 | 1.5951 | 2.265 | 1.4143 | 2.4777 | L
| Fixed O&M (*total) [EUR/MW_e/y] | 136111.7079 | 131858.217 | 124414.608 | 114844.2535 | 110590.7627 | 153125.6714 | 86133.1902 | 148872.1805 | 0
Technology-specific data
| Heat efficiency (net, annual average) [] | 69.23% | 69.23% | 69.14% | 69.57% | 47% | 73% | 45% | 73% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 67.69% | 67.69% | 67.6% | 68.05% | 44% | 71% | 42% | 71% | [A, H, F] | 1
| Nominal investment (*total) [MEUR/MW_i] | 1.0102 | 0.98894 | 0.93577 | 0.8826 | 0.8188 | 1.1591 | 0.66992 | 1.2016 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.64866 | 0.62739 | 0.59549 | 0.57422 | 0.51042 | 0.74436 | 0.41472 | 0.77626 | K
| Nominal investment (installation) [MEUR/MW_i] | 0.36155 | 0.35091 | 0.34028 | 0.30838 | 0.30838 | 0.42535 | 0.25521 | 0.42535 | K
| Variable O&M (*total) [EUR/MWh_i] | 0.60612 | 0.60612 | 0.60612 | 0.60612 | 0.48915 | 0.70183 | 0.43598 | 0.75499 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 42003.2223 | 40727.1751 | 38494.0924 | 35197.6369 | 34134.2642 | 47213.7487 | 26158.9689 | 45406.015
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | M
| Output of recovered condensate [t/MWh_i] | 0.06 | 0.06 | 0.06 | 0.06 | 0 | 0.06 | 0 | 0.06 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.729% | 1.729% | 1.729% | 1.73% | 1% | 11% | 1% | 13% | C | 1
Notes:
A. The boiler in the plant is a suspension fired boiler producing steam to be used in a subsequent back pressure steam turbine. It is possible to pulverize wood pellets and use it for suspension firing but it has not been possible to find an appropriate reference. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Through a turbine by-pass all the produced steam energy is used for District Heat production.
C. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper ranges of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. SNCR is assumed at NOx emissions at no less than 40 g/GJ. At lower NOx-levels it is chosen to include a tail-end SCR catalyst with slight adverse effect on electricity efficiency.
G. Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949

## 09b Wood Pellets, Small
Technology |  | Biomass CHP - boiler - wood pellets - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 3.08 | 3.08 | 3.09 | 3.05 | 3 | 3.12 | 2.95 | 3.12 | A
| Electrical efficiency (net, annual average) [] | 14.64% | 14.64% | 14.68% | 14.47% | 13% | 15% | 13% | 15% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 15.41% | 15.41% | 15.46% | 15.23% | 15% | 16% | 14% | 16% | [A, H] | 1
| Cb coefficient (40°C/80°C) | 0.18 | 0.18 | 0.19 | 0.18 | 0.18 | 0.19 | 0.18 | 0.19
Cv coefficient (40°C/80°C) | bar: ctrl to -
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.29% | 2.29% | 2.291% | 2.287% | 1.744% | 2.503% | 1.393% | 2.504% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.49 | 0.49 | 0.49 | 0.49 | 0.41 | 0.56 | 0.37 | 0.62
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | D | 1
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | D | 1
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | G | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 98.25% | 98.25% | 98.25% | 98.25% | 95.62% | 99.12% | 98.25% | 99.12% | F | 1
| NOX [g/GJ_i] | 90 | 50 | 40 | 30 | 40 | 70 | 20 | 40 | F | 1
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | 1
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | 1
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | 1
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 6.6142 | 6.444 | 6.1144 | 5.8911 | 5.6146 | 7.6031 | 4.6576 | 8.0285 | [E, J, K] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 4.3173 | 4.211 | 3.9876 | 3.9345 | 3.6686 | 4.9553 | 3.0412 | 5.3381 | K
| Nominal investment (installation) [MEUR/MW_e] | 2.2969 | 2.2437 | 2.1267 | 1.946 | 1.9566 | 2.6478 | 1.6163 | 2.701 | K
| Variable O&M (*total) [EUR/MWh_e] | 4.1365 | 4.1365 | 4.1259 | 4.1897 | 3.1795 | 4.7107 | 2.8392 | 5.1467 | L
| Fixed O&M (*total) [EUR/MW_e/y] | 292427.4975 | 288174.0066 | 277540.2794 | 269033.2977 | 246702.4706 | 333899.0335 | 204167.5619 | 345596.1334 | 0
Technology-specific data
| Heat efficiency (net, annual average) [] | 84.2% | 84.2% | 84.16% | 84.39% | 74% | 86% | 72% | 86% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 83.43% | 83.43% | 83.39% | 83.62% | 72% | 85% | 71% | 85% | [B, H] | 1
| Nominal investment (*total) [MEUR/MW_i] | 1.0208 | 0.98894 | 0.9464 | 0.89323 | 0.86133 | 1.1697 | 0.71246 | 1.2229 | [E, J, K] | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.65929 | 0.64866 | 0.61676 | 0.59549 | 0.56359 | 0.76563 | 0.45725 | 0.80816 | K
| Nominal investment (installation) [MEUR/MW_i] | 0.35091 | 0.34028 | 0.32965 | 0.29774 | 0.29774 | 0.40408 | 0.24458 | 0.41472 | K
| Variable O&M (*total) [EUR/MWh_i] | 0.63802 | 0.63802 | 0.63802 | 0.63802 | 0.48915 | 0.72309 | 0.43598 | 0.7869 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 45193.3405 | 44342.6423 | 42853.9205 | 40939.8496 | 37962.406 | 51467.2395 | 31050.4834 | 52636.9495
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Output of recovered condensate [t/MWh_i] | 0.06 | 0.06 | 0.06 | 0.06 | 0 | 0.06 | 0 | 0.06 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.729% | 1.729% | 1.729% | 1.73% | 1% | 11% | 1% | 13% | C | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate. The electric power is produced by an ORC module (Organic Rankine Cycle; Waste Heat Recovery - WHR). Refer for instance to the following link for further information about technology and suppliers: http://www.enova.no/upload_images/36AC689098414B05A7112FA2EE985BDA.pdf . This is low temperature and low efficiency electric power but at an affordable price. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper ranges of 2020 and 2050.
E. Since electricity generation is only a secondary objective for minor heat producers, it may make more sense to relate the total investment only to the thermail input.
F. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However to reach NOx-levels below 40 g/GJ SCR is assumed.
G. Warm start is starting with a glowing fuel layer on the grate.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.

## 09c Straw, Large, 40 degree
Technology |  | Biomass CHP, 40/80 degree - back pressure - straw - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 41.59 | 41.59 | 41.72 | 41.72 | 39.48 | 54.62 | 40.62 | 55.84 | A
| Electrical efficiency (net, annual average) [] | 29.94% | 29.94% | 30.03% | 30.03% | 26% | 40% | 27% | 41% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 31.51% | 31.51% | 31.61% | 31.61% | 29% | 42% | 30% | 43% | [A, H] | 1
| Cb coefficient (40°C/80°C) | 0.45 | 0.45 | 0.46 | 0.46 | 0.43 | 0.6 | 0.44 | 0.61
Cv coefficient (40°C/80°C) | bar: ctrl to -
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.838% | 2.838% | 2.84% | 2.84% | 2.091% | 3.137% | 1.729% | 3.298% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 3 | 3 | 3 | 3 | 2.5 | 3.5 | 2 | 3.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.24 | 0.24 | 0.24 | 0.24 | 0.2 | 0.28 | 0.18 | 0.3
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to upper
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40%
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | E | 1
| Cold start-up time [hours] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 95.45% | 96.36% | 99.09% | 99.82% | 90.9% | 99.82% | 95.45% | 99.91% | F | [1, 2]
| NOX [g/GJ_i] | 40 | 30 | 30 | 20 | 20 | 40 | 10 | 30 | F | [1, 2]
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | [1, 2]
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | [1, 2]
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | [1, 2]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 3.6793 | 3.5942 | 3.4134 | 3.0944 | 3.0412 | 4.2216 | 2.4989 | 4.2429 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 2.2756 | 2.2224 | 2.1055 | 1.9141 | 1.8396 | 2.6053 | 1.5206 | 2.6159 | [J, K]
| Nominal investment (installation) [MEUR/MW_e] | 1.4143 | 1.3718 | 1.3079 | 1.1803 | 1.2016 | 1.6163 | 0.9783 | 1.627 | [J, K]
| Variable O&M (*total) [EUR/MWh_e] | 2.2437 | 2.2437 | 2.2331 | 2.2331 | 1.7227 | 2.5521 | 1.51 | 2.7435 | L
| Fixed O&M (*total) [EUR/MW_e/y] | 133984.9625 | 129731.4716 | 122287.8626 | 109527.39 | 109527.39 | 150998.926 | 84006.4447 | 141428.5715 | J
Technology-specific data
| Heat efficiency (net, annual average) [] | 70.93% | 70.93% | 70.83% | 70.83% | 48% | 74% | 47% | 73% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 69.35% | 69.35% | 69.25% | 69.25% | 45% | 72% | 44% | 71% | [B, H] | 1
| Nominal investment (*total) [MEUR/MW_i] | 1.1591 | 1.1378 | 1.074 | 0.9783 | 0.95704 | 1.3292 | 0.7869 | 1.3398 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.71246 | 0.70183 | 0.66992 | 0.60612 | 0.58485 | 0.8188 | 0.47852 | 0.82943 | K
| Nominal investment (installation) [MEUR/MW_i] | 0.44662 | 0.43598 | 0.41472 | 0.37218 | 0.38281 | 0.51042 | 0.30838 | 0.51042 | K
| Variable O&M (*total) [EUR/MWh_i] | 0.70183 | 0.70183 | 0.70183 | 0.70183 | 0.54232 | 0.80816 | 0.47852 | 0.87197 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 42215.8969 | 40939.8496 | 38600.4296 | 34453.276 | 34559.6133 | 47426.4232 | 26477.9807 | 44555.3169 | J
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0.063802 | 0.063802 | 0.063802 | 0.053169 | 0.063802 | 0.074436 | 0.053169 | 0.08507 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | M
| Output of recovered condensate [t/MWh_i] | 0.09 | 0.09 | 0.09 | 0.09 | 0 | 0.09 | 0 | 0.09 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.768% | 1.768% | 1.768% | 1.768% | 1% | 15% | 1% | 15% | C | 1
Notes:
A. The boiler in the plant is grate fired producing steam to be used in a subsequent back pressure steam turbine. Though a grate is reasonable flexible with respect to combusting different fuels the fuel feed system will be dependent on the type of fuel used. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C. Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. For NOx-emissions no lower than 40 g/GJ SNCR is assumed. It is probably necessary to include a tail-end SCR catalyst to fulfill expected BREF requirements, particularly after year 2030. This has slight adverse effect on the electricity efficiency.
G. Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949

## 09c Straw, Large, 50 degree
Technology |  | Biomass CHP, 50/100 degree - back pressure - straw - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 38.99 | 38.99 | 39.11 | 39.11 | 36.88 | 52.01 | 38.07 | 53.28 | A
| Electrical efficiency (net, annual average) [] | 28.06% | 28.06% | 28.15% | 28.15% | 25% | 38% | 25% | 39% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 29.54% | 29.54% | 29.63% | 29.63% | 27% | 40% | 28% | 41% | [A, H] | 1
| Cb coefficient (50°C/100°C) | 0.43 | 0.43 | 0.43 | 0.43 | 0.41 | 0.57 | 0.42 | 0.59
Cv coefficient (50°C/100°C) | bar: ctrl to -
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.855% | 2.855% | 2.857% | 2.857% | 2.115% | 3.156% | 1.747% | 3.316% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 3 | 3 | 3 | 3 | 2.5 | 3.5 | 2 | 3.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.26 | 0.26 | 0.26 | 0.26 | 0.22 | 0.29 | 0.19 | 0.32
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to upper
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40%
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | E | 1
| Cold start-up time [hours] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 95.45% | 96.36% | 99.09% | 99.82% | 90.9% | 99.82% | 95.45% | 99.91% | F | [1, 2]
| NOX [g/GJ_i] | 40 | 30 | 30 | 20 | 20 | 40 | 10 | 30 | F | [1, 2]
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | [1, 2]
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | [1, 2]
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | [1, 2]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 3.9345 | 3.8388 | 3.6367 | 3.3071 | 3.2433 | 4.5087 | 2.6584 | 4.53 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 2.4245 | 2.3713 | 2.2544 | 2.0417 | 1.9672 | 2.7754 | 1.6163 | 2.786 | [J, K]
| Nominal investment (installation) [MEUR/MW_e] | 1.4994 | 1.4675 | 1.393 | 1.2548 | 1.276 | 1.7333 | 1.0421 | 1.7333 | [J, K]
| Variable O&M (*total) [EUR/MWh_e] | 2.2756 | 2.2756 | 2.2756 | 2.2756 | 1.8396 | 2.6159 | 1.6163 | 2.8179 | L
| Fixed O&M (*total) [EUR/MW_e/y] | 142491.9442 | 138238.4533 | 130794.8443 | 115907.6263 | 116970.999 | 160569.2804 | 89323.3083 | 150998.926 | J
Technology-specific data
| Heat efficiency (net, annual average) [] | 70.35% | 70.35% | 70.26% | 70.26% | 49% | 73% | 49% | 72% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 68.87% | 68.87% | 68.77% | 68.77% | 47% | 71% | 46% | 70% | [B, H] | 1
| Nominal investment (*total) [MEUR/MW_i] | 1.1591 | 1.1378 | 1.074 | 0.9783 | 0.95704 | 1.3292 | 0.7869 | 1.3398 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.71246 | 0.70183 | 0.66992 | 0.60612 | 0.58485 | 0.8188 | 0.47852 | 0.82943 | K
| Nominal investment (installation) [MEUR/MW_i] | 0.44662 | 0.43598 | 0.41472 | 0.37218 | 0.38281 | 0.51042 | 0.30838 | 0.51042 | K
| Variable O&M (*total) [EUR/MWh_i] | 0.66992 | 0.66992 | 0.66992 | 0.66992 | 0.54232 | 0.77626 | 0.47852 | 0.84006 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 42215.8969 | 40939.8496 | 38600.4296 | 34453.276 | 34559.6133 | 47426.4232 | 26477.9807 | 44555.3169 | J
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0.063802 | 0.063802 | 0.063802 | 0.053169 | 0.063802 | 0.074436 | 0.053169 | 0.08507 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | M
| Output of recovered condensate [t/MWh_i] | 0.06 | 0.06 | 0.06 | 0.06 | 0 | 0.06 | 0 | 0.06 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 4.22% | 4.22% | 4.22% | 4.22% | 4% | 15% | 4% | 15% | C | 1
Notes:
A. The boiler in the plant is grate fired producing steam to be used in a subsequent back pressure steam turbine. Though a grate is reasonable flexible with respect to combusting different fuels the fuel feed system will be dependent on the type of fuel used. The system is optimised at DH return temperature 50°C and flow 100°C.
B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C. Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. For NOx-emissions no lower than 40 g/GJ SNCR is assumed. It is probably necessary to include a tail-end SCR catalyst to fulfill expected BREF requirements, particularly after year 2030. This has slight adverse effect on the electricity efficiency.
G. Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949

## 09c Straw, Medium
Technology |  | Biomass CHP - back pressure - straw - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 25.29 | 25.29 | 25.36 | 24.99 | 23.67 | 25.72 | 24.33 | 25.84 | A
| Electrical efficiency (net, annual average) [] | 30.03% | 30.03% | 30.12% | 29.68% | 26% | 31% | 27% | 31% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 31.61% | 31.61% | 31.71% | 31.24% | 29% | 33% | 30% | 33% | [A, H] | 1
| Cb coefficient (40°C/80°C) | 0.46 | 0.46 | 0.46 | 0.45 | 0.43 | 0.47 | 0.44 | 0.47
Cv coefficient (40°C/80°C) | bar: ctrl to -
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.847% | 2.847% | 2.849% | 2.84% | 2.091% | 3.168% | 1.728% | 3.211% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 4 | 4 | 4 | 4 | 3.4 | 4.6 | 3 | 5
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 1.5 | 3 |  | 1
| Space requirement [1000 m2/MW_e] | 0.28 | 0.28 | 0.28 | 0.28 | 0.24 | 0.32 | 0.21 | 0.35
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40%
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | E | 1
| Cold start-up time [hours] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 95.45% | 96.36% | 99.09% | 99.82% | 90.9% | 99.82% | 95.45% | 99.91% | F | [1, 2]
| NOX [g/GJ_i] | 90 | 70 | 50 | 30 | 20 | 90 | 10 | 50 | F | [1, 2]
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | [1, 2]
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | [1, 2]
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | [1, 2]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 3.8919 | 3.7962 | 3.6048 | 3.4134 | 3.1901 | 4.5831 | 2.7435 | 4.6682 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 2.3607 | 2.2969 | 2.1799 | 2.1055 | 1.8822 | 2.8073 | 1.6589 | 2.8711 | [J, K] | 1
| Nominal investment (installation) [MEUR/MW_e] | 1.5419 | 1.4994 | 1.4249 | 1.3079 | 1.3079 | 1.7652 | 1.0846 | 1.8077 | [J, K] | 1
| Variable O&M (*total) [EUR/MWh_e] | 2.2331 | 2.2331 | 2.2224 | 2.2544 | 1.712 | 2.5415 | 1.5313 | 2.7754 | L | 1
| Fixed O&M (*total) [EUR/MW_e/y] | 156315.7895 | 152062.2987 | 142491.9442 | 131858.217 | 127604.7262 | 178646.6166 | 101020.4082 | 170139.6349 | J | 1
Technology-specific data
| Heat efficiency (net, annual average) [] | 70.21% | 70.21% | 70.11% | 70.57% | 56% | 74% | 56% | 73% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 68.63% | 68.63% | 68.52% | 69.01% | 53% | 72% | 53% | 71% | [B, H] | 1
| Nominal investment (*total) [MEUR/MW_i] | 1.2335 | 1.2016 | 1.1378 | 1.0634 | 1.0102 | 1.4462 | 0.86133 | 1.4568 | [J, K] | 1
| Nominal investment (installation) [MEUR/MW_i] | 0.48915 | 0.47852 | 0.44662 | 0.40408 | 0.41472 | 0.56359 | 0.34028 | 0.56359 | K
| Nominal investment (equipment) [MEUR/MW_i] | 0.74436 | 0.72309 | 0.69119 | 0.65929 | 0.59549 | 0.89323 | 0.52105 | 0.89323 | K
| Variable O&M (*total) [EUR/MWh_i] | 0.70183 | 0.70183 | 0.70183 | 0.70183 | 0.54232 | 0.80816 | 0.47852 | 0.87197 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 49553.1686 | 48064.4468 | 45299.6778 | 41152.5242 | 40408.1633 | 56358.754 | 31475.8324 | 53062.2986 | J
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0.074436 | 0.074436 | 0.063802 | 0.063802 | 0.063802 | 0.08507 | 0.053169 | 0.08507 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Output of recovered condensate [t/MWh_i] | 0.09 | 0.09 | 0.09 | 0.09 | 0 | 0.09 | 0 | 0.09 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.767% | 1.767% | 1.767% | 1.768% | 1% | 15% | 1% | 15% | C | 1
Notes:
A. The boiler in the plant is grate fired producing steam to be used in a subsequent back pressure steam turbine. Though a grate is reasonable flexible with respect to combusting different fuels the fuel feed system will be dependent on the type of fuel used. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C. Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. For NOx-emissions no lower than 40 g/GJ SNCR is assumed. It is probably necessary to include a tail-end SCR catalyst to fulfill expected BREF requirements, particularly after year 2030. This has slight adverse effect on the electricity efficiency.
G. Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949

## 09c Straw, Small
Technology |  | Biomass CHP - back pressure - straw - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 3.05 | 3.05 | 3.06 | 3.01 | 2.97 | 3.09 | 2.92 | 3.04 | A
| Electrical efficiency (net, annual average) [] | 14.49% | 14.49% | 14.53% | 14.3% | 13% | 15% | 13% | 15% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 15.25% | 15.25% | 15.3% | 15.06% | 14% | 16% | 14% | 16% | [A, H] | 1
| Cb coefficient (40°C/80°C) | 0.18 | 0.18 | 0.18 | 0.18 | 0.17 | 0.18 | 0.17 | 0.18
Cv coefficient (40°C/80°C) | bar: ctrl to -
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.373% | 2.373% | 2.374% | 2.37% | 1.807% | 2.594% | 1.443% | 2.59% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 4 | 4 | 4 | 4 | 3.4 | 4.6 | 3 | 5
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.98 | 0.98 | 0.98 | 1 | 0.84 | 1.13 | 0.75 | 1.25
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | D | 1
| Minimum load (of full load) [] | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | D | 1
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | G | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 95.45% | 96.36% | 99.09% | 99.82% | 90.9% | 99.82% | 95.45% | 99.91% | F | 1
| NOX [g/GJ_i] | 90 | 70 | 50 | 40 | 50 | 90 | 40 | 50 | F | 1
| CH4 [g/GJ_i] | 16 | 11 | 8 | 4 | 4 | 16 | 2 | 16 | F | 1
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | 1
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | 1
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 7.2841 | 7.1033 | 6.7418 | 6.4759 | 6.1995 | 8.3794 | 5.4126 | 8.8366 | [E, J, K] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 4.1153 | 4.0089 | 3.8069 | 3.775 | 3.4985 | 4.732 | 3.1795 | 5.1148 | K
| Nominal investment (installation) [MEUR/MW_e] | 3.1689 | 3.0944 | 2.9349 | 2.701 | 2.701 | 3.6474 | 2.2331 | 3.7218 | K
| Variable O&M (*total) [EUR/MWh_e] | 4.8064 | 4.8064 | 4.7852 | 4.8596 | 3.5517 | 5.4445 | 3.1795 | 5.9336 | L
| Fixed O&M (*total) [EUR/MW_e/y] | 338152.5243 | 332835.6607 | 321138.5608 | 311568.2064 | 284983.8884 | 384940.9239 | 241385.607 | 398764.7693 | J
Technology-specific data
| Heat efficiency (net, annual average) [] | 86.34% | 86.34% | 86.29% | 86.53% | 73% | 88% | 72% | 88% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 85.58% | 85.58% | 85.53% | 85.78% | 72% | 87% | 71% | 87% | [B, H] | 1
| Nominal investment (*total) [MEUR/MW_i] | 1.1059 | 1.0846 | 1.0315 | 0.9783 | 0.9464 | 1.276 | 0.8188 | 1.3292 | [E, J, K] | 1
| Nominal investment (installation) [MEUR/MW_i] | 0.48915 | 0.46788 | 0.44662 | 0.40408 | 0.41472 | 0.55295 | 0.34028 | 0.56359 | K
| Nominal investment (equipment) [MEUR/MW_i] | 0.62739 | 0.61676 | 0.58485 | 0.56359 | 0.53169 | 0.72309 | 0.47852 | 0.76563 | K
| Variable O&M (*total) [EUR/MWh_i] | 0.73373 | 0.73373 | 0.73373 | 0.73373 | 0.54232 | 0.82943 | 0.47852 | 0.89323 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 51679.9141 | 50722.8786 | 49021.4823 | 46894.7368 | 43385.6069 | 58804.5113 | 36367.3469 | 60080.5585 | J
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0.08507 | 0.08507 | 0.074436 | 0.074436 | 0.074436 | 0.095704 | 0.063802 | 0.095704 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Output of recovered condensate [t/MWh_i] | 0.09 | 0.09 | 0.09 | 0.09 | 0 | 0.09 | 0 | 0.09 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.767% | 1.767% | 1.767% | 1.768% | 1% | 14% | 1% | 15% | C | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate. The electric power is produced by an ORC module (Organic Rankine Cycle; Waste Heat Recovery - WHR). Refer for instance to the following link for further information about technology and suppliers: http://www.enova.no/upload_images/36AC689098414B05A7112FA2EE985BDA.pdf . This is low temperature and low efficiency electric power but at an affordable price. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance. Though, the load control of the heat production is important and most units will perform better than the figure shown. Also, minimum load could be substantially lower.
E. Since electricity generation is only a secondary objective for minor heat producers, it may make more sense to relate the total investment only to the heat production capacity.
F. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However, to reach NOx-levels below 40 g/GJ SCR is assumed.
G. Warm start is starting with a glowing fuel layer on the grate.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies. NOTICE: There are to our knowledge no references on ORC plants running on straw.

## 09a Wood Chips HOP, small
Technology |  | Biomass boiler - boiler - wood chips - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 6.84 | 6.84 | 6.84 | 6.84 | 5.34 | 6.86 | 5.34 | 6.87 | A | 1
| Heat efficiency (net, annual average) [] | 114% | 114% | 114% | 114% | 89% | 115% | 89% | 115% | [B, C] | 1
| Heat efficiency (net, name plate) [] | 114% | 114% | 114% | 114% | 89% | 115% | 89% | 115% | [B, C] | 1
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.216% | 2.216% | 2.216% | 2.216% | 2.114% | 2.472% | 1.691% | 2.47% | [C, K]
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 1.7 | 2.3 | 1.5 | 2.5
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 1
| Space requirement [1000 m2/MW_h] | 0.22 | 0.22 | 0.22 | 0.22 | 0.19 | 0.25 | 0.16 | 0.27
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | E | 1
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | E | 1
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | H | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.97% | 97.97% | 97.97% | 97.97% | 89.85% | 98.98% | 97.97% | 98.98% | G | 1
| NOX [g/GJ_i] | 90 | 60 | 50 | 40 | 40 | 80 | 30 | 40 | I | 2
| CH4 [g/GJ_i] | 16 | 11 | 8 | 4 | 4 | 16 | 2 | 16 | I | 2
| N2O [g/GJ_i] | 4 | 3 | 3 | 1 | 1 | 4 | 1 | 4 | I | 2
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | I | 2
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 0.75499 | 0.73373 | 0.70183 | 0.62739 | 0.63802 | 0.86133 | 0.52105 | 0.87197 | [F, L]
| Nominal investment (equipment) [MEUR/MW_h] | 0.43598 | 0.42535 | 0.40408 | 0.36155 | 0.37218 | 0.49979 | 0.29774 | 0.49979 | [F, L]
| Nominal investment (installation) [MEUR/MW_h] | 0.31901 | 0.30838 | 0.29774 | 0.26584 | 0.26584 | 0.36155 | 0.22331 | 0.37218 | [F, L]
| Variable O&M (*total) [EUR/MWh_h] | 2.7541 | 2.8924 | 3.6474 | 4.0195 | 2.4883 | 3.9451 | 3.4985 | 5.5508 | M
| Variable O&M (electricity cost) [EUR/MWh_h] | 1.4887 | 1.627 | 2.382 | 2.7541 | 1.6057 | 2.1161 | 2.7222 | 3.5942 | M
| Variable O&M (other O&M) [EUR/MWh_h] | 1.2654 | 1.2654 | 1.2654 | 1.2654 | 0.8826 | 1.829 | 0.77626 | 1.9566 | M
| Fixed O&M (*total) [EUR/MW_h/y] | 35091.2997 | 34559.6133 | 33496.2406 | 31475.8325 | 29561.7616 | 40089.1515 | 24244.898 | 40408.1633 | 0
Technology-specific data
| Nominal investment (*total) [MEUR/MW_i] | 0.86133 | 0.84006 | 0.79753 | 0.72309 | 0.73373 | 0.98894 | 0.59549 | 0.99957 | [J, L] | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.49979 | 0.48915 | 0.45725 | 0.41472 | 0.42535 | 0.57422 | 0.34028 | 0.57422 | L
| Nominal investment (installation) [MEUR/MW_i] | 0.36155 | 0.35091 | 0.34028 | 0.30838 | 0.30838 | 0.41472 | 0.25521 | 0.41472 | L
| Variable O&M (*total) [EUR/MWh_i] | 3.1369 | 3.2965 | 4.1578 | 4.5831 | 2.8498 | 3.5091 | 4.0089 | 4.9447 | M
| Fixed O&M (*total) [EUR/MW_i/y] | 40089.1515 | 39451.1278 | 38175.0806 | 35835.6606 | 33708.9151 | 45618.6896 | 27647.6907 | 46044.0387
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.010634 | 0.021267 | L
| Output of recovered condensate [t/MWh_i] | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0.25 | 0 | 0.25 | D
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Additional heat potential with heat pumps (of thermal input) [] | 1.943% | 1.943% | 1.943% | 1.943% | 1% | 26% | 1% | 26% | D | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. Efficiencies refer to lower heating value. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency. Direct condensation and combustion air humidification are included in all cases except in lower range of 2020 and 2050. The colder the return temperature of the district heating, the higher the total efficiency at direct condensation.
D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
E. Load control of the heat production is important and units of this size can make rapid load variations. Similarly, the minimum load is quite low
F. Reference to heat output because of the lack of electricity production
G. Assuming content of sulphur in fuel of 20 g/GJ
H. Warm start is starting with a glowing fuel layer on the grate.
I. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However, to reach NOx-levels below 40 g/GJ SCR is assumed.
J. The nominal investment is in the range 0.6 to 1.1 MEUR/MWth
K. Result of model calculation, there are reports of DH plants operating at lower power consumption, down to 1% of heat generation.
L. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
M. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
N. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.

## 09a Wood Chips HOP, medium
Technology |  | Biomass boiler - boiler - wood chips - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 51.64 | 51.64 | 51.64 | 51.64 | 40.38 | 51.81 | 39.66 | 51.86 | A | 1
| Heat efficiency (net, annual average) [] | 114.8% | 114.8% | 114.8% | 114.7% | 89% | 116% | 88% | 116% | [B, C] | 1
| Heat efficiency (net, name plate) [] | 114.8% | 114.8% | 114.8% | 114.7% | 89% | 116% | 88% | 116% | [B, C] | 1
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.204% | 2.204% | 2.204% | 2.203% | 2.098% | 2.459% | 1.709% | 2.455% | [C, K]
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 1.7 | 2.3 | 1.5 | 2.5
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 2 | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 |  | 1
| Space requirement [1000 m2/MW_h] | 0.06 | 0.06 | 0.06 | 0.06 | 0.05 | 0.07 | 0.04 | 0.07
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | E | 1
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% |  | 1
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | H | 1
| Cold start-up time [hours] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.97% | 97.97% | 97.97% | 97.97% | 94.92% | 98.98% | 97.97% | 98.98% | G | 1
| NOX [g/GJ_i] | 90 | 60 | 40 | 30 | 40 | 80 | 20 | 40 | I | 2
| CH4 [g/GJ_i] | 16 | 11 | 8 | 4 | 4 | 16 | 2 | 16 | I | 2
| N2O [g/GJ_i] | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | I | 2
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | I | 2
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 0.54232 | 0.52105 | 0.49979 | 0.47852 | 0.45725 | 0.61676 | 0.37218 | 0.65929 | [F, L]
| Nominal investment (equipment) [MEUR/MW_h] | 0.39345 | 0.38281 | 0.36155 | 0.36155 | 0.32965 | 0.45725 | 0.27648 | 0.48915 | [F, L]
| Nominal investment (installation) [MEUR/MW_h] | 0.14887 | 0.13824 | 0.13824 | 0.11697 | 0.1276 | 0.17014 | 0.095704 | 0.17014 | [F, L]
| Variable O&M (*total) [EUR/MWh_h] | 2.7329 | 2.8711 | 3.6261 | 3.9983 | 2.4777 | 3.9132 | 3.4772 | 5.604 | M
| Variable O&M (electricity cost) [EUR/MWh_h] | 1.4781 | 1.6163 | 2.3713 | 2.7435 | 1.5951 | 2.1055 | 2.7116 | 3.6261 | M
| Variable O&M (other O&M) [EUR/MWh_h] | 1.2548 | 1.2548 | 1.2548 | 1.2548 | 0.87197 | 1.8077 | 0.76563 | 1.9779 | M
| Fixed O&M (*total) [EUR/MW_h/y] | 45512.3523 | 44661.6542 | 43066.5951 | 40620.8378 | 38068.7433 | 51573.5768 | 30625.1343 | 51573.5768 | 0
Technology-specific data
| Nominal investment (*total) [MEUR/MW_i] | 0.61676 | 0.60612 | 0.57422 | 0.55295 | 0.52105 | 0.71246 | 0.42535 | 0.75499 | L | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.44662 | 0.43598 | 0.41472 | 0.41472 | 0.38281 | 0.52105 | 0.31901 | 0.56359 | L
| Nominal investment (installation) [MEUR/MW_i] | 0.17014 | 0.15951 | 0.14887 | 0.13824 | 0.13824 | 0.19141 | 0.11697 | 0.19141 | L
| Variable O&M (*total) [EUR/MWh_i] | 3.1369 | 3.2965 | 4.1578 | 4.5938 | 2.8498 | 3.5091 | 4.0089 | 4.9447 | M
| Fixed O&M (*total) [EUR/MW_i/y] | 52211.6004 | 51254.565 | 49340.4941 | 46682.0623 | 43704.6187 | 59123.5231 | 35091.2997 | 59229.8604
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0.021267 | 0.021267 | 0.021267 | 0.010634 | 0.010634 | 0.021267 | 0.010634 | 0.021267 | L
| Output of recovered condensate [t/MWh_i] | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0.25 | 0 | 0.25 | D
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Additional heat potential with heat pumps (of thermal input) [] | 1.943% | 1.943% | 1.943% | 1.944% | 1% | 26% | 1% | 28% | D | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate as the basis assumption. Fluid-bed combustion technology may be an alternative.It can be assumed that the data for this does not differ significantly from grate fired boilers. Data in this sheet is applicable for plants in the range of 30-49,9 MW fired capacity (heat input). The system is optimised at DH return temperature 40°C and flow 80°C.
B. Boilers larger than approx. 20 MW fuel input for hot water production are designed-for-purpose products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. Efficiencies refer to lower heating value. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency. Direct condensation and combustion air humidification are included in all cases except in lower range of 2020 and 2050. The colder the return temperature of the district heating, the higher the total efficiency at direct condensation.
D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
E. Load control of the heat production is important and units of this size can make rapid load variations.
F. Reference to heat output because of the lack of electricity production
G. assuming content of sulphur in fuel of 20 g/GJ
H. Warm start is starting with a glowing fuel layer on the grate.
I. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However, to reach NOx-levels below 40 g/GJ SCR is assumed.
K. Result of model calculation, there are reports of DH plants operating at lower power consumption, down to 1% of heat generation.
L. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
M. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
N. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplierand operator information, or pre-project studies.
2. Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.

## 09a Wood Chips HOP, large
Technology |  | Biomass boiler - boiler - wood chips - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 103.43 | 103.43 | 103.43 | 103.42 | 80.92 | 103.78 | 79.47 | 103.87 | A | 1
| Heat efficiency (net, annual average) [] | 114.9% | 114.9% | 114.9% | 114.9% | 89% | 116% | 88% | 116% | [B, C] | 1
| Heat efficiency (net, name plate) [] | 114.9% | 114.9% | 114.9% | 114.9% | 89% | 116% | 88% | 116% | [B, C] | 1
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.201% | 2.201% | 2.201% | 2.2% | 2.095% | 2.456% | 1.706% | 2.452% | [C, K]
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 1.7 | 2.3 | 1.5 | 2.5
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 |  | 1
| Space requirement [1000 m2/MW_h] | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | 0.06 | 0.04 | 0.06
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | E | 1
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% |  | 1
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | H | 1
| Cold start-up time [hours] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.97% | 97.97% | 97.97% | 97.97% | 94.92% | 98.98% | 97.97% | 98.98% | G | 1
| NOX [g/GJ_i] | 90 | 60 | 40 | 20 | 40 | 60 | 20 | 40 |  | [2, 3]
| CH4 [g/GJ_i] | 3 | 2 | 2 | 1 | 1 | 3 | 0 | 3 |  | 3
| N2O [g/GJ_i] | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 |  | 3
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 |  | 3
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 0.47852 | 0.46788 | 0.44662 | 0.42535 | 0.40408 | 0.55295 | 0.32965 | 0.58485 | [F, L]
| Nominal investment (equipment) [MEUR/MW_h] | 0.36155 | 0.35091 | 0.32965 | 0.32965 | 0.30838 | 0.41472 | 0.25521 | 0.44662 | [F, L]
| Nominal investment (installation) [MEUR/MW_h] | 0.11697 | 0.11697 | 0.10634 | 0.095704 | 0.095704 | 0.13824 | 0.08507 | 0.13824 | [F, L]
| Variable O&M (*total) [EUR/MWh_h] | 2.7329 | 2.8711 | 3.6261 | 3.9983 | 2.467 | 3.9026 | 3.4772 | 5.5933 | M
| Variable O&M (electricity cost) [EUR/MWh_h] | 1.4781 | 1.6163 | 2.3607 | 2.7329 | 1.5951 | 2.1055 | 2.7116 | 3.6261 | M
| Variable O&M (other O&M) [EUR/MWh_h] | 1.2548 | 1.2548 | 1.2548 | 1.2548 | 0.87197 | 1.8077 | 0.76563 | 1.9779 | M
| Fixed O&M (*total) [EUR/MW_h/y] | 37430.7197 | 36792.696 | 35410.3115 | 33389.9033 | 31369.4952 | 42428.5714 | 25095.5961 | 42428.5714 | 0
Technology-specific data
| Nominal investment (*total) [MEUR/MW_i] | 0.55295 | 0.53169 | 0.51042 | 0.48915 | 0.46788 | 0.63802 | 0.38281 | 0.66992 | L | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.41472 | 0.40408 | 0.38281 | 0.38281 | 0.35091 | 0.47852 | 0.28711 | 0.51042 | L
| Nominal investment (installation) [MEUR/MW_i] | 0.13824 | 0.1276 | 0.1276 | 0.11697 | 0.11697 | 0.15951 | 0.095704 | 0.15951 | L
| Variable O&M (*total) [EUR/MWh_i] | 3.1369 | 3.2965 | 4.1578 | 4.5938 | 2.8498 | 3.5091 | 4.0089 | 4.9447 | M
| Fixed O&M (*total) [EUR/MW_i/y] | 43066.5951 | 42215.8969 | 40620.8378 | 38387.7551 | 36048.3351 | 48808.8077 | 28923.7379 | 48702.4705
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0.010634 | 0.010634 | 0.010634 | 0.010634 | 0.010634 | 0.021267 | 0.010634 | 0.021267 | L
| Output of recovered condensate [t/MWh_i] | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0.25 | 0 | 0.25 | D
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Additional heat potential with heat pumps (of thermal input) [] | 1.943% | 1.943% | 1.943% | 1.944% | 1% | 26% | 1% | 28% | D | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate. Fluid-bed combustion technology may be an alternative. It can be assumed that the data for this does not differ significantly from grate fired boilers. Data in this sheet is applicable for plants in the range of 80-99,9 MW fired capacity (heat input). The system is optimised at DH return temperature 40°C and flow 80°C.
B. Boilers larger than approx. 20 MW fuel input for hot water production are designed-for-purpose products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. Efficiencies refer to lower heating value. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency. Direct condensation and combustion air humidification are included in all cases except in lower range of 2020 and 2050. The colder the return temperature of the district heating, the higher the total efficiency at direct condensation.
D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
E. Load control of the heat production is important and units of this size can make rapid load variations.
F. Reference to heat output because of the lack of electricity production
G. Assuming content of sulphur in fuel of 20 g/GJ
H. Warm start is starting with a glowing fuel layer on the grate.
K. Result of model calculation, there are reports of DH plants operating at lower power consumption, down to 1% of heat generation.
L. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
M. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
N. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
3. Emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.

## 09b Wood Pellets HOP
Technology |  | Biomass boiler - boiler - wood pellets - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 6.07 | 6.07 | 6.07 | 6.07 | 5.45 | 6.09 | 5.37 | 6.1 | A | 1
| Heat efficiency (net, annual average) [] | 101.2% | 101.2% | 101.2% | 101.2% | 90% | 102% | 89% | 102% | [B, C] | 1
| Heat efficiency (net, name plate) [] | 101.2% | 101.2% | 101.2% | 101.2% | 90% | 102% | 89% | 102% | [B, C] | 1
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.055% | 2.055% | 2.055% | 2.055% | 1.705% | 2.295% | 1.384% | 2.292% | [C, K]
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 1
| Space requirement [1000 m2/MW_h] | 0.16 | 0.16 | 0.16 | 0.16 | 0.14 | 0.19 | 0.12 | 0.21
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | E | 1
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | E | 1
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | H | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 98.25% | 98.25% | 98.25% | 98.25% | 91.25% | 99.12% | 98.25% | 99.12% | G | 1
| NOX [g/GJ_i] | 90 | 50 | 40 | 40 | 40 | 70 | 20 | 40 | G | 1
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G | 1
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | G | 1
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | G | 1
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 0.77626 | 0.75499 | 0.72309 | 0.64866 | 0.65929 | 0.89323 | 0.54232 | 0.95704 | [F, L]
| Nominal investment (equipment) [MEUR/MW_h] | 0.46788 | 0.45725 | 0.43598 | 0.39345 | 0.40408 | 0.54232 | 0.32965 | 0.60612 | [F, L]
| Nominal investment (installation) [MEUR/MW_h] | 0.30838 | 0.29774 | 0.28711 | 0.25521 | 0.25521 | 0.35091 | 0.21267 | 0.35091 | [F, L]
| Variable O&M (*total) [EUR/MWh_h] | 1.9566 | 2.0842 | 2.786 | 3.1369 | 1.9247 | 2.4458 | 2.9136 | 3.7431 | [F, M]
| Variable O&M (electricity cost) [EUR/MWh_h] | 1.3718 | 1.51 | 2.2118 | 2.5521 | 1.4887 | 1.712 | 2.5202 | 2.9455 | [F, M]
| Variable O&M (other O&M) [EUR/MWh_h] | 0.57422 | 0.57422 | 0.57422 | 0.57422 | 0.43598 | 0.73373 | 0.38281 | 0.79753 | [F, M]
| Fixed O&M (*total) [EUR/MW_h/y] | 35729.3233 | 34772.2879 | 32964.5543 | 29668.0988 | 29774.4361 | 40301.826 | 23075.188 | 39451.1278 | F
Technology-specific data
| Nominal investment (*total) [MEUR/MW_i] | 0.7869 | 0.76563 | 0.73373 | 0.65929 | 0.66992 | 0.90387 | 0.55295 | 0.96767 | [J, L] | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.47852 | 0.46788 | 0.44662 | 0.40408 | 0.40408 | 0.55295 | 0.32965 | 0.60612 | L
| Nominal investment (installation) [MEUR/MW_i] | 0.30838 | 0.29774 | 0.28711 | 0.25521 | 0.26584 | 0.36155 | 0.21267 | 0.36155 | L
| Variable O&M (*total) [EUR/MWh_i] | 1.9779 | 2.1055 | 2.8179 | 3.1689 | 1.9566 | 2.2224 | 2.9562 | 3.3496 | M
| Fixed O&M (*total) [EUR/MW_i/y] | 36154.6724 | 35197.6369 | 33283.5661 | 30093.4479 | 30093.4479 | 40727.1751 | 23287.8625 | 39876.4769
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | L
| Output of recovered condensate [t/MWh_i] | 0.06 | 0.06 | 0.06 | 0.06 | 0 | 0.06 | 0 | 0.06 | D
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Additional heat potential with heat pumps (of thermal input) [] | 1.729% | 1.729% | 1.729% | 1.729% | 1% | 11% | 1% | 13% | D | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency.
D. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
E. Load control of the heat production is important and units of this size can make rapid load variations. Similarly, the minimum load is quite low
F. Reference to heat output because of the lack of electricity production
G. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However to reach NOx-levels below 40 g/GJ SCR is assumed.
I. Warm start is starting with a glowing fuel layer on the grate.
J. The nominal investment is in the range 0.6 to 1.1 MEUR/Mwth
K. Result of model calculation, there are reports of DH plants operating at lower power consumption
L. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
M. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
N. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.

## 09c Straw HOP
Technology |  | Biomass boiler - boiler - straw - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 6.19 | 6.19 | 6.19 | 6.19 | 5.34 | 6.22 | 5.34 | 6.22 | A | 1
| Heat efficiency (net, annual average) [] | 103.2% | 103.2% | 103.2% | 103.2% | 88% | 104% | 88% | 104% | [B, C] | 1
| Heat efficiency (net, name plate) [] | 103.2% | 103.2% | 103.2% | 103.2% | 88% | 104% | 88% | 104% | [B, C] | 1
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.096% | 2.096% | 2.096% | 2.096% | 1.81% | 2.338% | 1.448% | 2.336% | [C, J]
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 4 | 4 | 4 | 4 | 3.4 | 4.6 | 3 | 5
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.28 | 0.18 | 0.3
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | E | 1
| Minimum load (of full load) [] | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | E | 1
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | H | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 95.45% | 96.36% | 99.09% | 99.82% | 90.9% | 99.82% | 95.45% | 99.91% | G | 1
| NOX [g/GJ_i] | 90 | 70 | 70 | 70 | 40 | 90 | 20 | 70 | G | 1
| CH4 [g/GJ_i] | 16 | 11 | 8 | 4 | 4 | 16 | 2 | 16 | G | 1
| N2O [g/GJ_i] | 4 | 3 | 2 | 1 | 1 | 4 | 1 | 4 | G | 1
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | G | 1
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 0.95704 | 0.93577 | 0.8826 | 0.79753 | 0.80816 | 1.1484 | 0.65929 | 1.1591 | [F, K]
| Nominal investment (equipment) [MEUR/MW_h] | 0.46788 | 0.45725 | 0.42535 | 0.39345 | 0.39345 | 0.58485 | 0.31901 | 0.58485 | [F, K]
| Nominal investment (installation) [MEUR/MW_h] | 0.48915 | 0.47852 | 0.45725 | 0.41472 | 0.41472 | 0.56359 | 0.34028 | 0.57422 | [F, K]
| Variable O&M (*total) [EUR/MWh_h] | 2.1161 | 2.2437 | 2.9562 | 3.3177 | 2.0417 | 2.7541 | 3.0412 | 4.0834 | [F, L]
| Variable O&M (electricity cost) [EUR/MWh_h] | 1.4037 | 1.5419 | 2.2544 | 2.6053 | 1.5206 | 1.8184 | 2.5734 | 3.0838 | [F, L]
| Variable O&M (other O&M) [EUR/MWh_h] | 0.71246 | 0.71246 | 0.71246 | 0.71246 | 0.52105 | 0.93577 | 0.45725 | 0.99957 | [F, L]
| Fixed O&M (*total) [EUR/MW_h/y] | 55614.3932 | 54019.3341 | 50935.5532 | 45618.6896 | 46150.376 | 63377.014 | 34878.6252 | 59229.8604 | F
Technology-specific data
| Nominal investment (*total) [MEUR/MW_i] | 0.98894 | 0.95704 | 0.9145 | 0.82943 | 0.84006 | 1.191 | 0.68056 | 1.191 | [I, K] | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.47852 | 0.46788 | 0.44662 | 0.40408 | 0.40408 | 0.60612 | 0.32965 | 0.60612 | K
| Nominal investment (installation) [MEUR/MW_i] | 0.51042 | 0.48915 | 0.46788 | 0.42535 | 0.43598 | 0.58485 | 0.35091 | 0.58485 | K
| Variable O&M (*total) [EUR/MWh_i] | 2.1799 | 2.3182 | 3.0519 | 3.4241 | 2.1161 | 2.4458 | 3.1476 | 3.6367 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 57422.1267 | 55720.7304 | 52530.6122 | 47001.0741 | 47639.0977 | 65503.7594 | 36048.3351 | 61143.9313
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0.08507 | 0.08507 | 0.074436 | 0.074436 | 0.074436 | 0.095704 | 0.063802 | 0.095704 | K
| Output of recovered condensate [t/MWh_i] | 0.09 | 0.09 | 0.09 | 0.09 | 0 | 0.09 | 0 | 0.09 | [D, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.767% | 1.767% | 1.767% | 1.767% | 1% | 15% | 1% | 15% | D | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate.
B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency.
D. Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050. The system is optimised at DH return temperature 40°C and flow 80°C.
E. Load control of the heat production is important and units of this size can make rapid load variations. Similarly, the minimum load is quite low
F. Reference to heat output because of the lack of electricity production
G. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However, to reach NOx-levels below 40 g/GJ SCR is assumed. Warm start is starting with a glowing fuel layer on the grate.
I. The nominal investment is in the range 0.6 to 1.1 MEUR/MWth
J. Result of model calculation, there are reports of DH plants operating at lower power consumption
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.

## 09a Wood Chips extract. plant
Technology |  | Biomass CHP - extraction - wood chips - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 257.7 | 258.2 | 259.7 | 248.6 | 238.8 | 258.6 | 242.6 | 261.3 | A
| Electrical efficiency (net, annual average) [] | 40.8% | 40.9% | 41% | 39.4% | 37.8% | 41% | 38.5% | 41.4% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 43% | 43% | 43.2% | 41.4% | 39.8% | 43.1% | 40.4% | 43.6% | [A, H] | 1
| Cb coefficient (50°C/100°C) | 0.44 | 0.45 | 0.42 | 0.4 | 0.42 | 0.41 | 0.43 | 0.44
| Cv coefficient (50°C/100°C) | 0.14 | 0.14 | 0.14 | 0.13 | 0.13 | 0.13 | 0.13 | 0.14
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.6 | 3.5 | 2.3 | 3.8
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 1
| Construction time [years] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 |  | 1
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to upper
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 45% | 45% | 45% | 45% | 45% | 45% | 45% | 45%
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [E, G] | 1
| Cold start-up time [hours] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.5% | 97.5% | 97.5% | 97.5% | 97.5% | 97.5% | 97.5% | 97.5% | F | [1, 2, 3]
| NOX [g/GJ_i] | 30 | 20 | 20 | 10 | 10 | 30 | 10 | 20 | F | [1, 2, 3]
| CH4 [g/GJ_i] | 3 | 2 | 2 | 1 | 1 | 3 | 0 | 3 | F | [1, 2, 3]
| N2O [g/GJ_i] | 10 | 8 | 6 | 5 | 5 | 10 | 3 | 10 | F | [1, 2, 3]
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | [1, 2, 3]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 2.7648 | 2.6584 | 2.5521 | 2.4458 | 2.5521 | 3.2965 | 2.3394 | 3.5091 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 1.7014 | 1.7014 | 1.5951 | 1.4887 | 1.5951 | 2.0204 | 1.4887 | 2.2331 | K
| Nominal investment (installation) [MEUR/MW_e] | 1.0634 | 0.95704 | 0.95704 | 0.8507 | 0.8507 | 1.1697 | 0.8507 | 1.276 | K
| Variable O&M (*total) [EUR/MWh_e] | 2.7648 | 2.7648 | 2.7648 | 2.8711 | 2.9774 | 2.7648 | 2.8711 | 2.6584 | L
| Fixed O&M (*total) [EUR/MW_e/y] | 74436.0903 | 73372.7175 | 68055.854 | 65929.1085 | 70182.5994 | 85069.8174 | 60612.2449 | 84006.4447 | 0
Technology-specific data
| Nominal investment (*total) [MEUR/MW_i] | 1.1697 | 1.1484 | 1.0846 | 0.99957 | 0.99957 | 1.4037 | 0.93577 | 1.5313 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.73373 | 0.71246 | 0.66992 | 0.62739 | 0.62739 | 0.89323 | 0.58485 | 0.9783 | K
| Nominal investment (installation) [MEUR/MW_i] | 0.44662 | 0.43598 | 0.42535 | 0.38281 | 0.37218 | 0.51042 | 0.35091 | 0.55295 | K
| Variable O&M (*total) [EUR/MWh_i] | 1.1803 | 1.1803 | 1.1803 | 1.1803 | 1.1803 | 1.1803 | 1.1803 | 1.1803 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 32113.8561 | 31369.4952 | 29668.0988 | 27116.0043 | 28073.0397 | 36580.0215 | 24670.247 | 36367.3469
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.021267 | K
Steam reheat | bar: ctrl to -
Flue gas condensation | bar: ctrl to -
| Combustion air humidification | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | M
| Additional heat potential with heat pumps (of thermal input) [] | 4.1% | 4.1% | 4.1% | 4.1% | 4.1% | 4.1% | 4.1% | 4.1% | C | 1
Notes:
A. The boiler in the plant is a circulating fluid bed boiler (CFB) producing steam to be used in a subsequent extraction steam turbine with steam re-heat.
C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). This comes in addition to direct condensation that may yield 22% (of thermal input) when operated with combustion air humidification and assuming 50 °C DH return temperature. DH water may be heated in two (or more) stages, first stage being direct condensation (at hardly any drop in electricity output), second stage extraction steam with drop in electricity output, cf. the Cv-value.
D. Secondary regulation normally relates to power production.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator). Warm start-up time is particularly low for fluid bed types of plants.